## TOC
Data Center Assessment Inputs and Actions
DRAFT 1-24-08
Worksheet | Description
Inputs | Lists the features and metrics that are needed for each assessement area
Actions | Lists the potential efficiency actions in each assessment area
Notes:
1. This is a draft in development. Some fields are incomplete
2. All sheets set to print in landscape format

## Inputs
Data Center Assessment Inputs: Features and Metrics
DRAFT 1-24-08
Notes:
1. Each assessment area has two types of inputs: features and metrics
2. The features checklist can be used for stage 1 assessment (prior to site visit), and to prioritize metrics for stage 2 assessment
3. Input fields are shaded in blue - defaults are provided for priorities
4. Priority levels for metrics: 1 - Must have; 2 - Important, subject to ease of data collection; 3 - collect only if easily available
1. Overall Energy Management
Has an audit or commissioning been conducted within the last 2 years?
Is there a written energy management plan?
Are there staff with explicit energy management responsibility?
What is the redundancy level for Electrical systems? (N, N+x, 2N)
What is the redundancy level for HVAC systems? (N, N+x, 2N)
What is the current usage factor? (% of space?)
Metrics | Unit | Data Required | Priority | Value
Overall Energy Effectiveness (IT energy use / total energy use) | - | IT Equipment Energy Use Total DC Energy Use (Site) | 1
Site Energy Use Intensity | Site BTU/sf-yr | Total DC Energy Use (Site) DC Floor Area | 2
Source Energy Use Intensity | Source BTU/sf-yr | Total DC Energy Use (Source) DC Floor Area | 3
Purchased Energy Cost Intensity | Energy $/sf-yr | Total DC Energy Cost DC Floor Area | 2
Peak Electrical Load Intensity | Peak W/sf | Total DC Peak Elec Demand DC Floor Area | 2
2. Environmental Conditions
What are the temperature setpoints (specify range)?
What are the humidity setpoints (specify range)?
Recommended and allowable intake temperatures and humidity (specify ranges)?
Where are temperature and humidity sensors located (return, other)?
Do CRAC/CRAH units have centralized or distributed controls?
Are there humidity controls and does the data center need humidity control?
Are there procedures and personnel/cable grounding equipment to prevent ESD?
Are unit controls fighting each other (for example, simultaneously humidifying and dehumidifying)?
Does system have capability of taking slope and offset for sensor recalibration?
Metrics | Unit | Data Required | Priority | Value
Ratio Max Density to Average Heat Density | None | Max Heat Density Average Heat Density | 2
Actual Dew-Point Temperature | F | Data Center Dewpoint Temperature | 1
Climate Data | F | TMY/TRY/WYEC data | 1
Temperature and humidity sensor calibration | Slope and offset | Reference sensor reading | 1
3. Air Management, CRAC/CRAH/AHU
How many CRAC/CRAH/AHUs are there? Identify which operate under normal conditions and which are standby.
For each CRAC/CRAH/AHU collect nameplate data for unit, for each motor and submittal data identifying capacity and design conditions.
What is the clear ceiling in feet (slab to slab minus raised floor minus dropped ceiling)?
Is there a ceiling return plenum? If yes, what is the height and static pressure?
Is there a floor supply plenum (raised floor)? If yes, what is the height and static pressure?
What is the estimated floor leakage in percent of total system airflow?
Where are cables and pipes located?
Any significant cable build-up in floor plenum or over-head?
What is the rack arrangement (rows or cages)?
Are alternating hot and cold aisles implemented?
How wide are the cold aisles?
Are the racks and lineups tight to prevent air mixing (for example, are blanking panels used)?
What is the room architecture (open, semi-enclosed, enclosed)?
What is the configuration of air delivery (overhead [VOH], underfloor [VUF],...)?
Where are the overhead diffusers or perforated floor tiles placed (cold aisles, hot aisles, …)
What are the overhead diffuser characteristics (flow spread, exit velocity)?
Where are the air returns located (ceiling, wall, CRAC,...)?
Central or local (e.g., CRAC) air handling?
What is the airflow configuration of the CRAC units (down-flow, up-flow)?
Location of the CRAC units (perimeter, distributed, parallel, perpendicular, cold aisle, hot aisle)?
Is the air-delivery system balanced to ensure correct airflow rates?
Capacity control mechanism (supply temperature, supply flow, …) and control sensor location?
Are the fans VAV?
What is the dominant Equipment-Cooling (EC) Class (intake and exhaust locations on equipment)?
Any cosmetic doors on the equipment racks (none, solid, perforated,…)?
Is there any supplemental cooling (in-row, modular overhead, rear-door, liquid-cooled cabinet,…)?
Is there an air-balancing (allow proper aiflow distribution) program in place?
Is there a cable-mining (allow proper pressure distribution) program in place?
Is there a diffuser/tile-location (to conserve hot and cold aisles) program in place?
Is there a floor-tightness (sealing leaks) program in place?
Is there a rack/lineup-tightness (using blanking panels) program in place?
Are the cable penetrations sealed?
Does the CRAC/CRAH/AHU have a free cooling coil (water side economizer)?
Is there air-side free cooling?
Metrics | Unit | Data Required | Priority | Value
CRAC/CRAH/AHU Temperature Differential | F | Average Supply Air Temperature Average Return Air Temperature | 1
Average Rack Temperature Rise | F | Rack Intake Temps, Rack Exhaust Temps | 2
Return Temperature Index (RTI), measure of by-pass air and recirculation air. | % | Average Supply Air Temperature Average Return Air Temperature, Average Rack Temp Rise | 2
Individual Rack Intake Temperatures | F | Rack Intake temperatures | 2
Rack Cooling Index (RCI), measure of conformance with an intake temperature specification (e.g., ASHRAE, NEBS). | % | Rack Intake Temperatures, Recommended Temp Range, Allowable Temp Range | 2
CRAC/CRAH/AHU Moisture Differential | lbs | Entering and leaving absolute humidity and airflow | 1
Airflow Efficiency | W/cfm | CRAC Power / AHU Power CRAC Airflow / AHU Airflow | 2
Ratio Total System Flow to Total Rack Flow | None | Total System Airflow Rate, Total Rack Airflow Rate | 2
System Pressure Drop | in. w.g. | Supply Side Pressure Drop Return Side Pressure Drop | 3
Fan motor efficiency | % | Nameplate data | 1
Econ Utilization Factor | % | Cooling Load Served w/ Econ Total Cooling Load Served | 1
4. Central Cooling Plant
What is the chiller water distribution system? (need pull down menu)
For each chiller identify the type and unloading mechanism (need pull down menu)
For each chiller identify if it has hot-gas bypass (need pull down menu)
For each tower identify the type and fan contorl (need pull down menu)
For each pump identify the type and control (need pull down menu)
For each TES identify the type (need pull down menu)
Are there any 3 way valves or bypasses?
For each chiller, pump and tower note the make, model and serial number
For each chiller get the following design data: Tchws, Tchwr, CHWflow, capacity and power. For each water cooled chiller record Tcws, Tcwr and CWflow, for each air cooled chiller record Tosa-db. Minimum and maximum flow for evaporator and condenser (if applicable)
For each cooling tower get the following design data: FanHP, Tr, Ta, Twb, design flow per cell, min flow per cell, max flow per cell and number of cells
For each pump get the following design data: PumpHP, Meff, Flow, Head, BHP (if noted), Impeller size (if noted)
Get a piping schematic of the chilled water system (if available)
Get the control drawings including the sequence of operations
Is there water side free-cooling?
Water side econiomizer type
Cooling Tower Staging
Metrics | Unit | Data Required | Priority | Value
Chiller Plant Wire to Water Efficiency | kW/ton | Total Cooling Load Served Total Chiller Plant Energy Use | 1
Chiller Rated Efficiency at Design | kW/ton and NPLV | Chiller Rated Efficiency | 2
Cooling Tower Design Efficiency | gpm/HP | Cooling Tower Energy Use Total Cooling Load Served | 2
Cooling Tower Design Approach | F | Condenser Water Supply Temp Outside Wet Bulb Temp | 2
Condenser Approach Temperature | F | Consenser Refrigerant Temp Condenser Water Return Temp
Chilled Water Pumping Efficiency | W/gpm | Chilled Water Pumps Power Chilled Water Pumps Flow | 2
Condenser Water Pumping Efficiency | W/gpm | Condenser Water Pumps Power Condenser Water Pumps Flow | 2
Pump and fan motor efficiency | % | Nameplate data | 1
Chiller Water-Side Econ Utilization Factor | % | Cooling Load Served w/ Water Econ Total Cooling Load Served | 1
5. IT Equipment Power Chain
What is the Utility input voltage?
What is the UPS redundancy configuration?
What is the power distribution configuration?
What is the UPS load capacity?
What type of the UPS is being used?
What is the UPS input current total harmonic distortion?
What is the UPS input power factor?
Number of transformers downstream the UPS system?
Number of transformers / PDUs upstream the UPS system?
Number of STSs downstream the UPS system?
What is the anticipated future IT loads?
What is the standby-by power configuration?
Is there co-generation?
Do the servers have an efficiency rating?
Is virtualization used?
Metrics | Unit | Data Required | Priority | Value
UPS load capacity | kVA/kW | UPS rating | 1
UPS System Efficiency | % | UPS Output kW/UPS Input kW | 1
UPS input power factor | PF | UPS Power Factor measure at Input | 1
Transformer (upstream UPS system) Efficiency | % | XFMR Output kW/XFMR Transformer Input | 1
PDU (with built-in transformer) System Efficiency | % | PDU Output kW/ PDU Input kW | 1
IT Peak Power Density (actual) | W/sf | IT Peak Power (actual) / DC Floor Area | 1
IT Ave Power Density (actual) | W/sf | IT Ave Power (actual) / DC Floor Area
IT Peak Power Density (design) | W/sf | IT Peak Power (design) / DC Floor Area | 2
IT Rack Power Density (actual) | kW/rack | IT Peak Power (actual) / rack quantity | 1
IT Rack Power Density (design) | kW/rack | IT Peak Power (design) / rack quantity | 1
UPS output voltage | V - 120/208/480 / dc
Stand-by Generator Block heater power | W | Block Heater Power (actual) | 3
6. Lighting
Lights power density?
How are the lights controlled?
What type of lamps are used?
Metrics | Unit | Data Required | Priority | Value
Installed Lighting Power Density | W/sf | Data Center Lighting Installed Power Data Center Floor Area | 1

## Actions
Data Centers Assessment: Efficiency Actions
DRAFT 1-24-08
Actions
1. Overall Energy Management
Create an energy management plan
Assign staff with energy management
Sub-meter end-use loads and track over time
Review full system operation, and efficiency on regular basis.
Install monitoring equipment to measure system efficiency and performance.
Raise awareness and develop understanding among Data Center staff about the financial and environment impact of energy savings.
Train / raise awareness data center designers in the latest energy management best practices and tools.
Use life-cycle cost decision-making
Conduct regular preventative maintenance
Install peak shaving devices to support lights and non-critical lights where applicable.
2. Environmental Conditions
Review and revise temperature setpoints to target higher supply air temperature and higher intake temperatures
Eliminate humidification if possible, if not widen the setpoints.
Place temperature and humidity sensors so that they mimic the equipment intake conditions
Eliminate dehumidification controls
If possible recalibrate temperature and humidity sensors
Network CRAC/H unit humidifier controls or move humidifier to OSA system
Change the type of humidifier
Change unit cooling setpoints based on server thermal demand
Add personnel and cable grounding
3. Air Management, CRAC/CRAH/AHU
Ensure adequate match between heat load and raised-floor plenum height, by reducing heat density
Provide Adequate Ceiling Supply/Return Plenum Height. Height can be increased if clear ceiling allows.
Provide Adequate Clear Ceiling. Remove dropped ceiling if not used for air and clear ceiling is <12 feet.
Consider using dropped ceiling (if present) as return plenum
Remove abandoned cable and other obstructions from underfloor and over-head.
Implement alternating hot aisle/cold aisles
Provide physical separation of hot and cold air: Provide semi-enclosed aisles (e.g., aisle end doors) Provide flexible strip curtains to enclose aisles Provide rigid enclosures to enclose aisles Use in-rack ducted exhaust
Convert to VFD fans that allow variation of airflow to meet cooling demand.
Configure equipment in straight lineups (rows) for hot/cold aisles and cable management
Place supply devices in cold aisles only
Use appropriate overhead diffusers (if present)
Place returns at high elevation (extensions)
Take return from hot aisles
Provide adequate floor plenum pressure
Seal floor leaks (including cable cutouts)
Use supplemental cooling (for example, high density areas)
Line up CRAC units with hot aisles
Use adequate ratio system flow to rack flow (target 1.0 or RTI=100%)
Balance the air-distribution system (diffusers/tiles)
Use IT equipment with higher temperature rise
Use IT equipment with front to rear or front to top airflow
Remove cosmetic doors from equipment racks
Provide adequate free area on rack doors for air movement if doors are necessary for security reasons
Maintain tight racks to prevent bypass of air (blanking panels & sealing between racks)
Maintain unbroken lineups to prevent bypass of air
Shut off CRAC/H units
Add VSD to fans and control all fans in parallel. Add pressure sensor (under floor or in duct) for control of fans. Consider fan reset by demand.
Get rid of prefilters
Change dirty filters or change filters to appropriate MERV rating
Seal ducts or casings to reduce leakage
Fix system effects in distribution ducts
Change CRAC/CRAH/AHU motors to premium efficiency
Add Airside Economizer(s) to the Existing CRAC/CRAH/AHU(s)
Add Waterside Economizer(s) to the Existing CRAC/CRAH/AHU(s)
Retro-Commission and Optimize the Existing Airside Economizer(s)
Convert from air-cooled DX to water-cooled DX or evaporative precooled condensing units.
Consider fans/CRAC/CRAH/AHU for replacement with new more efficient equipment
4. Cooling Plant
Add VSDs to cooling tower fans
Convert cooling towers to accommodate 3:1 variable flow and fix controls to run as many cells as possible.
Evaluate chillers for replacement
Optimize all plant controls: Staging of equipment (chillers, pumps and fans CWS reset CW flow reset CHW reset pump speed reset by demand..
Convert all 3 way valves to 2 way and close off all bypasses. Add VSD to pumps. Control pump speed to pressure. Consider reset of pressure setpoint by demand.
Change (CT fans and pumps) motors to premium efficiency
Select Chiller for High Full and Part-Load Efficiency
Select Towers for Efficiency >80gpm/hp and close approach (3-4°F)
Convert primary secondary systems to primary-series secondary systems, add VSDs to primary pumps as required.
Monitor System Efficiency
Right size the Cooling Plant
Recover Waste Heat for heating uses in other spaces
Add integrated waterside economizer to plant
Improve cooling tower water treatment to reduce energy use
Recalibrate CHWS, and CWS temperature sensors.
5. IT Equipment Power Chain
Maximize UPS load capacity: - UPS types / topologies (DB Con/DLT Con/Rotary) - Redundant configuration not to exceed (N+1) or 2 N. - Use modular UPS - Shutting down / idle modules when the redundancy level is high enough
Consider high efficient UPS types / topologies.
Consider UPS without input filters.
Consider actual IT power consumption instead of nameplate - If expanding to data center.
Use MV & LV transformers with higher efficiency, e.g. NEMA TP1
Minimize / reduce the number of transformers upstream and downstream UPS systems)
Locate transformers outside raised floor area, if practical.
Maintain power factor (PF) at the Main feeder Panel 0.90 PF or higher without power factor correction
Retrofit IT equipment with unity power factor (PF) and low current total harmonic distortion (THD)
Eliminate or improve control power source for block heater(s) / HWJ(s) i.e. solar, natural Gas, chw heat rejection system, etc
Standby Generator block heater / heater water jacket(s) (HWJ) operate with thermostat control
Install power analyzer meters at critical components to measure instant power and energy values (to generate periodic 12 month tracking reports)
Specify High Efficiency Power Supplies
Eliminate redundant power supplies
Eliminate UPS Systems
Bypass UPS
Consider DC voltage to IT rack
Perform an Infra-Red (IR) test for the main transformers and other electrical systems
Perform routine maintenance and testing.
Improve the load balance of the RPP between the phases
Change UPS DC capacitors if older than 5 years
Conduct assessments to find near-term ways to cut electricity demand
6. Lighting
Employ Retrofit energy-efficient lighting and ballasts
Employ lighting controls such as occupancy sensors for data center, emergency generator(s), UPS(s), and Battery rooms
Lights in raised floor area are located above the aisles
Install peak shaving devices to support lights where applicable.
Bi-Level Lighting
Task Lighting

## Scratch (hidden)
Data Center Performance Metrics
DRAFT 1-24-08
Indicates metrics that have incorporated into new spreadsheet
ID | Name | Unit | Priority | Data Required | Notes
Overall Data Center
B1 | Energy Effectiveness | % | 1 | dB1, dB2, dB3, dP1 | IT equipment energy vs. Site energy use
B2 | Source Energy Use Intensity | Source BTU/sf-yr | 2 | dG1, dG7, dB1, dB2, dB3 | Note if on-site generation included
B3 | Purchased Energy Cost Intensity | Energy $/sf-yr | 2 | dG1, dB4 | Note if on-site generation included
B4 | Site Energy Use Intensity | Site BTU/sf-yr | 2 | dG1, dB1, dB2, dB3 | Note if on-site generation included
B5 | Peak Electrical Load Intensity | Peak W/sf | 2 | dG1, dB5 | Note if on-site generation included
Air Handling System
V1 | Air Handling Energy Use Intensity | kWh/sf-yr | 1 | dV1, dV6, dG1 | Aggregate for all AHU and CRACs
V2 | Air Handling Power Intensity | W/sf | 1 | dV2, dV7, dG1 | Aggregate for all AHU and CRACs
V3 | Air Handling Airflow Efficiency | W/cfm | 2 | dV2, dV3, dV7, dV8 | Aggregate for all AHU and CRACs
V4 | Total System Pressure Drop | in. w.g. | 3 | dV4, dV5 | Total = supply+exhaust
Cooling and Heating System
M1 | Temperature Deadband | F | 2 | dM1, dM2
M2 | Humidity Deadband and Control | % | 1 | dM3, dM4, dM6, dV12, dV13, dV14, dV15 | AHU and CRACs
M3 | Hot Spot Intensity | F | 1 | dM5
M4 | Supply temperature control | F | 1 | dV9, dV11, dV15
M5 | Temp Difference through CRACs | F | 1 | dV10, dV11
M6 | Cooling Load Intensity | sf/ton | 2 | dM7, dG1 | central plant, CRAC Dx
M7 | Cooling System Energy Use Intensity | kWh/sf-yr | 3 | dM8, dG1 | central plant, CRAC Dx
M8 | Cooling System Efficiency | kW/ton | 1 | dM9, dM13, dM15, dM18, dM26 | central plant, CRAC Dx
M9 | Cooling System Design Load Efficiency | kW/ton | 2 | dM10, dM7 | central plant, CRAC Dx
M10 | Cooling System Design Load Intensity | W/sf | 2 | dM10, dG1 | central plant, CRAC Dx
M11 | Chiller Rated Efficiency | NPLV | 2 | dM12 | 1 metric per chiller
M12 | Cooling Tower Efficiency | kW/ton | 3 | dM15, dM9
M13 | Cooling Tower Approach | F | 3 | dM28, dG9
M14 | Chilled Water Design Pumping Efficiency | W/gpm | 3 | dM16, dM17
M15 | Chilled Water Pumping Efficiency | W/gpm | 3 | dM18, dM19
M16 | Condenser Water Pumping Efficiency | W/gpm | 3 | dM26, dM27
M17 | Reheat Energy Use Factor | % | 1 | dM31, dB1, dB2, dB3 | alternative metric?
M18 | Water-Side Economizer Utilization Factor | % | 1 | dM29, dM9
M19 | Air-Side Economizer Utilization Factor | % | 1 | dM30, dM9
Process Loads
P1 | IT Equipment Power Density: Design | W/nsf | 2 | dP2, dG2 | Uses Electrically Active Floor Area
P2 | IT Equipment Power Density: Actual | W/nsf | 1 | dP1, dG2 | Uses Electrically Active Floor Area
P3 | IT Equipment Power Sizing Ratio | - | 1 | dP1, dP2
P4 | UPS Efficiency | % | 1 | dP7, dP8, dP9
P5 | PDU Effeciency | % | 1 | dP10, dP11, dP12
P6 | Standby Genertor Losses | - | 2 | dP13, dP14, dP15
Lighting System
L1 | Lighting Energy Use Intensity | kWh/sf-yr | 2 | dL1, dG1
L2 | Data Center Lighting Installed Power Intensity | W/sf | 2 | dL2, dG1