MEMORANDUM

DATE:	June 27, 2005

SUBJECT:	Emission Standards for Emergency Stationary CI Engines

FROM:	Melanie Taylor, Alpha-Gamma Technologies, Inc.

TO:		Sims Roy, EPA OAQPS ESD Combustion Group

The purpose of this memorandum is to provide the rationale used to establish the emission standards for emergency engines, including fire pump engines, in the proposed new source performance standards (NSPS) for stationary compression ignition (CI) internal combustion engines (ICE).  An emergency stationary CI internal combustion engine is defined in the proposed NSPS as a stationary internal combustion engine whose operation is limited to emergency situations, maintenance checks, and readiness testing.  Examples include stationary ICE used to produce power for critical networks or equipment (including power supplied to portions of a facility) when electric power from the local utility is interrupted, or stationary ICE used to pump water in the case of fire or flood, etc.  Examples also include stationary ICE used during Federal or State declared disasters and emergencies, and simulations of emergencies by Federal, State, or local governments.

Emission Standards for Emergency Engines

For engines with a displacement of less than 10 liters per cylinder, the emission standards in the proposed NSPS are primarily based on the EPA standards for nonroad diesel engines.  The emission standards for engines with a displacement between 10 and 30 liters per cylinder in the NSPS are based on the EPA standards for marine diesel engines.  The standards for nonroad and marine diesel engines are phased in over several years and have Tiers with increasing levels of stringency.  Engines are separated into engine power ranges, and some emission standards vary between ranges.  The basis for this is EPA’s analysis of the applicability of specific emission control strategies for each power range of engines.  The Tier 2 and Tier 3 standards for nonroad diesel engines and the Tier 2 standards for marine engines are based on the most advanced engine-based technologies available for the various engines classes in the timeframe of the nonroad and marine diesel engine rulemakings.  For most nonroad diesel engines, the Tier 4 levels represent the emission reductions possible from the application of catalyzed diesel particulate filters (CDPF) and nitrogen oxides (NOx) adsorbers to the expected emission levels for the previous tier engines.  The Tier 4 particulate matter (PM) standard for nonroad diesel engines below 25 horsepower (HP) and the Tier 4 NOx standard for nonroad diesel engines below 75 HP are not based on the application of add-on emission control.  Tier 4 standards for marine engines have not been promulgated at this time.  The EPA is currently reviewing the possibility of promulgating more stringent standards for marine engines similar to the Tier 4 standards promulgated for land based nonroad CI engines.  In that context, the EPA will review whether such technologies are appropriate for stationary CI ICE with a displacement between 10 and 30 liters per cylinder.  The NSPS for such engines may, therefore, be revised at that time to require more stringent standards in the future.

The EPA believes that it is appropriate to base the standards for most stationary CI engines on the nonroad and marine diesel engine standards because the design and emissions characteristics of the engines are very similar.  Engine manufacturers have indicated to EPA that in most cases they do not separately design and manufacture separate CI engines for stationary use, and they often sell the same CI engine for use in nonroad and marine equipment as they do for use in stationary applications.  Most CI engines that are ultimately used in stationary applications are designed and built for use in both stationary and nonroad/marine applications.  Engine manufacturers indicated that stationary CI engines with a displacement of less than 10 liters per cylinder were similar to nonroad diesel engines, and stationary CI engines with a displacement of 10 liters per cylinder or more were similar to marine diesel engines.

The EPA expects that even if there were no NSPS for stationary CI engines, emissions from those engines would generally decline in step with the decreasing emissions from nonroad and marine engines, since many stationary engines are similar to nonroad and marine engines.  The EPA believes that this would be true until the Tier 4 standards that are based on add-on control take effect; without the NSPS, engine manufacturers would not equip stationary engines with add-on controls.  As part of the NSPS rulemaking process, the EPA evaluated the cost of control per ton of pollutant reduced that would result from requiring stationary engines to be equipped with add-on controls that would reduce emissions to meet the Tier 4 emission standards.  The cost per ton analysis is presented in the memorandum entitled “Cost per Ton for NSPS for Stationary CI ICE.”  In that memo, the cost per ton of CDPF and NOx adsorber was evaluated for both emergency and prime (non-emergency) engines.  Prime engines are estimated to operate approximately 1,000 hours per year, while emergency engines operate an estimated 37 hours per year.  Because emergency stationary CI engines are only operated for a few hours each year, emissions from these engines are relatively low compared to emissions from prime engines.  The cost of control per ton of pollutant reduced is therefore much higher for emergency engines.

The EPA determined that the relatively high cost of control as compared to the amount of pollutant reduced did not justify the selection of add-on controls for emergency engines.  The emission standards for emergency engines are therefore based on the most stringent standards that do not require add-on emission controls.  The basis for the proposed standards is as follows:

- For emergency stationary CI engines with a displacement of less than 10 liters per cylinder, the proposed standards are based on the Tier 2 and 3 nonroad diesel engine standards, except that for emergency engines less than 25 HP, the proposed standards are based on the Tier 4 PM standard for nonroad diesel engines below 25 HP, and for emergency engines less than 75 HP, the proposed standards are based on the Tier 4 NOx standard for nonroad diesel engines below 75 HP.

- For emergency stationary CI engines with a displacement of 10 liters per cylinder or more, the proposed standards are based on the Tier 2 marine diesel engine standards.

Fire Pump Engines

Stationary CI fire pump engines are a subset of emergency engines.  Fire pump engines are emergency stationary CI engines certified to National Fire Protection Association (NFPA) requirements that are used to provide power to pump water for fire suppression or protection.  During the NSPS rulemaking process, EPA met with Clarke Fire Protection Products, a leading provider of fire pump engines.  Representatives from John Deere and Moore Pump and Equipment also attended one of the meetings.

During the initial meeting with Clarke, EPA presented the potential emission standards for emergency engines, which have been discussed previously in this memorandum.  The fire pump engine supplier stated that engine manufacturers would not be able to produce fire pump engines that could meet the Tier 2 emission standards in the timeframe proposed by EPA.  Also, according to Clarke, additional time is needed to meet the Tier 3 levels, because engines must be designed, certified, and manufactured to meet the specifications of NFPA 20 (Standard for the Installation of Stationary Pumps for Fire Protection), which requires the engine to be certified by independent certifying organizations such as Underwriters Laboratory and Factory Mutual.  This is a process that takes approximately 3 years.  Clarke also indicated that high speed engines, which are engines with a rated speed of 2,560 revolutions per minute or greater, would need even more time to comply with the Tier 3 standards.

According to Clarke, high speed engines allow the fire pump to produce greater output water pressures, eliminating the need for a second pump.  Furthermore, Clarke indicated that many, if not all, of these high speed engines are not replaceable with similar engines that meet EPA’s emission standards.  Clarke indicated that it may be able to produce high speed emergency fire pump engines that meet Tier 3 emission standards if an additional 3 years are provided in addition to the extra 3 years needed for emergency fire pump engines that are not high speed engines to meet Tier 3 emission standards.  In other words, high speed emergency fire pump engines would be given up to 6 additional years to meet Tier 3 emission standards after the timeframe that other stationary CI engines that are not fire pump engines would be required to meet Tier 3 levels.

Emergency fire pump engines account for a small percentage of all stationary CI emergency engines.  According to EPA estimates, emergency fire pump engines represent about 3 percent of stationary CI emergency engines.  Resulting emissions by allowing certain emergency fire pump engines to skip Tier 2 and providing additional time to comply with the proposed Tier 3 emission standards are therefore minimal with respect to the emissions from all stationary CI emergency engines.  The EPA believes it is appropriate to allow certain emergency fire pump engines to skip Tier 2 and be given additional time to comply with the Tier 3 emission standards of the proposed NSPS, as discussed above.  For emergency fire pump engines where there is no Tier 3 emission standard, i.e., engines less than 50 HP and engines greater than 600 HP, EPA has provided additional time to comply with the Tier 2 level.  Stationary CI fire pump engines are used in critical situations for life safety purposes and EPA believes that the proposed allowances will ensure that the emergency fire pump development process is not compromised and will provide sufficient time to develop fire pumps that meet the requirements of NFPA and EPA’s proposed emission standards.