ELECTRICAL SPECIFICATION

SECTION 16851

ARCHITECTURAL LIGHTING CONTROL SYSTEM

PART 1 - GENERAL

1.01	WORK INCLUDED

Provision, installation and testing of architectural lighting control system.

1.02	RELATED WORK

A.	Conduit

B.	Wire and cable

C.	Control wiring

D.	Any other related sections of specifications 16001 Electrical Work.

1.03	SYSTEM DESCRIPTION

A.	System shall use solid state devices for control of lighting loads.

B.	Dimmer equipment cabinets and fixture packs contain all power devices.

C.	All user operated controls are low voltage.

D.	System shall be factory pre-assembled.  Sub-assembly-type system for contractor final construction in field shall not be acceptable.

1.04	REGULATORY REQUIREMENTS

A.	National Electric Code (N.E.C.)

B.	National Electric Manufacturer's Association (N.E.M.A.)

C.	Underwriters Laboratories, Inc. (UL)

1.05	SUBMITTALS

A.	Submittals shall be as specified.

B.	Submit all shop drawings showing all mechanical and electrical construction details.

C.	Submit complete interconnecting schematic diagrams.

D.	Submit manufacturer's standard catalog data and specification sheets giving all construction and specification information on components and sub-systems.

E.	Provide test data as required to demonstrate conformance with PART 2 of this specification.

1.06	QUALITY ASSURANCE

A.	Manufacturer:  Company specializing in architectural lighting control systems with a minimum of ten years experience.

B.	The entire system shall be listed by Underwriters Laboratories, Inc.  In addition, each dimming module shall be specifically listed by UL for control of the required loads (i.e., incandescent, fluorescent).

C.	The dimming system shall meet Military Standard 217C to ensure a minimum average design lifetime of ten years continuous operation.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURER

A.	Lutron Electronics Company, Inc.

2.02	DIMMING CABINETS

A.	Cabinets shall be wall or floor mounted NEMA grade, constructed of sheet steel plates not less than #14 U.S. gauge.

B.	Dimming cabinets shall be completely pre-wired by the manufacturer.  The contractor shall be required to provide input feed wiring, load wiring, and control wiring which terminates to a set of clearly marked low-voltage terminals.  No other wiring or assembly by the contractor shall be permitted.

C.	Cabinets shall contain output circuit breakers to provide primary line side protection and outgoing branch circuit protection for each dimming module.  Circuit breakers shall be designed to trip within 8 milliseconds after a 400 ampere surge.  Circuit breakers shall contain a visual trip indicator and shall be rated at 10,000 AIC (120V).

D.	Cabinets shall contain current carrying terminals with factory installed brass or copper jumpers.  These jumpers will enable power to completely bypass the dimmer modules.  Bypass jumpers shall be clearly and permanently labeled and shall be reusable at any time.  Low voltage control signal methods of bypass shall not be acceptable.

E.	Cabinets shall be cooled exclusively by means of free convection, unaided by fans.

F.	All load current carrying components shall be mechanically attached to a black anodized heat sink.  The readings of three temperature probes placed in the upper quarter of the cabinet equi-distant from each other and the cabinet walls shall neither exceed ambient temperature by more than 15oC nor differ from each other by more than 5oC.

G.	Internal wire used within the cabinet shall be UL listed AWM and have a 105oC temperature rating clearly labeled on the surface of the wire.  All wiring shall be harnessed with cable ties or wire ducts at sufficient intervals to present a neat, orderly appearance.  All field connections shall be provided to allow the use of stranded or solid wire for field connections.

H.	All solid state circuit boards shall be made of UL approved flame retardant epoxy glass material, and shall use plate-through holes.

2.03	DIMMER MODULES

A.	Silicon thyristors shall be used to control the power furnished to the loads.  The complete load current shall be carried by these devices.  They shall be capable of withstanding surges, without impairment to performance, of 6000 volts, 3000 Amps as specified by I.E.E.E. std. 587-1980.  In addition, under fully loaded operating conditions, all devices shall operate at a minimum 20oC safety margin below the component temperature rating.

B.	A positive air gap switch shall be employed with each dimmer to insure that the load circuits are open when the dimmer is switched off.  Use of semi-conductors to accomplish this result shall not be acceptable.

C.	The dimmers shall be designed to respond to a control signal not exceeding 42 VDC or 30 VAC (class II wiring maximums) which shall be independent of the phase connection to the module.

D.	All modules shall be voltage regulated so that ± 10% change in line voltage shall cause no more than ± 3% change in output voltage.

E.	All modules shall provide a smooth and continuous "square law" dimming curve throughout the entire dimming range.

F.	All modules shall be completely modular in nature and interchangeable with each other within the cabinets to allow ease of maintenance and future modification and/or expansion of the system.

G.	All dimmers shall be 98% or greater in efficiency at 100% intensity, 100% full load.

H.	Incandescent

1.	All modules shall employ electronic soft start operation: dimmer shall turn on at 0o conduction angle and fade up to set lighting level.  Completion of operation must occur within 0.5 seconds without overshoot.  Performance shall be independent of light level.

2.	Filtering for incandescent loads shall be provided in each dimmer so that current rise time shall be at least 350 microseconds at 50% rated dimmer capacity, and at no point rise faster than 30 mA/microsecond at a 90o conduction angle as measured from 10-90% of the load current wave form.

3.	Incandescent Standard

Incandescent modules shall be rated to control 1200 to 7200 watts of standard 120 volt tungsten load.  Minimum light levels shall be user adjustable.

4.	Non-Dim Module

The non-dim module shall be rated to control 2000 VA of tungsten, fluorescent or other lighting loads or non-lighting loads per section.  Each module contains up to three sections.  The module shall contain electrically held mercury contactors rated for a minimum of 35 Amperes.  When used with a preset control system, the modules shall turn off and on positively at the start of the light level transition period.

2.04	CONTROLS

A.	Controls shall be low voltage type as specified here and as listed below and/or shown on the drawings.  Switch box controls shall use low voltage Class II wiring, electrically isolated from power wiring by means of a UL listed Class II transformer.

B.	Faceplates shall be machine fabricated from a single piece of solid brushed aluminum.

C.	Faceplates shall attach to the wallbox using no visible means of attachments and shall be attached in a manner so as to prevent unauthorized removal (i.e., magnets or Velcro are not acceptable).

D.	Faceplate graphics shall be silk-screened by the manufacturer and shall be standard graphics.  The graphics process shall be such that the graphic material chemically bonds to the metal plate base, so that it resists removal via commercial cleaning solutions or scratching by fingernails.

E.	Wiring to controls from the dimmer equipment panels shall utilize low voltage class II wiring.  Connections to the controls shall be made to clearly numbered leads on the controls.

F.	Preset Control Systems

Each flush-mount unit shall consist of four touch buttons to provide scene selection, solid state LED's to indicate which scene is activated, individually illuminated potentionmeters to indicate lighting levels of each zone and electronic fade between each scene.  Fade rate for all zones shall be adjusted by one screwdriver adjustment at the panel.  A fifth touch-button shall switch the system off.  The entire preset section shall be concealed behind a smoked translucent flush window which shall appear black except for the illuminated potentionmeters in the active scene.

1.	Preset activator control shall contain the same 4-scene activating buttons with indicating LED's and off button as specified above.  Stations shall be as indicated on drawings.

2.	Entrance control station shall contain an on button with LED and an off button.  This control shall call up a single pre-designated scene upon activation.  Stations shall be as indicated on drawings.

2.05	QUALITY CONTROL

A.	All components used in the dimming system shall be inspected following Military Standard 105D or equivalent.

B.	Dimming module main power semiconductors shall be 100% tested at a case temperature of 100oC and with rated voltage applied for a minimum of 48 hours.

C.	The completely assembled dimming system shall be operated at full rated load for a minimum of five hours before shipment.

D.	Finished system shall be fully tested for proper operation of all control functions per system approved submittals.

E.	Submittals shall include certification by the manufacturer of the successful completion of the tests described in paragraphs A, B, C, and D above.

PART 3 - EXECUTION

3.01	INSTALLATION

A.	The system shall be installed utilizing complete manufacturer's shop drawings and in accordance with these specifications.

B.	Upon completion of the installation and prior to removal of the bypass jumpers, the contractor shall completely test all line voltage power and low voltage control wiring for continuity and accuracy of connections.  The jumpers shall remain in place until all loads have been fully tested and found to be free of miswires, short circuits or other wiring defects.

3.02	SYSTEM CHECK-OUT

A.	Upon completion of the installation, the system shall be completely checked out by a factory based engineer.  The check out will be performed upon notification by the contractor that the system installation is complete and that all loads have been tested live for continuity and freedom from defects and that all control wiring has been connected and checked for proper continuity.

B.	Upon completion of the system check out, the engineer shall demonstrate the operation of the system to any interested parties.

C.	Warranty service to be done by factory based engineer.