MSFC PRACA : 2003-02-12 08:41

MSFC Problem Reporting and Corrective Action (PRACA) System

WHOLE RECORD REPORT( + ADDENDUM)

| MSFC Record # A17352 | In-Flight Anomaly Number -- | Contractor Report Number S-080 | JSC# -- | KSC# -- |
| --- | --- | --- | --- | --- |
| Problem Title FACILITY BUILDING 103 PARTICULATE INTRUSION |
| EICN# -- | ELEMENT ET | Contractor LMMSS | FSCM# -- | FCRIT 3 |
| HCRIT -- | Sys_Lvl -- | Misc Codes A B C D E F G H I J K L M N O |
| HARDWARE EIM | NOMENCLATURE -- | PART# -- | SER/LOT# -- | MANUFACTURER -- |
| HARDWARE LRU | NOMENCLATURE -- | PART# -- | SER/LOT# -- | MANUFACTURER -- |
| HARDWARE NCA | NOMENCLATURE ET COMPLETE | PART# 80901010000 | SER/LOT# N/A | MANUFACTURER LMMSS |
| Test/Operation MI - MFI | Prevailing Condtion E - ENVIRONMENT | F / U UC | Fail Mode UC - UNSAT | Cause M - MANUFG |
| System ET-COMPLETE | Defect -- | Material -- | Work Contact M. BANKESTER | Fail Date 12/12/1998 |
| Received at MSFC 12/16/1998 | Date Isolated 12/12/1998 | FMEA Reference NONE | IFA: Mission Phase -- | Mission Elapsed Time -- |
| Location MAF | Symptom UC - UNSAT | Time Cycle -- |
| Effectivity Text ET NONE |
| Vehicle Effectivity Codes |
| Vehicle 1 -- | Vehicle 2 -- | Vehicle 3 -- | Vehicle 4 -- | Vehicle 5 -- |
| Mission Effectivity Codes |
| Mssn 1 -- | Mssn 2 -- | Mssn 3 -- | Mssn 4 -- | Mssn 5 -- |
| Estimated Completion Dates |
| MSFC Approved Defer Until Date -- | Contractor Req Defer Until Date 03/30/1999 | LVL 3 Close -- | Remark / Action 03/30/1999 |
| Investigation / Resolution Summary |
| Last MSFC Update 02/02/2001 | CN RSLV SBMT -- | Defer Date -- | Add Date 12/16/1998 | R/C Codes -- -- -- |
| Assignee |
| Design N. OTTE | Chief Engineer J. LUSK | S & MA J. GREEN | Project -- | Project MGR P. COUNTS |
| Approval |
| Design N. OTTE | Chief Engineer J. LUSK | S & MA A. ADAMS | Project -- | Project MGR P. COUNTS |
| PAC Assignee R. TUCKER | PAC Review Complete -- | MSFC Closure Date 05/04/1999 | Status C - CLOSED | F/A Completion -- |
| Problem Type -- | SEV -- | Program Name -- | REVL -- | OPRINC -- |
| FUNC MOD -- | Software Effectivity -- -- -- -- -- | Software Fail CD -- | SUBTYPE -- | Software Closure CD -- |
| RES PERSON L2 -- | Approval Signature L3 -- |
| Related Document Type -- | Related Document ID N/A |
| Related Document Title -- |
| Related Document Type -- | Related Document ID -- |
| Related Document Title -- |
| Related Document Type -- | Related Document ID -- |
| Related Document Title -- |
| Contractor Status Summary |
| Reliability/Quality Assurance Concerns, Recommendations: |
| Problem Description PROBLEM: NOTE: THIS CAPS IS BEING GENERATED PER REQUEST FROM MANAGEMENT AND NASA TO DOCUMENT AND REPORT THE ACTIONS TAKEN TO CLEAR ALL FLIGHT HARDWARE AT APPROXIMATELY 1 A.M. SATURDAY, DECEMBER 12, A SHOP AIR LINE RUPTURED UNDER THE FLOOR IN FRONT OF FINAL ASSEMBLY IN BUILDING 103. THE RESULTING AIR PRESSURE SCATTERED DUST AND SAND FROM AROUND THE LINE OVER A LARGE AREA OF BUILDING 103, INCLUDING FLIGHT HARDWARE AND TOOLING. NO INJURIES WERE REPORTED AS A RESULT, NORMAL ET PRODUCTION HAS BEEN SUSPENDED. A TIGER TEAM HAS BEEN FORMED TO ASSESS THE SITUATION, DETERMINE THE EXTENT OF THE DAMAGE AND RECOMMEND CLEAN-UP ACTIONS THE TEAM IS ALSO CHECKING TO SEE IF ET-102 IN FINAL ASSEMBLY AND COMPONENT HARDWARE IN THE VAB WERE AFFECTED. INITIAL EXAMINATION SUGGESTS THAT THE HARDWARE WAS NOT AFFECTED REV. B, DATED 3/30/99, REVISES TASK I, II AND IV (INDICATED BY AN *) AND CLOSES THIS CAPS |
| Contractor Investigation/Resolution GENERAL: TASK I FAILURE/PROBLEM INVESTIGATION * A. IDENTIFY POTENTIALLY CONTAMINATED FLIGHT HARDWARE LOCATIONS, AND PROVIDE CLEARANCE RATIONALE FOR THOSE FLIGHT HARDWARE LOCATIONS DETERMINED NOT TO BE CONTAMINATED WITHIN THE MAF FACILITY RESPONSIBILITY: R. LEBOUEF/4643 B. MEYER/4640 P. CATARELLA/3050 CLOSED: 1-27-99 CLOSURE STATEMENT O THE TECHNICAL OPERATIONS LAB PERFORMED A CONTAMINATION ANALYSIS OF THE MAF FACILITY (REFERENCE LAB 98A334). THE RESULTS OF THE ANALYSIS ARE OUTLINED IN A MATRIX PER ATTACHMENT 2 OF THIS DOCUMENT. USING THE INFORMATION IN THE DATA MATRIX OF THE SAMPLING AND ANALYSIS PLAN, CONTAMINATION ASSESSMENT MAPS WERE GENERATED OF THE GROUND AND CRANE LEVEL AREAS OF BUILDING 103 PLANT AREA IN ORDER TO ASSESS THE LATERAL AND VERTICAL MIGRATION OF THE AIRBORNE CONTAMINANT DURING THE AIR LINE RUPTURE EVENT. ACCORDING TO THESE CONTAMINATION ASSESSMENT MAPS, THE AIRBORNE CONTAMINANT MATERIAL MIGRATED LATERALLY THROUGHOUT THE MAJOR WELD AREA (WSA-3), THROUGH THE GRAY BOX AREA (WSA-2), AND INTO THE DOME WELD AREA (WSA-1). FINAL ASSEMBLY POSITION 3 WAS ALSO AFFECTED, AS WAS A LOCATION EAST OF THE GRAY BOX, NOT IN THE DOME WELD AREA (COLUMN L-5). THE CONTAMINANT WAS NOT DETECTED IN THE VAB, NOR WAS IT DETECTED IN THE REMAINDER OF THE BUILDING 103 AREAS SOUTH OF THE MAJOR WELD AREA (INCLUDING SOUTH OF D-7, E-7 AND J-7), AND EAST OF THE DOME WELD AREA (P-3 AND EAST) O THE "TIGER TEAM" HAS DIVIDED LOCATIONS WITHIN THE MAF FACILITY INTO THE FOLLOWING CATEGORIES: A) PRODUCTION ACCESS CATEGORY I SEPARATE FROM BUILDING 103 CATEGORY II BUILDINGS ATTACHED TO BUILDING 103 CATEGORY III AREAS WITHIN BUILDING 103 WITH BARRIERS CATEGORY IV GENERAL FACTORY AREA B) INVENTORY C) FACILITY (NON-FLIGHT HARDWARE PRODUCTION OR TOOLING AREAS.) A TOTAL OF NINETY (90) LOCATIONS HAVE BEEN IDENTIFIED WITHIN THE AFOREMENTIONED CATEGORIES REQUIRING A "CLEANING PLAN", WHICH INCLUDES AUTHORIZATION FOR RESTART OF PRODUCTION ACTIVITIES. THE FOLLOWING IS A LIST OF THE IDENTIFIED LOCATIONS (NOTE: ATTACHMENT 1 SHOWS THE NUMBERED LOCATION WITHIN THE MAF FACILITY IN REFERENCE TO WHERE THE ANOMALY OCCURRED.): LOCATION # LOCATION CATEGORY 1 BUILDING 318 I 2 BUILDING 420 I 3 BUILDING 451 I 4 BUILDING 220 I 5 BUILDING 221 I 6 BUILDING 130 I 7 BUILDING 131 I 8 BUILDING 303 I 9 BUILDING 110 VAB II 10 BUILDING 114 HIGHBAY II 11 FINAL ASSEMBLY POS. 1 III 12 FINAL ASSEMBLY POS. 2 III 13 FINAL ASSEMBLY POS. 3 III 14 FINAL ASSEMBLY POS. 4 III 15 H13 CLEAN ROOM III 16 K4 CLEAN LINE III 17 F13 SOFI SHOP III 18 D18 SOUTH MEZZ. HARNESS FAB. III 19 K4 PAINT BOOTH III 20 VALVE SHOP III 21 J15 TUBE SHOP III 22 L14 METROLOGY III 23 F19 WELD LAB III 24 L15 MACHINE LAB III 25 L15 METALOGRAPHY TEST LAB III 26 L14 TEST VERIFICATION LAB III 27 D8 CELL Q-SPRAY BOOTH III 28 J17 COMMODITY SHOP INSP. III 29 L7 X-RAY III 30 WSA I-DOMES IV 31 WSA II-BARRELS/OGIVES IV 32 WSA III-MAJOR WELD(WEST) IV 33 WSA III-MAJOR WELD(EAST) IV 34 WSA III-MAJOR WELD(FAR EAST) IV 35 WSA IV-WIDE PANEL IV 36 R3 DOME MECHANICAL IV 37 N4 I/T ASSEMBLY IV 38 M4 FRAME MECH. SUBASSEMBLY IV 39 F5 BARREL/TANK MECHANICAL IV 40 N3 BAFFLE/RINGS/X-BEAM IV 41 CROSSBEAM ASSEMBLY (7020) IV 42 MACHINE SHOP/HT/SHEET METAL IV 43 PROOFLOAD EAST/WEST IV 44 D5 F/A TOOLING STORAGE IV 45 A5 I/T POSITION 3 STA.-1 IV 46 A5 I/T POSITION 3 STA.-2 IV 47 E11 GUN ROOM TPS IV 48 P13 TOOL FAB./MAINTENANCE IV 49 N13 TOOLING ELECTRICAL IV 50 L4 RING WELD/X-BEAM WELD IV 51 N3 WSA 1 DOME REPAIR IV 52 S2 TOOLING WELD SHOP IV 53 S2 TECH. OPS. TEST SAMPLE STG. IV 54 A4 THRU AISLE IV 55 F8 ROLLRING INST./STAGING AREA IV 56 P8 TOOLING QC INSP. IV 57 J17 COMMODITY SHOP INSP. CRIB IV 58 F18 TECH OPS MACHINE SHOP IV 59 S. MEZZ. J16 TPS TRAINING LAB IV 60 S. MEZZ. H16 WELD/RIVET TRAIN. IV 61 GEMCORE/ASRM AREA IV 62 E6 ET TOOL MAINTENANCE IV 63 P15-S-18 FLIGHT INVENTORY 64 P3 FLIGHT INVENTORY 65 M-6 TOOL CRIB INVENTORY 66 J-18 RAW MATERIAL INVENTORY 67 L10 TOOLING INVENTORY 68 K-17 TOOL CRIB ANNEX INVENTORY 69 L-2 FLIGHT INVENTORY 70 K-10 FLIGHT INVENTORY 71 F/A TOOL CRIB INVENTORY 72 D8 VAB SUPPORT STAGE INVENTORY 73 M-18 FLIGHT (COOLER) INVENTORY 74 K-16 CENTRAL TOOL CRIB INVENTORY 75 K-17 RESERVE TOOL CRIB INVENTORY 76 B2 LCC-5 INVENTORY CRIB INVENTORY 77 D18 LCC-3 INVENTORY CRIB INVENTORY 78 F8 RAW MATERIAL DOME STORAGE INVENTORY 79 N7 LCC 1 MECHANICAL CRIB INVENTORY 80 M6 MECHANICAL TOOL CRIB INVENTORY 81 H7 TOOL KITING CRIB INVENTORY 82 C2 FASTENER TOOL CRIB INVENTORY 83 Q3 STORAGE CRIB INVENTORY 84 H8 QC CRIB INVENTORY 85 M10 MRB CRIB INVENTORY 86 D17 PA NDT SUPPORT STORAGE INVENTORY 87 H10 LCC1 WIP STORAGE INVENTORY 88 H11 CLEANROOM CRIB INVENTORY 89 E7 LCC4 (ADJACENT TO PL EAST) INVENTORY 90 M8 BULK STOCK ALL NINETY (90) LOCATIONS HAVE BEEN ADDRESSED BY A SPECIFIC CLEANING PLAN DESIGNATED FOR EACH LOCATION, AND RECEIVED FINAL APPROVAL BEFORE PRODUCTION PROCESSING WAS INITIATED (SEE ACTION ITEM "D" FOR THE "CLEANING PLAN"). ALL APPROVED CLEANING PLANS FOR EACH LOCATION WITH THE "RATIONALE FOR RESUMPTION" ARE ON FILE (CAPS S-080) IN RELIABILITY ASSURANCE, DEPT. 3741. REFERENCE ATTACHMENT 4 FOR THE FLOW CHART WHICH OUTLINED THE PROCESS FOR ESTABLISHING CLEARANCE OF EACH PRODUCTION AND SUPPORT AREA B. IDENTIFY THE EFFECTS OF THE FOREIGN OBJECT DEBRIS (FOD) ON FLIGHT HARDWARE RESPONSIBILITY: R. LEBOUEF/4643 B. MEYER/4640 M. CAMPBELL/4630 P. HINKELDEY/4600 CLOSED: 1-29-99 CLOSURE STATEMENT A MAF RESTART VERIFICATION PLAN WAS ESTABLISHED TO ENSURE THAT THE INTRUSION OF SAND AND DEBRIS THROUGHOUT THE FACILITY DOES NOT AFFECT FURTHER PROCESSING OF FLIGHT HARDWARE. THE FOLLOWING TEST PLANS WERE ESTABLISHED AND THE NUMBERS FOR EACH PLAN ARE LISTED FOR REFERENCE OF ALL TEST DATA: O ETTP-608 (VERIFICATION OF SAND REMOVAL FROM AIR LINE RUPTURE AS AFFECTING FURTHER PROCESSING) - TESTING IS COMPLETE. STANDARD METAL FINISHING PROCESSES (CLEANING, CHEM-FILM OR EPOXY PRIMER APPLICATION) ARE NOT EFFECTED BY THE CLEANUP METHOD USED TO REMOVE SAND FROM THE FLIGHT HARDWARE O ETTP-610 (NORMAL WELD PREPARATION ADEQUACY TEST) - REMOVING THE GROSS CONTAMINANT BY VACUUMING AND IPA WIPING FROM THE AREA FACILITY, PRODUCTION EQUIPMENT AND PRODUCTION HARDWARE IS IN PROGRESS. HOWEVER, IN PRODUCING ALUMINUM TANKS FOR FLIGHT, MANY OF THE METAL FINISHING AND WELDING OPERATIONS REQUIRE SURFACES FREE OF CONTAMINANT SURFACE CLEANING PROCEDURES ARE GOVERNED BY STANDARD ENGINEERING SPECIFICATIONS WHICH ARE EMPLOYED IN NORMAL FINISHING AND WELDING OPERATIONS. TESTING HAS SHOWN THAT FOR INITIAL WELDS, WELDS IN PROGRESS AND THE REPAIR WELDS THAT WERE COVERED WITH THE DECEMBER 12TH CONTAMINANT, THE CURRENT WELD SURFACE PREPARATION PROCEDURES USED WILL ENSURE CLEAN SURFACES PRODUCING VIABLE WELDS. BY FOLLOWING NORMAL WELD PREPARATION PRACTICES, PRODUCTION WELDING OPERATIONS CAN RESUME O ETTP-611 (VERIFICATION TESTING FOR SOFI, SLA, ADHESIVE BONDING TO PRIMED SURFACES) - DUST CONTAMINATION RESULTING FROM THE AIRLINE RUPTURE WHICH WAS SUBSEQUENTLY CLEANED FROM THE CURED PRIMED SURFACES USING EXISTING APPROVED MATERIALS AND PROCESSES, DID NOT IMPACT THE TPS AND WIRE BOND ADHESION PERFORMANCE STUDIED IN THIS TEST O EXTENDED ASSESSMENT OF PARTICULATE DEBRIS RESULTANT FROM SHOP AIR LINE RUPTURE - (REFERENCE LAB 98A336) CURRENT TOTAL SUSPENDED PARTICULATE (TSP) DATA FOR THE WSA-1 DOME WELD AREA HAS EXCEEDED THE UPPER CONTROL LIMIT OF THE HISTORICAL BASELINE DATA TWICE SINCE LABORATORY OPERATIONS BEGAN HIGH VOLUME AIR SAMPLING AFTER THE AIR LINE RUPTURE INCIDENT. THESE EXCURSIONS OCCURRED ON 12/15/98 AND 1/6/99. WHENEVER THE TSP LEVELS IN A SAMPLE AREA EXCEEDED THESE CONTROL LIMITS, WORKERS AND SUPERVISION WERE QUESTIONED AS TO WHAT SPECIFIC WORK ACTIVITY TOOK PLACE DURING THAT PERIOD OF TIME. A WORK ACTIVITY LOG WAS MAINTAINED FOR EACH AREA FOR PROBABLE SPECIAL CAUSES THAT MAY HAVE TAKEN PLACE DURING THE SAMPLE PERIOD. THE WORK ACTIVITY LOG ENTRY ON 12/15/98 INDICATED THAT CLEANING ACTIVITY WAS BEING PERFORMED ON THE OVERHEAD CRANE RAILS DURING THIS SAMPLE PERIOD. ON 1/6/99, THE WSA-1 AREA PROBABLE SPECIAL CAUSE IS THE MOVING OF THE DOME IN THE T01A5005 FIXTURE. THE DOME WAS ALSO CLEANED WITH COMPRESSED AIR, AND GRINDING WORK WAS PERFORMED ON A NEARBY TOOL WITH WIRE WHEELS ATTACHED TO DRILL MOTORS ON 1/6/99, THE WSA-II PROBABLE SPECIAL CAUSE IS THE EXTENSIVE CLEANING AND VACUUMING OF THE AREA ABOVE THE SAMPLER AND ON THE WALLS. ON 1/8/99 MORE CLEANING ACTIVITY WAS PERFORMED WITH THE FLOOR BEING VACUUMED AND WAXED NEAR THE SAMPLE AREA THE PROBABLE SPECIAL CAUSE IN FINAL ASSEMBLY POSITION 3 FOR 12/27/98 IS THE CLEANUP OF THE GENERAL AREA BY FINAL ASSEMBLY PERSONNEL. DURING THE SAMPLE PERIOD OF 1/6/99, WORK CREWS IN FINAL ASSEMBLY USED COMPRESSED AIR TO CLEAN THE WORK PLATFORMS AND STANDS THAT SURROUNDED THE ET IN ORDER TO BLOW THE DUST FROM THE PLATFORMS. ON 1/8/99 WORKERS IN THE FINAL STAGES OF CLEANING WERE SWEEPING WITH PUSH BROOMS AND THEREBY PRODUCING AIRBORNE PARTICULATE THE CURRENT HIGH VOLUME SAMPLE DATA FROM THE WSA-III MAJOR WELD AREA, AND FROM THE VAB AISLE DID NOT EXCEED THE HISTORICAL DATA UPPER CONTROL LIMITS WITH THESE EXCEPTIONS, THE CURRENT AIR QUALITY DATA SHOWS THAT THE TSP LEVELS FOR THE BUILDING 103 WELD AREAS AND THE VAB WERE WITHIN THE CONTROL LIMITS OF THE HISTORICAL BASELINE DATA. THE DATA INDICATE THAT THE PLANT HAS NOT SUSTAINED ANY LONG TERM AIR QUALITY PROBLEMS AS A RESULT OF THE AIR LINE RUPTURE INCIDENT AND THE EXTENSIVE CLEANUP PROJECT THEREAFTER O PER A BROWN BOOK (TERRY HIBBARD) ACTION ITEM, A QUESTION AS TO WHY CRYO TESTS ARE NOT BEING PERFORMED WHEN ASSESSING THE PARTICULATE CONTAMINATION OF THE FACTORY WAS RAISED. THE FOLLOWING RATIONALE WAS PROVIDED BY TECHNICAL OPERATIONS (R. PONTIFF): THE PARTICULATE THAT WAS GENERATED IS WELL DEFINED. IT IS NOT HYGOSCOPIC AND IT IS NOT VERY REACTIVE. THE PARTICULATE IS EASILY REMOVED THROUGH VACUUMING OR WIPING THIS TYPE OF PARTICULATE IN SUFFICIENT QUANTITIES IS KNOWN TO PRODUCE WELDABILITY ISSUES AND NDE DETECTABLE DEFECTS LONG BEFORE WELD STRENGTH PROPERTIES ARE AFFECTED. THE FACT THAT THERE WERE NO NDE INDICATIONS IN THE WELD TEST PANELS SUPPORTS THE CONCLUSION THAT THE WELD PREPARATION PROCESS IS SUFFICIENT TO ASSURE A GOOD WELD AGAIN THE PARTICULATE IS NOT REACTIVE WITH OUR COATING SYSTEMS (CHEM-FILM AND PRIMER). ONE CONCERN IS THAT IF SUFFICIENT PARTICULATE WAS PRESENT THE COATING WOULD BOND TO THE SAND AND NOT THE SUBSTRATE. EVEN THOUGH THERE ARE SOME CRYO-TESTING POSSIBLE TO TEST THE COATING SYSTEMS, THEY ARE NOT STANDARD PRIMER ACCEPTANCE TESTS. THE WET-TAPE TEST FOR PRIMER IS CONSIDERED ONE OF THE MOST CONSERVATIVE TESTS THAT A PRIMER SYSTEM CAN BE SUBJECTED TO. IT SHOULD ALSO BE NOTED THAT GRIT-BLASTING USED TO PREPARE SOME ET PARTS LEAVES A SIMILAR PARTICULATE ON THE PART. OUR IN-PROCESS PREPARATION FOR PRIMING HAS BEEN SUFFICIENT TO REMOVE THIS TYPE OF PARTICULATE THE PARTICULATE IS NOT REACTIVE WITH OUR TPS AND TPS BONDING SYSTEMS. A CONCERN IS THAT IF SUFFICIENT PARTICULATE WAS PRESENT THE SYSTEMS WOULD BOND TO THE SAND AND NOT THE SUBSTRATE. THIS BONDING CONCERN IS DRIVEN BY A PHYSICAL ISSUE AS OPPOSED TO A CHEMICAL ISSUE AND IT IS FELT THAT ROOM TEMPERATURE ADHESIVE TESTING WOULD BE MORE THAN ADEQUATE IN DETERMINING WHETHER OR NOT DEGRADATION HAD OCCURRED THE TEST PLANS AND THE CRITERIA FOR SUCCESS HAVE BEEN CONCURRED WITH BY THE APPROPRIATE TECHNICAL AND QUALITY PARTIES INCLUDING NASA/MSFC * C. DIVIDE THE MAF FACILITY INTO QUADRANTS AND IDENTIFY ALL FLIGHT HARDWARE CLEANED AND LOCATED WITHIN THE CONTAMINATED AREAS AS ADDRESSED IN ACTION ITEM "A" RESPONSIBILITY: M. BANKESTER-3741 D. WESTPHAL-3700 J. STANLEY-3630/M. JAVERY-3600 COMPLETE: 3-29-98 CLOSURE STATEMENT ALL FLIGHT HARDWARE CLEANED AS A RESULT OF THE AIR LINE RUPTURE INCIDENT HAS BEEN DOCUMENTED ON ATTACHMENT 3. THE MATRIX IDENTIFIES THE PART NUMBER, THE SERIAL NUMBER (WHEN APPLICABLE), EFFECTIVITY, LOCATION, AUTHORIZATION DOCUMENT AND BUYOFF STAMPS D. DETERMINE AND ESTABLISH THE CLEANING PROCESS FOR THE MAF FACILITY, FACILITY EQUIPMENT, FLIGHT HARDWARE TOOLING AND FLIGHT HARDWARE RESPONSIBILITY: J. STANLEY-3630 M. CAMPBELL/4630 P. HINKELDEY/4600 CLOSED: 12-16-98 CLOSURE STATEMENT THE "INTEGRATED FACTORY RESTART TEAM" HAS ESTABLISHED THE FOLLOWING GENERAL CLEANING PROCESS, WHICH HAS BEEN APPROVED BY NASA, PRODUCTION OPERATIONS, PRODUCT ASSURANCE TECHNICAL OPERATIONS AND FACILITIES. EACH DESIGNATED AREA (SEE ACTION A) WILL BE CLEARED VIA "WALK DOWN" AND SIGNATURE OF APPROVAL BY A REPRESENTATIVE OF NASA, PRODUCTION OPERATIONS, TECHNICAL OPERATIONS AND PRODUCT ASSURANCE: FACTORY ASSESSMENT AND CLEANING O CRANES AND BRIDGES - ASSESS AREA AND COVER HARDWARE/TOOLING AS REQ'D - GENERALLY CLEAN BRIDGE AND TROLLEY - VACUUM - DRY/WET WIPE AS REQ'D INTO VACUUM SYSTEM - ASSESS RESULTS AND REPEAT IF NECESSARY O DUCTS/TRUSSES/PURLINGS - GENERALLY CLEAN TO FLOOR LEVEL ALONG WALLS VACUUM/WIPE INTO VACUUM SYSTEM O UNLOADED TOOLING/EQUIPMENT - GENERALLY CLEAN STRUCTURES TOP DOWN > VACUUM > WET WIPE WITH IPA OR MEK OR WATER OR WINDEX - POWER DOWN ANY VENTED CABINETS PER W/A - GENERALLY CLEAN INSIDE AND OUT > INSIDE/VACUUM/INERT GAS > OUTSIDE VACUUM/WIPE - CLEAN/REPLACE FILTERS/ELEMENTS/FANS ETC - PERFORM GENERAL VACUUM/WIPE OF PERIPHERAL WIRING/KEYBOARDS/SCREENS ETC - POLY WRAP OR SEAL NON-NEMA-4 ENCLOSURES NOTE VERIFICATION OF TOOL FUNCTIONALITY/ PM OF PURGE SYSTEM WILL BE ACCOMPLISHED PRIOR TO RESUMPTION OF MANUFACTURING O LOADED TOOLING - UNLOAD IF POSSIBLE - GENERALLY CLEAN STRUCTURES AND LOADED PANELS TOP DOWN > VACUUM > DAMP WIPE (NO WATER) MANDATORY - IPA/MEK - EVALUATE TOOL STATUS FOR POWER UP/DOWN CAPABILITY PRIOR TO REMOVING POWER > GENERATE W/A - POWER DOWN OK > GENERALLY CLEAN VENTED ENCLOSURES - VACUUM/INERT GAS > CLEAN/REPLACE FILTERS/ELEMENTS > WRAP/SEAL ENCLOSURES - POWER PROHIBITED > GENERALLY CLEAN ACCESSIBLE AREAS > PERFORM VENTED ENCLOSURE CLEANING AFTER TOOL IS UNLOADED > CLEAN ANY AREAS THAT WERE INACCESSIBLE DUE TO LOADED HARDWARE O FACILITIES - WELD EQUIPMENT > REPLACE WIRE SPOOLS > PRODUCTION DISPOSE OF OLD WELD WIRE PER PROCEDURE > VACUUM/WIPE EQUIPMENT/WIRING/KEYBOARDS ETC > REPLACE FILTERS/ELEMENTS (PM CYCLE) > SEAL/WRAP AS REQ'D > CLEAN TORCHES NOTE: EQUIPMENT VERIFICATION WILL BE PERFORMED PRIOR TO RESUMPTION OF MANUFACTURING - OTHER EQUIPMENT > VACUUM/WIPE ALL EQUIPMENT, WIRING, KEYBOARDS, SCREENS ETC. (GENERAL PM) > REPLACE FILTERS/SCREENS ETC SEAL/WRAP AS REQ'D O MOBILE EQUIPMENT - ALL MOBILE EQUIPMENT INSIDE BLDG. 103 DURING INCIDENT MUST BE WIPED DOWN PRIOR TO USE (FORKLIFTS, GIRAFFES, ETC.) - VACUUM /WIPE DOWN ALL SCISSORS LIFTS - VACUUM /WIPE DOWN LOADED DOLLIES - MOVE ALL UNLOADED DOLLIES TO DESIGNATED AREA (PKG LOT 'F') AND CLEAN - WIPE DOWN ALL SLINGS/SPREADER BARS, ETC O SMALL SUPPORT TOOLING - GENERALLY CLEAN EXPOSED TOOLING - EMPHASIZE VIA CREW BRIEFINGS NEED TO CONFORM TO STANDARD CLEANING OF ITEM PRIOR TO USE O FLOOR - VACUUM/MOP FLOORS IN ALL AREAS ZAMPBONI MAIN AISLES O FLIGHT HARDWARE - DOCUMENT P/N AND S/N AND EFFECTIVITY IF APPLICABLE ON PAWS - CLEAN HARDWARE PER APPROVED CLEANING PROCEDURE(S) TO OBTAIN VISUAL O OTHER ISSUES - QUANTITY OF IPA/MEK MAY REQUIRE AIR PERMIT - RESPIRATOR CERTS, ETC WITH LARGE QUANTITY OF SOLVENTS - DISCARD ALL EXPOSED CONSUMABLES O RYMPLE CLOTH, ETC - SUFFICIENT QUANTITY OF PPE'S AND CLEANING SUPPLIES DISPOSAL OF RIMPLE CLOTH IN MASSIVE QUANTITIES AS HAZARDOUS WASTE GENERAL GROUNDRULES O NO PLANS TO CLEAN BELOW FLOOR LEVEL O CONDUCT CREW BRIEFINGS TO ENSURE THAT ALL PERSONNEL UNDERSTAND THE CRITICALITY OF CLEANING AND PROPER METHODOLOGY O NEED ACCESS CONTROL IN ALL MAJOR AREAS TO PREVENT ENTRY/OPENING MAJOR DOORWAYS WITHOUT AUTHORIZATION TO MINIMIZE RECONTAMINATION O PROCEED CLEANING TOP-TO-BOTTOM IN EACH SPECIFIC AREA O NO AIR GUNS WILL BE USED DURING THIS EFFORT O ASSUME ALL EQUIPMENT/TOOLING STORED OUTSIDE IS ACCEPTABLE UNDER NORMAL USE CONDITIONS E. PROVIDE A SCHEDULE FOR THE CLEANING IMPLEMENTATION PLAN, AND ENSURE THAT ALL "CLEANED" HARDWARE MOVES TO "CLEAN" AREAS RESPONSIBILITY: J. STANLEY- 3630 B. MAGENDIE-3652 D. WROBEL-3650 CLOSED: 1-18-99 CLOSURE STATEMENT O REFERENCE ATTACHMENT 5 FOR THE SCHEDULE PROVIDED BY THE TIGER TEAM TITLED MAF FACILITIES RESTART AND REACTIVATION PLAN. NO PRODUCTION PROCESSING IS ALLOWED IN ANY AREA UNTIL APPROVAL OF THE "CLEANING PLAN" O PRECAUTIONS HAVE BEEN INCORPORATED TO MINIMIZE THE POSSIBILITY OF ANY DUST FROM THE INSTALLATION OF INTERTANK RIVETER FOUNDATIONS AND UTILITIES PROJECTS, AND ONGOING FACILITY CONSTRUCTION FROM CONTAMINATING PRODUCTION AREAS: - MINIMIZE THE QUANTITY OF BACK FILL MATERIAL STORED AT THE JOB SITE - COVER BACK FILL MATERIAL WITH VISQUEEN - USE FLOOR SWEEP WHENEVER SWEEPING AREA - WET DOWN BACK FILL MATERIAL BEFORE MOVING * F. DETERMINE ROOT CAUSE FOR THE REPORTED DISCREPANCY RESPONSIBILITY: D. SWORDS 3160 R. ABADIE-3100 CLOSED: 1-12-99 CLOSURE STATEMENT CAUSE FOR THE RUPTURED AIR LINE WAS CORROSION OF AN UNCOATED 2 INCH, SCREW PIPE "TEE" FITTING LOCATED APPROXIMATELY 16 INCHES UNDER THE EXISTING FLOOR SLAB O TECHNICAL OPERATIONS ANALYSIS REVEALED THAT THE PRIMARY CAUSE OF THE CORROSION WAS DETERMINED TO BE ELECTROLYSIS BETWEEN THE SHELLS, SAND, AND METAL COMPONENTS NOTE: REFERENCE FACILITIES ENGINEERING PRESENTATION, ASSESSMENT & CORRECTIVE ACTION OF PLANT AIR INCIDENT FOR FURTHER DISCUSSION OF CAUSE CAUSE REFERENCE TASK I, F FOR CAUSE DETERMINATION TASK II CORRECTIVE ACTION * CLEANED AND DOCUMENTED ALL FLIGHT HARDWARE IDENTIFIED IN POTENTIALLY CONTAMINATED AREAS THROUGHOUT THE MAF FACILITY * CORRECTIVE ACTIONS TAKEN TO ADDRESS THE MAF FACILITY HAVE BEEN DOCUMENTED PER A FACILITIES DEPARTMENT INVESTIGATION TITLED "ASSESSMENT & CORRECTIVE ACTION OF PLANT AIR " INCIDENT", PREPARED BY DAN SWORDS OF FACILITIES ENGINEERING A PRESENTATION WAS PROVIDED TO NASA (PARKER COUNTS) BY FACILITIES ENGINEERING ADDRESSING THIS ISSUE ON 1/13/99 TASK III CLEARANCE OF EFFECTIVITIES ET-99 AND ET-100; THESE ETS WERE DELIVERED AND WERE NOT AT THE MAF FACILITY AT THE TIME THE INCIDENT OCCURRED. NO RISK TO FLIGHT HARDWARE ALL FLIGHT HARDWARE PRESENTLY AT MAF AND DESIGNATED AS POTENTIALLY CONTAMINATED, HAS BEEN CLEANED PER DIRECTION AND AUTHORIZATION OF THE "TIGER TEAM", AND CLEARED FOR FLIGHT TASK IV CAPS CLOSURE SUMMARY * AT APPROXIMATELY 1 A.M. SATURDAY, DECEMBER 12, A SHOP AIR LINE RUPTURED UNDER THE FLOOR IN FRONT OF FINAL ASSEMBLY IN BUILDING 103. THE RESULTING AIR PRESSURE SCATTERED DUST AND SAND FROM AROUND THE LINE OVER A LARGE AREA OF BUILDING 103, INCLUDING FLIGHT HARDWARE AND TOOLING. NO INJURIES WERE REPORTED. SAMPLES WERE TAKEN THROUGHOUT THE FACILITY BY THE TECHNICAL OPERATIONS LAB TO DETERMINE WHICH AREAS WERE POTENTIALLY CONTAMINATED. A "TIGER TEAM" INVESTIGATION ENSUED, AND CLEANING PLANS WERE INITIATED TO RETURN THE MAF FACILITY TO PRODUCTION PROCESSING. ALL DESIGNATED AREAS THROUGHOUT THE MAF FACILITY CLEANED PER THE CLEANING PLANS, RECEIVED FINAL APPROVAL FROM THE "TIGER TEAM" INCLUDING CUSTOMER AUTHORIZATION FOR PRODUCTION RESTART. ALL FLIGHT HARDWARE IDENTIFIED IN THE AREAS REQUIRING A CLEANING PLAN WAS DOCUMENTED ON AN ATTACHED MATRIX BY PART NUMBER. A MAF RESTART VERIFICATION PLAN WAS ESTABLISHED TO ENSURE THAT THE INTRUSION OF SAND AND DEBRIS THROUGHOUT THE FACILITY DOES NOT AFFECT FURTHER PROCESSING OF FLIGHT HARDWARE. THE FOLLOWING TESTS WERE PERFORMED: O VERIFICATION OF SAND REMOVAL FROM AIR LINE RUPTURE AS AFFECTING FURTHER PROCESSING O NORMAL WELD PREPARATION ADEQUACY TEST O VERIFICATION TESTING FOR SOFI, SLA, ADHESIVE BONDING TO PRIMED SURFACES O EXTENDED ASSESSMENT OF PARTICULATE DEBRIS RESULTANT FROM SHOP AIR LINE RUPTURE ALL TESTS WERE ACCEPTABLE AND PRODUCTION PROCESSING CONTINUED CAUSE FOR THE RUPTURED AIR LINE WAS CORROSION OF AN UNCOATED 2 INCH, SCREW PIPE "TEE" FITTING LOCATED APPROXIMATELY 16 INCHES UNDER THE EXISTING FLOOR SLAB. TECHNICAL OPERATIONS ANALYSIS REVEALED THAT THE PRIMARY CAUSE OF THE CORROSION WAS DETERMINED TO BE ELECTROLYSIS BETWEEN THE SHELLS, SAND, AND METAL COMPONENTS. ALL ET-99 AND SUBSEQUENT FLIGHT HARDWARE IDENTIFIED AS POTENTIALLY CONTAMINATED, HAS BEEN CLEANED AND CLEARED FOR FLIGHT. CORRECTIVE ACTIONS TAKEN TO ADDRESS THE MAF FACILITY HAVE BEEN DOCUMENTED PER A FACILITIES DEPARTMENT INVESTIGATION TITLED "ASSESSMENT & CORRECTIVE ACTION OF PLANT AIR INCIDENT" THIS CAPS IS CLOSED. NO FURTHER ACTION REQUIRED |
| MSFC Response/Concurrence 05/04/99 - MSFC CONCURS WITH CLOSURE |

MSFC Problem Reporting and Corrective Action (PRACA) System

ASSESSMENT ADDENDUM REPORT

| MSFC Report# A17352 | IFA# -- | Contractor RPT# S-080 | JSC# -- | KSC# -- | EICN# -- |
| --- | --- | --- | --- | --- | --- |
| Asmnt Part# 80901010000 | Asmnt Part Name ET COMPLETE | Asmnt Serial/Lot# -- |
| HCRIT CD -- | FCRIT CD 3 | CAUSE CD M - MANUFG | FAIL MODE UC - UNSAT |
| Asmnt FMEA N/A | Asmnt FM N/A | FMEA CSE -- | FMEA SCSE -- |
| Asmnt FMEA -- | Asmnt FM -- | FMEA CSE -- | FMEA SCSE -- |
| Asmnt FMEA -- | Asmnt FM -- | FMEA CSE -- | FMEA SCSE -- |
| Correlated Part# -- | Correlated Part# -- | Correlated Part# -- |
| Associated LRU# -- | Associated LRU# -- | Associated LRU# -- |
| MAJOR DESIGN CHANGES |
| APRV DATE -- | DESCRIPTION OF CHANGES -- |
| ASSESSMENT TEXT |