Project Number:  AW-2271

Contract Number:  TW-0663

November 4, 1994

SPECIAL SPECIFICATION

SECTION 04221

CONCRETE MASONRY

Page

PART 1 - GENERAL

1.01	Description Of Work	1

1.02	Delivery, Storage And Handling	1

1.03	Submittals	1

1.04	Job Conditions	2

PART 2 - PRODUCTS

2.01	Materials, General	2

2.02	Concrete Masonry Units (CMU)	3

2.03	Mortar	3

2.05	Grout	4

2.06	Masonry Accessories	5

PART 3 - EXECUTION

3.01	Inspection	6

3.02	Placing Reinforcement	6

3.03	Installation	6

3.04	Grouting	8

3.05	Repair, Pointing, And Cleaning, And Waterproofing	9

SPECIAL SPECIFICATION

SECTION 04221

CONCRETE MASONRY

PART 1 - GENERAL

1.01	DESCRIPTION OF WORK

A.	Extent of Work:  The extent of each type of unit masonry work is shown on the drawings and in schedules and specifications.

B.	Related Work:  Building insulation.

1.02	DELIVERY, STORAGE AND HANDLING

A.	Delivery:  Deliver masonry materials to project in undamaged condition.

B.	Storage:  Store and handle masonry products to prevent their deterioration or damage due to moisture, temperature changes, etc.

1.	Limit moisture absorption of CMU during delivery and until time of installation to the maximum percentage specified for Type I units.

2.	Store cementitious materials off the ground, under a covering in a dry location.

3.	Store masonry accessories including metal items to prevent deterioration by corrosion and accumulation of dirt.

1.03	SUBMITTALS

A.	Provide written certification that products to be used meet or exceed the requirements stated in this specification and that materials to be used on this project meet the fire performance characteristics stated.

Provide manufacturer's written certification as to the hourly fire resistance rating of the material, referencing testing laboratories results where applicable.

B.	Provide manufacturer's specifications and product data for all masonry materials and accessories.

C.	Provide steel producers certificates of mill tests for all reinforcing.

D.	Provide mortar color samples or charts for mortar color selection.

1.04	JOB CONDITIONS

A.	General:  Protect newly laid masonry from exposure to precipitation, excessive drying, freezing, soiling, backfill, and other harmful elements.

At the end of each day's work and whenever there is perceptible rain or drizzle, the tops and upper 2 feet on both sides of all masonry work except floors shall be protected and kept protected by rain-and-windproof, well-anchored covering such as heavy polyethylene or tarpaulins.  Such protection shall be continued until the masonry receives its permanent structural or other top/covering per design.

B.	Staining:  Prevent grout or mortar from staining the face of masonry to be left exposed or painted.  Immediately remove grout or mortar in contact with such masonry.  Protect sills, ledges and projections from droppings of mortar.

C.	Cold Weather Protection:

1.	Remove any ice or snow formed on masonry bed by carefully applying heat until top surface is dry to the touch.  Remove all masonry determined to be frozen or damaged by freezing conditions.

2.	Do not erect masonry when the ambient temperature is below 32 degrees F on a rising temperature or below 40 degrees F on a falling temperature unless special provisions are made for heating the materials and protecting the work.

D.	Hot Weather Protection:  Protect masonry construction from direct exposure to wind and sun when erected in an ambient air temperature of 90 degrees F (32 degrees C) or greater in the shade, with relative humidity less than 50%, or when the relative humidity is less than 40% at any temperature, for at least 24 hours.

PART 2 - PRODUCTS

2.01	MATERIALS, GENERAL

All materials used shall not contain asbestos fibers.

2.02	CONCRETE MASONRY UNITS (CMU)

A.	Manufacturer:  Obtain masonry units from one manufacturer, of uniform texture and color for each kind required for each continuous area and visually related area.

B.	Fire Performance Characteristics:  Where indicated, provide materials and construction to meet fire resistance stated, which are identical to those of assemblies whose fire endurance has been determined by testing in compliance with ASTM E119.

C.	Size and Standards:  Manufacturer's standard load bearing units with nominal face dimensions of 16" long x 8" high (15- 5/8" x 7- 5/8"), unless otherwise shown.

1.	Standard, plain, normal weight, uncolored units unless shown otherwise.

2.	Use 8 split/flute 4 inches thick and 8 inches thick block, as shown on the drawings, with red scoria aggregate and 1-1/4 inch projecting flutes.

3.	All block to be per latest revision of ASTM C90, Grade N, Type 1.

D.	Special Shapes:  Provide where required for lintels, corners, jambs, sash, control joints, headers, bonding, and other special conditions.

2.03	MORTAR

A.	General:  Under no conditions shall air entrainment be used in mortar.  Under no conditions shall masonry cement be used for mortar.

B.	Portland Cement:  ASTM C150, Type I, except Type III may be used for cold weather construction.

C.	Hydrated Lime:  ASTM C207, Type S.

D.	Water:  Clean and potable.

E.	Sand:  ASTM C144.

F.	Type:  Mortar mix proportions per ASTM C270:

1.	Walls Below Grade:  Type M, 1/4 lime to 1 Portland cement, 2500 psi compressive strength.

2.	Exterior Walls Above Grade:  Type S, 1/4 to 1/2 lime to 1 Portland cement, 1800 psi.

3.	Interior Load Bearing Walls:  Type S.

4.	Interior Non-load bearing Partitions:  Type S or Type N, 1/2 to 1-1/4 lime to 1 Portland cement, 750 psi.

5.	Do not add admixtures unless otherwise indicated.

2.05	GROUT

A.	Portland Cement:  ASTM C150, Type I.

B.	Hydrated Lime:  ASTM C207, Type S.

C.	Water:  Clean and potable.

D.	Aggregate:ASTM C404, coarse aggregate size No. 8 and fine aggregate size No. 1.

E.	Proportions:  2000 psi compressive strength.

1 part Portland cement

1/10 part hydrated lime

3 parts sand

2 parts coarse aggregate

Do not add admixtures unless otherwise indicated.

F.	Color:  Natural gray.

2.06	MASONRY ACCESSORIES

A.	Horizontal Joint Reinforcement:

1.	Where indicated, install welded wire units prefabricated in straight lengths of not less than 10 feet, with matching corner and tee units.  Fabricate from cold-drawn steel wire complying with ASTM A82, with deformed continuous side rods and plain cross-rods, and a unit width of 1-1/2  to 2 inches less than thickness of wall or partition.

2.	Where indicated, install truss type fabricated with single pair of 9 gauge side rods and 9 gauge continuous diagonal cross-rods spaced not more than 16 inches o.c. (unless otherwise detailed on the drawings).

3.	For interior walls, fabricated from mill galvanized wire.

4.	For exterior walls, hot-dip galvanized after fabrication with 0.8 oz. zinc coating, ASTM A116, Class 3.

B.	Reinforcing Bars:  Deformed steel, ASTM A615, Grade 60 of the sizes shown or indicated on the drawings.  Shop fabricate and bend bars which are shown to be bent or hooked.

C.	Anchoring Devices for Masonry:  Provide straps, bars, bolts and rods fabricated from not less than 16 gauge sheet metal or 3/8-inch diameter rod stock, unless otherwise indicated.

D.	Miscellaneous Masonry Accessories:

1.	Nonmetallic Expansion Joint Strips:  Provide premolded, compressible, elastic fillers of foam rubber, or neoprene, complying with ASTM D1056, Grade RE41E1 capable of compression up to 35% of width.

2.	Premolded Control Joint Strips:  Solid rubber strips with a Shore A durometer hardness of 60 to 80, designed to fit standard sash block and maintain lateral stability in masonry wall, size and configuration as indicated.

3.	Weep Holes:  Install medium density polyethylene 1/4 inch diameter x 4 inch long tubes as weep holes where indicated.

4.	Waterproofing:  Provide "Prime-a-Pell 200" one coat water repellent on all exterior exposed CMU.

PART 3 - EXECUTION

3.01	INSPECTION

Masonry installer must examine the areas and conditions under which masonry is to be installed and notify the Inspector of conditions detrimental to the proper and timely completion of the work.  Do not proceed with the work until unsatisfactory conditions have been corrected in a manner acceptable to masonry installer and Sandia Designated Representative (SDR).

3.02	PLACING REINFORCEMENT

A.	General:  Clean reinforcement of loose rust, mill scale, earth, ice, or other materials which will reduce bond to mortar or grout.  Do not use reinforcement bars with kinks or bends not shown on drawings or final shop drawings, or bars with reduced cross-section due to excessive rusting or other causes.

1.	Position reinforcement accurately at the spacing shown. Support and secure vertical bars against displacement. Horizontal reinforcement may be placed as the masonry work progresses.  Where vertical bars are shown in close proximity, provide a clear distance between bars of not less than the nominal bar diameter or 1 inch, whichever is greater.

2.	Where columns, piers and pilasters are indicated, provide a clear distance between vertical bars as shown, but not less than 1-1/2 times the nominal bar diameter or 1-1/2 inches, whichever is greater.  Provide lateral ties as shown.

3.	Provide lapped splices, unless otherwise shown.  In splicing vertical bars or attaching to dowels, lap ends, place in contact, and wire tie.  Provide not less than minimum lap indicated, or if not indicated, as required by latest edition of UBC.

B.	Horizontal Joint Reinforcing:  If horizontal joint reinforcing is not otherwise indicated on drawings, provide continuous horizontal joint truss or ladder reinforcing in every other course.  Fully embed longitudinal side rods in mortar for their entire length with a minimum cover of 5/8 inch for exterior side of walls and 1/2 inch at other locations.  Lap reinforcement a minimum of 6 inches.  Do not bridge control and expansion joints with truss or ladder reinforcing, unless otherwise indicated.  Provide continuity at corners and wall intersections by use of prefabricated "L" and "T" sections.

3.03	INSTALLATION

A.	General:  Build masonry construction to the full thickness shown using units of nominal thickness shown or specified.

1.	Cut masonry units with motor-driven dry-cutting saw designed to cut masonry with clean, sharp, unchipped edges.  Cut units as required to provide pattern shown and to fit adjoining work neatly.  Use full units without cutting wherever possible.

2.	Do not wet concrete masonry units, except to dampen slightly before installation in extremely hot weather, strictly and only as recommended by  National Concrete Masonry Association (NCMA).

3.	Do not use frozen materials or materials mixed or coated with ice or frost.  Do not build on frozen work.  Remove and replace masonry work damaged by frost or freezing.

4.	Do not lower the freezing point of mortar by use of admixtures or anti-freeze agents.  Calcium chloride is prohibited in any mortar or grout.

5.	Layout walls in advance for accurate spacing of surface bond patterns, with uniform joint widths and to properly locate openings, movement-type joints, returns and offsets.  Avoid the use of less-than-half-size units at corners, jambs, and wherever possible at other locations.  Lay-up walls plumb and true and with courses level, accurately spaced, and coordinated with other work.

6.	Stopping and Resuming Work:  Rack back 1/2 masonry unit length in each course; do not tooth.  Clean exposed surfaces of set masonry, and remove loose masonry units and mortar prior to laying fresh masonry.

7.	Built-In Work:  As the work progresses, build in items specified under this and other sections of these specifications.  Fill in solidly with masonry around built-in items.  Fill space between hollow metal frames and masonry solidly with mortar.  Leave openings for equipment to be installed before completion of masonry work.  After installation of equipment, complete masonry work to match work immediately adjacent to the opening.

8.	Lay masonry units with full-face shell mortar beds. Fill vertical head joints (end joints between units) solidly with mortar from face of unit to a distance behind face equal to not less than the thickness of longitudinal face shells.  Solidly bed cross-webs of starting courses in mortar.  Maintain head and bed joint widths shown, or if not shown, provide 3/8-inch joints.

B.	Walls:

1.	Pattern Bond:  Lay wall units in running bond with vertical joints in each course centered on units in courses above and below, unless otherwise indicated.  At radiused walls, lay masonry units in stack bond with vertical joints aligned above and below.  Cut block side to taper as required for block to align in smooth curves without enlarged vertical joints, see drawings.  Bond and interlock each course at corners and intersections. Use special-shaped units where shown, and as required for corners, jambs, sash, control joints, lintels, bond beams, and other special conditions.

2.	Maintain vertical continuity of core or cell cavities, which are to be reinforced and grouted, to provide minimum clear dimensions indicated and to provide minimum clearance and grout coverage for vertical reinforcement bars.  Keep cavities free of mortar where adjacent to reinforced cores or cells.

3.	Where horizontal reinforced beams (bond beams) are shown, use special units or modify regular units to allow for placement of continuous horizontal reinforcement bars.  Place small mesh expanded metal lath or screening in mortar joints under bond beam courses or provide units with solid bottoms.

C.	Columns, Piers, and Pilasters:  Use CMU of the size, shape and number of vertical core spaces shown.  If not shown, use units which provide minimum clearances and grout coverage for number and size of vertical reinforcement bars shown.

D.	Control and Expansion Joints:

1.	Provide vertical expansion, control and isolation joints in masonry where shown.  Build-in related masonry accessory items as the masonry work progresses.  Rake out mortar in preparation for application of caulking and sealants.

2.	If location of control joints is not shown, place vertical joints spaced not to exceed 30'-0" o.c.  Locate control joints at points of natural weakness in the masonry work.

E.	Miscellaneous Items:  Install reglets and nailers for flashing and other related work where shown or required to be built into masonry work.

F.	Construction Tolerances:

1.	Variation from Plumb:  For vertical lines and surfaces of columns, walls and arrises, do not exceed 1/4 inch in 10 feet, or 3/8 inch in a story height not to exceed 20 feet, nor 1/2 inch in 40 feet or more.  For external corners, expansion joints, control joints and other conspicuous lines, do not exceed 1/4 inch in any story or 20 feet maximum, nor 1/2 inch in 40 feet or more.  For vertical alignment of head joints do not exceed plus or minus 1/4 inch in 10 feet, 1/2 inch maximum.

2.	Variation from Level:  For bed joints and lines of exposed lintels, sills, parapets, horizontal grooves and other conspicuous lines, do not exceed 1/4 inch in any bay or 20 feet maximum, nor 1/2 inch in 40 feet or more.  For top surface of bearing walls do not exceed 1/8 inch between adjacent floor elements in 10 feet or 1/16 inch within width of a single unit.

3.	Variation of Linear Building Line:  For position shown in plan and related portion of columns, walls and partitions, do not exceed 1/2 inch in any bay or 20 feet maximum, nor 3/4 inch in 40 feet or more.

4.	Variation in Cross-Sectional Dimensions:  For columns and thickness of walls, from dimensions shown, do not exceed minus 1/4 inch nor plus 1/2 inch.

5.	Variation in Mortar Joint Thickness:  Do not exceed bed joint thickness indicated by more than plus or minus 1/8 inch, with a maximum thickness limited to 1/2 inch.  Do not exceed head joint thickness indicated by more than plus or minus 1/8 inch.  Do not allow vertical joints to enlarge at curves.

G.	Tooling:  Tool exposed joints slightly concave using a jointer larger than joint thickness, unless otherwise indicated.

3.04	GROUTING

A.	General:  Place reinforcement before grouting.  Place before or after laying masonry units, as required by job conditions.

B.	Preparation:  Prior to grouting, inspect and clean grout spaces.  Remove dust, dirt, mortar droppings, loose pieces of masonry and other foreign materials from grout spaces. After final cleaning and inspection, close cleanout holes and brace closures to resist grout pressures.  Lay CMU to maximum pour height.  Do not place grout until entire height of masonry to be grouted has attained sufficient strength to resist displacement of masonry units and breaking of mortar bond.  Install shores and bracing, if required, before starting grouting operations.

C.	Pouring:  Limit grout pours to sections which can be completed in one working day, with not more than one-hour interruption of pouring operation.  Place grout in lifts which do not exceed 5 feet.  Allow not less than 30 minutes, nor more than one hour, between lifts of a given pour.  Rod or vibrate each grout lift during pouring operation.  When more than one pour is required to complete a given section of masonry, extend reinforcement beyond masonry as required for splicing.  Pour grout to within 1-1/2 inches of top course of first pour.  After grouted masonry is cured, lay masonry units and place reinforcement for second pour section before grouting.  Repeat sequence if more pours are required.

D.	Bond Beams:  Stop grout in vertical cells 1-1/2 inches below bond beam course.  Place horizontal reinforcement in bond beams; lap at corners and intersections as shown.  Place grout in bond beam course before filling vertical cores above bond beam.

3.05	REPAIR, POINTING, AND CLEANING, AND WATERPROOFING

A.	Repairs:  Remove and replace masonry units which are loose, chipped, broken, stained or otherwise damaged, or if units do not match adjoining units as intended.  Provide new units to match adjoining units and install in fresh mortar or grout, pointed to eliminate evidence of replacement.

B.	Pointing:  During the tooling of joints, enlarge any voids or holes, except weep holes, and completely fill with mortar.  Point-up all joints at corners, openings and adjacent work to provide a neat, uniform appearance, properly prepared for application of caulking or sealant compounds.

C.	Cleaning:  Clean exposed masonry by dry brushing at the end of each day's work and after final pointing to remove mortar spots and droppings.

D.	Waterproofing:  Apply waterproofing in single coat according to the manufacturers installation instructions ensuring that all exposed masonry surfaces receive full coverage.

END OF SECTION