WESTERN ELECTRICITY COORDINATING COUNCIL

ASSOCIATED MATERIAL

FOR

2008 LSP1-SA BASE CASE

March 12, 2003

ASSOCIATED MATERIAL

2008 LSP1-SA BASE CASE

INDEX

Page

I.	Summary of Significant System Changes		1

II.	Interchange Diagram		12

III.	Supplemental Line Flow Summary		13

IV.	Phase Shifting Transformer Representation		18

V.	Power Flow Case Analysis		21

A.  	Area Reserve Factor

VI.	Information by Area		23

A.	Interchange Schedules

B.	Loads and Resources

C.	Generation Schedules

VII.	Power System Stabilizers In-Service Tabulation		107

SUMMARY OF SIGNIFICANT SYSTEM CHANGES

TO THE 2002 LSP2 OPERATING CASE

TO COMPILE THE 2008 LSP1-S BASE CASE

A.	AREA COORDINATOR:  DESERT SOUTHWEST

-	Added Saguaro-Tortolita #2 500 kV line.

- Added Tortolita 500/138 kV #2 transformer.

- Added Gila River (2856 MVA), Red Hawk (2672 MVA), Harquahala (1224 MVA), Mesquite (1628 MVA), and Arlington (841 MVA) generation projects in southern Arizona.

-	Centennial Project in southern Nevada is represented and includes the following:

Crystal North, Harry Allen, Duke, Mirant, Reliant and Calpine 500 kV substations.

Harry Allen – Duke, Mirant, Reliant and Crystal – Calpine 500 kV lines to facilitate generation interconnection.

Harry Allen – Northwest 500 kV line and Northwest 500/230 kV transformer.

Mead – Harry Allen – Crystal North 500 kV line.

Two 500 kV phase shifters at Crystal.

Bighorn 230 kV bus and Arden – Bighorn 230 kV lines #1 and #2.

Duke units 1-6 (1682 MVA), Mirant units 1-3 (733 MVA), Reliant units 1-3

(760 MVA), Calpine units 1-4 (1373 MVA), and Bighorn units 1-6 (1682 MVA).

- Added Blythe (612 MVA), Sundance (605 MVA), and Big Sandy (1112 MVA) generation projects in WAPA LC control area.

- Greenway 230 kV bus added in Faulkner – Mead South 230 kV line to service load at Greenway.

- Estrella 500/230 KV substation renamed to Rudd.

B.	AREA COORDINATOR:  CANADA

Significant changes for B.C. Hydro:

- Added following generation:  LB2 GEN (18 MVA), VIGP G1,2 (300 MVA),

BRX G1 (225 MVA), RVG G1 (25 MVA), and PIN Ipp 1 and 2 (37 MVA),

ALH G1, 2 (189 MVA), SEV G4 (225 MVA), and POW 132 (136 MVA).

- Added 40 MVAR switched shunt capacitor at VNT138 (50654).

- HVDC cable ARN230AC (50947) to VIT 230 (50360) is removed.

- Generating plants PUR-IPP1 and PUR-IPP2 are combined and renamed to CRS-IPP.

Significant changes for Aquila Network Canada:

- Added the following 230 kV transmission lines:

WSS230 (52525) – BTS230 (52502)

BTS230 (52502)  – KCL230 (50788)

BTS230 (52502)  – SEL230 (50783)

BTS230 (52502)  – ALH230 (51061)

WSS230 (52525) – RGA230 (52211)

- Added the following transformers:

BTS230 (52502)   – BRX63 (52477) 230/63 kV #1 & #2

WSS230 (52525)  – WSS63 (52224) 230/63 kV #1 & #2

KCL230 (50788)  – KCL63B (52661) 230/63 kV

RGA73L (52211) – RGA63T1 (52231) 230/63 kV

LEE230C (52317) – LEE138C (52302) 230/138 kV

-	Waneta – Boundary 230 kV line is rerouted through Nelway 230 kV.

Significant changes for Alberta:

- No significant system changes.

C.	AREA COORDINATOR:  IDAHO

-	For load growth in the Boise area, added the Caldwell – Garnet – Locust 230 kV line  and a second Locust 230/138 kV tie bank.

-	Added a 230/138 kV tie bank at Garnet and the Garnet – Hill 138 kV line.

-	Reconductored the Ontario – Caldwell 230 kV line.

- Added phase two of the Brownlee – Boise Bench 230 kV project with the addition of the Brownlee – Oxbow #2 230 kV.

-	Added Garnet (332 MVA) and Danskin (197 MVA) generation projects with associated transmission integration projects.

-	Added 30% series compensation at Midpoint in the Midpoint – Kinport 345 kV line.

-	Added a 175 MVAR shunt bank on the Borah 345 kV bus.

-	Replaced the two 345/230 kV transformer banks at Midpoint with two 700 MVA    units.

D.	AREA COORDINATOR:  MONTANA

-	No significant system changes.

E.	AREA COORDINATOR:  NORTHWEST

Changes from the 2001 Significant Additions Report:

- A new Big Hanaford combined-cycle generation project (248 MW) near Centralia, Washington is available but off-line.  (TAU)

- A new Condon wind generation project (24 MW) near Condon, Oregon is in service.  (NWWnd)

- The Four Mile Hill geothermal generation project (45 MW) near Glass Mtn, California is not yet in service.  (CALP)

- New generation plants 3 & 4 at Fredonia, Washington (100 MW total) are in service.  (PSE)

- A new GNA Cliff combined-cycle gas generation project (180 MW) near Goldendale, Washington is available but off-line.   (GNAE)

- A new Klondike Schoolhouse wind generation project (24 MW) near Condon, Oregon is in service.  (NWWind)

- A new Klamath Addition single-cycle gas generation project (100 MW) adjacent to the existing Klamath Falls combined-cycle plant is available but off-line.  (KLA)

- The Longview “Mint Farm” combined-cycle generation project (248 MW) near Longview, Washington is delayed.  (MIR)

- The Mercer Ranch combined-cycle generation project (740 MW) near Crow Butte, Washington has been cancelled.  (COGNX)

- The Newport (Wallula) combined-cycle generation project (1300 MW) near Wallula, Washington is delayed.  (NEWP)

- A new Nine Canyon wind generation project (50 MW) near Paterson, Washington is available but off-line.  This replaces the 8 MW Energy NW Wind project.  (EnNW)

- The Starbucks combined-cycle gas generation project (1200 MW) near Little Goose dam, Washington is available but off-line.  (NWPwr)

- The Sumas II combined-cycle generation project (550 MW) near Sumas, Washington is not yet in service.  (PSE)

- The Umatilla combined-cycle generation project (500 MW) in Umatilla County, Oregon is not yet in service.  (PSE)

- The Albany – Eugene 115 kV reinforcement project is delayed.  (BPA)

- The Beacon North – Rathdrum 230 kV line is looped into a new Otis sub, where a new 230/115 kV transformer (300 MVA) is installed.  (AVA)

- The Benton – Glade – Franklin 115 kV line is reconductored to 205 MVA.  (BPA)

- A long stretch of existing 69 kV line in the Olympic Peninsula, Washington area, running from Happy Valley to Port Angeles, is upgraded to 115 kV.  (CLA)

- The Chief Joseph – Monroe 500 kV #2 line is delayed.  (BPA)

- The Echo Lake – Monroe 500 kV #2 line (3460 MVA) is in service.  (BPA)

- In support of the Chehalis generation project, the Paul – Allston #1 500 kV line is looped into a new 500 kV substation at Napavine.  (BPA)

- The Leavenworth – Coles Corner 115 kV line is delayed.  (CHPD)

- In support of the Starbuck generation, the Little Goose – Lower Monumental 500 kV line is looped into a new Starbuck substation and a new 500 kV line from Starbuck to Lower Monumental is added.  (BPA)

- The new Silverdale – Foss Corner 115 kV line is delayed.  (PSE)

- The SnoKing – Clearview 115 kV line upgrade is delayed.  (SNPD)

- The SnoKing tap on the Monroe – Samammish 230 kV line, serving the SnoKing 230 kV bus, is removed and replaced with a SnoKing tap on the Echo Lake – Monroe #1 500 kV line, along with a new 500/230 kV (1800 MVA) transformer.  (BPA)

- The existing Hanford – John Day 500 kV and Hanford – Ostrander 500 kV lines are both looped into a new substation called Wautoma.  From Wautoma, a new 500 kV line (3950 MVA) runs to Schultz substation.  The new line replaces the Schultz – Hanford 500 kV addition project.  (BPA)

- The 500/230 kV transformer at Satsop substation is relocated to Shelton substation.  The existing Paul – Satsop 500 kV line is split, with the Paul section being extended and reterminated at Shelton and the Satsop section being operated at 230 kV and extended and reterminated at Olympia.  (BPA)

- To support the Wallula generation project, the existing McNary – Sacajawea Tap 500 kV line is tapped at Smiths Harbor, and a new Smiths Harbor – Wallula 500 kV line is added.  (BPA)

- A new Priest Rapids – Wahluke - Frenchman – Potholes 230 kV line is in service.  A new 672 MVA phase-shifter is installed in the Wahluke – Frenchman section.  A new 230/115 kV, 250 MVA transformer is installed at Frenchman sub.  (GCPD)

- A second 500/230 kV transformer at Meridian, Oregon sub (650 MVA) is in service.  (PACW)

- A new 230/115 kV transformer at South Bremerton sub, Washington (325 MVA) is in service.  (PSE)

- Series compensation (50%) has been added to the Bell – Taft 500 kV line.  (BPA)

- Series compensation (50%) has been added to the Dworshak – Taft 500 kV line.  (BPA)

- Series compensation (42%) has been added to the Echo Lake - Kangley – Schultz 500 kV line.  (BPA)

- Series compensation (45%) has been added to the Raver – Schultz #1 500 kV line.  (BPA)

Changes from the 2002 LSP2 Operating Case:

- A new Big Hanaford combined-cycle generation project (248 MW) near Centralia, Washington is available but off-line.  (TAU)

- A new Condon wind generation project (24 MW) near Condon, Oregon is in service.  (NWWnd)

- The Chehalis combined-cycle generation project (600 MW) near Chehalis, Washington is available but off-line.  (CPGLP)

- The Everett Delta combined-cycle gas generation project (225 MW) near Everett, Washington is available but off-line.  (FPLE)

- PSE’s temporary generation at Fredrickson 3 and 4 is removed.  (PSE)

- The Goldendale Aluminum (GEP) combined-cycle generation project (248 MW) near Goldendale, Washington is available but off-line.  (GOLD)

- A new GNA Cliff combined-cycle gas generation project (180 MW) near Goldendale, Washington is available but off-line.   (GNAE)

- The Hermiston (HPP) combined-cycle gas generation project (600 MW) in Umatilla County, Oregon is available but off-line.   (CALP)

- A new Klamath Addition single-cycle gas generation project (100 MW) adjacent to the existing Klamath Falls combined-cycle plant is available but off-line.  (KLA)

- A new Klondike Schoolhouse wind generation project (24 MW) near Condon, Oregon is in service.  (NWWind)

- A new Nine Canyon wind generation project (50 MW) near Paterson, Washington is available but off-line.  This replaces the 8 MW Energy NW Wind project.  (EnNW)

- The Satsop combined-cycle gas generation project (630 MW) near Elma, Washington is available but off-line.  (DUKE)

- The Starbucks combined-cycle gas generation project (1200 MW) near Little Goose Dam, Washington is available but off-line.  (NWPwr)

- The Beacon North – Rathdrum 230 kV line is looped into a new Otis sub, where a new 230/115 kV transformer (300 MVA) is installed.  (AVA)

- The Bell – Grand Coulee 500 kV line is in service.  (BPA)

- The Benton – Glade – Franklin 115 kV line is reconductored to 205 MVA.  (BPA)

- The Benewah – Shawnee 230 kV line is in service.  (AVA)

- The Bethel – Santiam 230 kV line is in service, replacing service to Bethel from a tap on the Santiam – Chemawa 230 kV line.  (BPA)

- A new Canby – Twilight Tap – Wilsonville line is upgraded from 59.8 kV to 115 kV.  (PGE)

- A second Echo Lake – Monroe 500 kV line (3460 MVA) is in service.  (BPA)

- The John Day – McNary 500 kV line (3950 MVA) is in service.  (BPA)

- A long stretch of existing 69 kV line in the Olympic Peninsula, Washington area, running from Happy Valley to Port Angeles, is upgraded to 115 kV.  (CLA)

- In support of the Chehalis generation project, the Paul – Allston #1 500 kV line is looped into a new 500 kV substation at Napavine.  (BPA)

- The San Juan submarine cable 34.5 kV to 69 kV upgrade is complete.  (BPA)

- The Schultz – Kangley – Echo Lake 500 kV line is in service, replacing the Schultz – Raver #2 500 kV line.  The line has 42% series compensation added at Schultz.  (BPA)

- The SnoKing tap on the Monroe – Samammish 230 kV line, serving the SnoKing 230 kV bus, is removed and replaced with a SnoKing tap on the Echo Lake – Monroe #1 500 kV line, along with a new 500/230 kV (1800 MVA) transformer.  (BPA)

- A Sherwood “A” – Murray Hill 115 kV line (197 MVA) is in service.  (PGE)

- A second Sherwood – Murray Hill 230 kV line (525 MVA) is in service.  (PGE)

- A new Sherwood – Wilsonville 115 kV line (200 MVA) is in service.  (PGE)

- A new Shelton – South Bremerton 230 kV line (400 MVA) plus a new 230/115 kV transformer at South Bremerton (325 MVA) are in service.  (BPA)

- In support of the Starbuck generation, the Little Goose – Lower Monumental 500 kV line is looped into a new Starbuck substation and a new 500 kV line from Starbuck to Lower Monumental is added.  (BPA)

- The existing Hanford – John Day 500 kV and Hanford – Ostrander 500 kV lines are both looped into a new substation called Wautoma.  From Wautoma, a new 500 kV line (3950 MVA) runs to Schultz substation.  The new line replaces the Schultz – Hanford 500 kV addition project.  (BPA)

- To support the Wallula generation project, the existing McNary – Sacajawea Tap 500 kV line is tapped at Smiths Harbor, and a new Smiths Harbor – Wallula 500 kV line is added.  (BPA)

- A new Priest Rapids – Wahluke - Frenchman – Potholes 230 kV line (400 MVA) is in service.  A new 672 MVA phase-shifter is installed in the Wahluke – Frenchman section.  A new 230/115 kV, 250 MVA transformer is installed at Frenchman sub.  (GCPD)

- The 500/230 kV transformer at Satsop substation is relocated to Shelton substation.  The existing Paul – Satsop 500 kV line is split, with the Paul section being extended and reterminated at Shelton and the Satsop section being operated at 230 kV and extended and reterminated at Olympia.  (BPA)

- The Bothell 230/115 kV transformers #2 and #3 are both upgraded to 300 MVA.  (SCL)

- The second Pearl 500/230 kV transformer is in service.  (BPA)

- Series compensation (50%) has been added to the Bell – Taft 500 kV line.  (BPA)

- Series compensation (50%) has been added to the Dworshak – Taft 500 kV line.  (BPA)

- Series compensation (45%) has been added to the Raver – Schultz #1 500 kV line.  (BPA)

- The 230 kV buses at Grand Coulee, McNary, Midway and Rocky Reach are

re-modeled to show multiple sections around intervening circuit breakers.  All except Midway are adjacent to large hydro plants, and the plants are re-modeled along powerhouse lines.  At Coulee, the Area slack bus is changed from the first 18 units in aggregate to the single unit 22.

F.	AREA COORDINATOR:  PACE

- Added two 300 MVA 230 kV phase shifting transformers at Monument.

- Added generation at Mona (619 MVA), Gadsby 7 & 8 (430 MVA) and Hunter 4

(590 MVA).

-	Added Monument-Opal 230 kV line.

-	Added Point of Rocks-Rock Springs 230 kV line.

G.	AREA COORDINATOR:  PACIFIC GAS AND ELECTRIC COMPANY

- Added following generation:  Gilroy Peakers 1-3 (150 MVA), SECAL 1-3

(746 MVA), Sunset CC (606 MVA), Sunrise 3 (293 MVA), GWFTRACY 1-3

(339 MVA), Three Mountain Project (660 MVA), and Metcalf Energy Center (777 MVA).

H.	AREA COORDINATOR:  SIERRA PACIFIC POWER COMPANY

-	Added the Falcon-Gonder 345 kV project.

I.	AREA COORDINATOR:  SOUTHERN CALIFORNIA

- Added Otay generation (798 MVA) in SDG & E area.

- Added Mission 230 kV statcom (+/- 200 MVAR).

- Impedance and ratings changed on Imperial Valley – LaRosita 230 kV tie line due to line bundling.

- Miguel – Tijuana 230 kV tie line replaced by Otay Mesa – Tijuana 230 kV.

- Added SVD’s at Miguel 230 kV (63 MVAR) and Sycamore 230 kV (126 MVAR).

- Added generation in CFE area:  CCBC 1 & 2 (600 MVA) and LRP units 1-4

(968 MVA).

- Numerous topology changes in SDG & E and CFE areas.

-	Added generation in LADWP area:  Valley repower units 1-3 (714 MVA) and Haynes repower units 1-3 (714 MVA).

- Removed Rinaldi – Toluca 230 kV ck #3.

- Added the Rinaldi – Valley #2 and Valley – Toluca #2 230 kV lines.

- Added a fourth McCullough 500/230 kV transformer (400 MVA).

J.	AREA COORDINATOR:  ROCKY MOUNTAIN

-	Added the Walsenburg-Gladstone 230 kV tie between Colorado and New Mexico.

- TECHNICAL STAFF

- Listed below are series compensation levels portrayed on major transmission lines for the 2008 LSP1-SA base case:

Percent Series

Arizona	Compensation

Cholla-Saguaro 500 kV	36

Coronado-Cholla 500 kV	0

Coronado-Silver King 500 kV	0

Four Corners-Cholla 345 kV (1 & 2)	25

Four Corners-Moenkopi 500 kV	0

Four Corners-West Mesa 345 kV	39

Greenlee-Winchester-Vail 345 kV	0

Liberty-Peacock-Mead 345 kV	35

McKinley-San Juan 345 kV (1 & 2)	30

Navajo-Crystal 500 kV	72

Crystal-McCullough 500 kV	70

Navajo-Moenkopi 500 kV	70

Navajo-Westwing 500 kV	40

Palo Verde-North Gila 500 kV	0

Perkins-Mead 500 kV	70

San Juan-BA 345 kV	39

Springerville-Greenlee 345 kV 	38

Springerville-Luna 345 kV	26

Percent Series

Arizona (cont.)	Compensation

Springerville-Vail 2 345 kV	40

Westwing-Yavapai 500 kV	43

Yavapai-Moenkopi 500 kV	28

Canada

Ashton Creek – Selkirk 500 kV	50

Cheekye-Kelly Lake 500 kV	55

G. M. Shrum-Williston 500 kV (1 & 2)	50

Kelly Lake-Clayburn 500 kV	55

Kelly Lake-Nicola 500 kV	50

Kelly Lake-Williston 500 kV (1 & 3)	50

Kennedy-Williston 500 kV	100

Nicola-Ingledow 500 kV	50

Nicola-Meridian 500 kV	50

Nicola – Selkirk 500 kV	50

Idaho

Boise Bench-Brownlee 230 kV (1 - 4)	58

Bridger-Borah 345 kV	45

Bridger-Goshen 345 kV	45

Bridger-Kinport 345 kV	45

Brownlee-Ontario 230 kV	70

Midpoint-Boise Bench 230 kV (2 & 3)	28

Midpoint-Kinport 345 kV	30

Oxbow-Lolo 230 kV	0

Montana

Broadview-Townsend-Garrison 500 kV (1 & 2)	35

Colstrip-Broadview 500 kV (1 & 2)	35

Northwest

Alvey-Dixonville 500 kV	52

Alvey-Marion 500 kV	50

Bell BPA-Taft 500 kV	50

Buckley-Slatt 500 kV	29

Burns-Midpoint 500 kV	50

Burns-Summer Lake 500 kV	112

Coulee-Schultz 500 kV (1 & 2)	40

Dixonville-Meridian 500 kV	50

Dworshak-Taft 500 kV	50

Echo Lake-Schultz 500kV (2)	42

Garrison-Taft 500 kV (1 & 2)	31

Percent Series

Northwest (cont.)	Compensation

Garrison-Townsend 500 kV (1 & 2)	81

Grizzly-Captain Jack 500 kV 	62

Grizzly-Malin 500 kV 	60

Malin-Summer Lake 500 kV	53

Ponderosa-Summer Lake 500 kV	72

Raver-Schultz 500 kV	45

Walla Walla-Enterprise 230 kV	66

PG&E

Captain Jack-Olinda 500 kV	62

Gates-Midway 500 kV	64

Los Banos-Gates 500 kV 	54

Los Banos-Midway 500 kV	58

Malin-Round Mountain 500 kV (1 & 2)	(1) 62  (2) 64

Olinda-Maxwell-Tracy 500 kV	74

Round Mountain-Table Mountain 500 kV (1 & 2)	74

Table Mountain-Tesla 500 kV	66

Table Mountain-Vaca Dixon 500 kV	68

Tesla-Vaca Dixon 500 kV	75

Southern California

Eldorado-Lugo 500 kV	35

Imperial Valley-Miguel 500 kV	51

Imperial Valley-North Gila 500 kV	52

Marketplace-Adelanto 500 kV line	47

McCullough-Victorville 500 kV (1 & 2)	35

Midway-Vincent 500 kV 	 (1-2) 70 (3) 74

Mohave-Lugo 500 kV	35

Palo Verde-Devers 500 kV	47

Moenkopi-Eldorado 500 kV	70

WAPA

Flagstaff-Glen Canyon 345 kV (1 & 2)	 (1) 70  (2) 69

Flagstaff-Pinnacle Peak 345 kV (1 & 2)	76

Shiprock-Kayenta-Glen Canyon 230 kV	80

SUPPLEMENTAL LINE FLOW SUMMARY

2008 LSP1-SA APPROVED BASE CASE

CANADA AND NORTHWEST

1. Alberta - British Columbia

Langdon(*) - Cranbrook 500 kV                          171.6

Pocatera - Fording Coal Tap(*) 138 kV                   12.7

Colman - Natal(*) 138 kV                                15.5

TOTAL                                                  199.9

2. Canada - Northwest

Ingledow(*) - Custer 1&2 500 kV                        332.3

Nelway - Boundary(*) 230 kV                            168.5

TOTAL                                                  500.8

3. Northwest - California

Malin(*) - Round Mt. 1&2 500 kV                       2351.7

Delta(*) - Cascade 115 kV                               74.9

Captain Jack(*) - Olinda 500 kV                       1325.0

AC TOTAL                                              3751.6

Pacific DC Intertie at Sylmar 230 kV                           2734.5

4. North of John Day

Raver(*) - Paul 500 kV                                1009.2

Hanford(*) - Wautoma 1&2 500 kV                       1347.7

Ashe(*) - Marion 500 kV                                724.9

Ashe(*) - Slatt 500 kV                                 912.7

Smiths Harbor Jct. - McNary(*) 1&2 500 kV             1221.9

TOTAL                                                 5216.4

NORTHEAST

1. MPC High Line

Cut Bank - Cut Bank Pump(*) 115 kV                     -13.6

Great Falls(*) - Havre 161 kV                           19.6

Conrad(*) - Shelby 230 kV                               27.8

TOTAL                                                   33.8

2. West of Taft

Taft(*) - Dworshak 500 kV                              572.8

Taft(*) - Bell 500 kV                                  378.9

TOTAL                                                  951.7

SUPPLEMENTAL LINE FLOW SUMMARY

2008 LSP1-SA BASE CASE

PAGE 2

3. Southeast Montana Ties

Crossover(*) - Huntley 230 kV                          135.3

Crossover(*) - Hardin 230 kV                           -57.3

Yellowtail - Rimrock PS(*) 161 kV                       29.3

Yellowtail - Billings PS(*) 230 kV                      65.7

TOTAL                                                  172.9

4. West of Borah

Kinport(*) - Midpoint 345 kV                           361.0

Borah(*) - Adelaide 345 kV                             278.6

Borah(*) - Adelaide Tap 345 kV                         255.2

American Falls(*) - Pleasant Valley 138 kV              59.2

American Falls(*) - Raft River 138 kV                   45.7

TOTAL                                                  999.7

5. Bridger System West at Bridger

Bridger(*) - Goshen, Kinport, and Borah 345 kV                 1584.3

6. Path C

Ben Lomond - Borah (*) 345 kV                          -33.9

Treasureton - Brady (*) 345 kV                         -45.5

Grace - Goshen (*) 161 kV                              -73.7

Malad - American Falls (*) 138 kV                      -29.1

TOTAL                                                 -182.2

7. Brownlee East

Brownlee(*) - Boise Bench 1-4 230 kV                   506.3

Brownlee(*) - Ontario 230 kV                           230.7

Oxbow(*) - McCall 138 kV                                14.0

Quartz(*) - Nelson Tap 138 kV                           -3.9

TOTAL                                                  747.1

8. Midpoint(*) - Burns 500 kV                                        901.1

9. Total 4A

Dave Johnston(*) - Difficulty 230 kV                   121.9

Riverton(*) - Wyopo 230 kV                             132.1

Spence(*) - Mustang 230 kV                             112.3

TOTAL                                                  366.3

10. Total 4B

Wyodak(*) - Buffalo 230 kV                             224.8

Spence(*) - Badwater 230 kV                             35.6

Alcova(*) - Raderville 115 kV                           25.0

Casper(*) - Midwest 230 kV                             -14.8

Riverton(*) - Thermopolis 230 kV                       -27.6

Riverton 230 kV(*) - Riverton 115 kV                     4.1

TOTAL                                                  247.0

SUPPLEMENTAL LINE FLOW SUMMARY

2008 LSP1-SA BASE CASE

PAGE 3

11. Intermountain DC at Intermountain 345 kV                         1763.6

12. Utah/Colorado - Nevada/Arizona/New Mexico

Red Butte(*) - Harry Allen PS 345 kV                   102.1

Sigurd PS - Glen Canyon(*) 230 kV                      215.8

Pinto PS - Four Corners(*) 345 kV                      331.7

Lost Canyon - Shiprock PS(*) 230 kV                    130.3

Hesperus - San Juan PS(*) 345 kV                       280.8

Durango - Coyote(*) 115 kV                              25.3

TOTAL                                                 1086.0

13. Sierra - PG&E

Summit 1 120(*) - Drum 115 kV                          -13.4

Summit 2 120(*) - Drum 115 kV                           -5.8

Summit 3(*) - Cisco 60 kV                               -5.8

TOTAL                                                  -25.0

14. Total 1A West

Artesia - Vernal(*) 138 kV                              -8.2

Rangely - Bonanza(*) 138 kV                            -60.8

Bears Ears - Bonanza(*) 345 kV                          42.4

TOTAL                                                  -26.6

15. Total 2A South

Hesperus - San Juan PS(*) 345 kV                       280.8

Lost Canyon - Shiprock PS(*) 230 kV                    130.3

Durango - Coyote(*) 115 kV                              25.3

TOTAL                                                  436.4

SOUTHEAST

1. East of Colorado River (500-345 kV)

Navajo(*) - Crystal 500 kV                            1043.5

Moenkopi - Eldorado(*) 500 kV                          859.1

Palo Verde(*) - Devers 500 kV                         1048.5

Hassyampa(*) - North Gila 500 kV                       660.9

Perkins(*) - Mead 500 kV                               -65.6

Liberty(*) - Mead 345 kV                               -50.1

TOTAL                                                 3496.3

2. East of Colorado River (230 kV)

Harcuvar (Liberty) - Parker(*) 230 kV                   -0.1

McConnico - Davis(*) 230 kV                            -19.4

Eagle Eye - Parker(*) 230 kV                            -5.8

TOTAL                                                  -25.4

SUPPLEMENTAL LINE FLOW SUMMARY

2008 LSP1-SA BASE CASE

PAGE 4

3. Four Corners Area

Four Corners(*) - Moenkopi 500 kV                      933.3

Four Corners(*) - Cholla 1&2 345 kV                    891.0

TOTAL                                                 1824.3

SOUTHWEST

1. Northwest of the Colorado River

McCullough(*) - Victorville 1&2 500 kV                1285.4

Eldorado(*) - Lugo 500 kV                              798.7

Marketplace(*) - Adelanto 500 kV                       642.4

Mohave(*) - Lugo 500 kV                               1028.8

Mead(*) - Victorville 287 kV                           117.5

Eldorado(*) - Pisgah - Lugo 1&2 230 kV                 136.7

J. Hinds - Mirage(*) 230 kV                             54.3

TOTAL                                                 4063.7

2. Other Flows

Palo Verde - Devers(*) 500 kV                         1025.0

North Gila(*) - Imperial Valley 500 kV                 634.0

El Centro - Imperial Valley(*) 230 kV                  -30.9

MIRIID - Mirage(*) 230 kV                              166.5

Coachella - Devers(*) 230 kV                           131.0

TOTAL                                                 1925.6

3. Round Mtn.(*) - Table Mtn. 1&2 500 kV                            2762.4

4. Table Mtn. 500 kV South

Table Mtn.(*) - Vaca Dixon 500 kV                     1780.8

Table Mtn.(*) - Tesla 500 kV                          1388.6

TOTAL                                                 3169.5

5. Table Mtn. 500/230 kV                                            -444.0

6. Midway - Los Banos (Path 15)

Gates(*) - Los Banos 500 kV                           -484.6

Midway(*) - Los Banos 500 kV                          -556.6

Gates(*) - Panoche 1&2 230 kV                          -56.5

Gates(*) - Gregg 230 kV                                255.1

Gates(*) - McCall 230 kV                                49.6

TOTAL                                                 -793.0

SUPPLEMENTAL LINE FLOW SUMMARY

2008 LSP1-SA BASE CASE

PAGE 5

7. Southern California Imports

Pacific DC Intertie at Sylmar 230 kV                  2734.5

Intermountain DC at Adelanto 500 kV                   1707.0

Midway(*) - Vincent 1,2,3 500 kV                      2048.9

McCullough(*) - Victorville 1&2 500 kV                1285.4

Eldorado(*) - Lugo 500 kV                              798.7

Mohave(*) - Lugo 500 kV                               1028.8

Palo Verde - Devers(*) 500 kV                         1025.0

North Gila(*) - Imperial Valley 500 kV                 634.0

Marketplace(*) - Adelanto 500 kV                       642.4

Mead(*) - Victorville 287 kV                           117.5

Kramer - Lugo(*) 1&2 230 kV                            464.7

Victor - Lugo(*) 1&2 230 kV                            -81.5

Eldorado(*) - Pisgah - Lugo 1&2 230 kV                 136.7

J. Hinds - Mirage(*) 230 kV                             54.3

El Centro - Imperial Valley(*) 230 kV                  -30.9

MIRIID - Mirage(*) 230 kV                              166.5

Coachella - Devers(*) 230 kV                           131.0

TOTAL                                                12862.8

OTHER FLOWS -------------------

West of the Colorado River                                          5989.3

Northeast - Northwest                                               2457.1

Southern California Inertia

LADWP                       12489

- Intermountain            -5698

SOCALIF                     57636

SANDIEGO                     8214

Hoover A5-A7,N1-N7           7289

-------

79930.0

PHASE SHIFTING TRANSFORMER REPRESENTATION

FOR THE 2008 LSP1-SA BASE CASE

AREA   	PHASE SHIFTING TRANSFORMER	                     REPRESENTATION

ARIZONA	LIBTYPHS230 - LIBERTY 230	0.0 degrees fixed phase. Not used to control a schedule.  It is sometimes operated to reduce loading on parallel lines.

ARIZONA	PERK PS1500 - WESTWING 500	0.0 degrees fixed phase.  Not used to control a

PERK PS2500 - WESTWING 500	schedule in this case.

B.C. HYDRO	NLY230   230 - NLYPHS   230	-20.0 degrees fixed phase.  Used to prevent overloading of the Nelway-Boundary 230 kV tie line.

LADWP	SCATERGD230 - SCATERGD138	5.0 degrees fixed phase.  Not used to control a schedule.  Used to prevent overloading of the Scattergood cables.

MONTANA	RIMROCK  161 - RMRK PHA 161	Regulating to hold -30 MW on the Rimrock-Rimrock PHA 161 kV line.

MONTANA	BILINGS  230 - BLGS PHA 230	Regulating to hold -59 MW on the Billings-Billings PHA 230 kV line.

NEVADA	CRSTL2PS230 - CRYSTAL 230	Two phase shifting transformers regulating to

CRSTL3PS230 - CRYSTAL 230	hold 250 MW into the Nevada Power System.

NEVADA	CRSTL N 500 - CRYSTAL 500 #1	Two phase shifting transformers regulating to

CRSTL N 500 - CRYSTAL 500 #2	hold 0 MW on the Harry Allen – Crystal 500 kV line.

NEVADA	HA PS    345 - H ALLEN 345	Regulating to hold 100 MW on the Red Butte-Harry Allen 345 kV line.

NEW MEXICO	ARR   PS345 - ARROYO  345	Regulating to hold 182 MW on the West Mesa-Arroyo 345 KV line.

NORTHWEST	BOX CANY 115 - BOX PS 115	This phase shifter is operated to force flows south from Box Canyon.

NORTHWEST	FRCHMNPS 230 - FRENCHMN 230	Regulating to hold 370 MW from Priest Rapids 230 kV north to Potholes 230 kV.  Used to reduce flows on other utilities lines.

NORTHWEST	TONO 115 - TONO PHA 115	-4.70 degrees fixed phase.  Used to reduce parallel flows within the PACW system.

PHASE SHIFTING TRANSFORMER REPRESENTATION

FOR THE 2008 LSP1-SA BASE CASE

AREA   	PHASE SHIFTING TRANSFORMER	                     REPRESENTATION

NORTHWEST	WEED JCT 115 - WEED JPS 115	Regulating to hold within +/- 10 MW of schedule between the Northwest and PG&E on the Delta-Cascade 115 kV line.  Schedule is 80 MW.

PACE	MONUMENT 230 - MONU PST 230 #1	0.0 degrees fixed phase.  These two phase shifters

MONUMENT 230 - MONU PST 230 #2	are not used to control schedules.  When necessary, they are used to regulate flows on the Monument-Naughton 230 kV line.

PACE	JFRSNPHA 161 - JEFFERSN 161	0.0 degrees fixed phase.  The Jefferson phase shifter is not used to control schedules.  When necessary, it is used to prevent overloading of the Goshen-Jefferson 161 kV line.

PACE	PINTO 345 - PINTO PS 345		0.0 degrees fixed phase.  Actual schedule is

115 MW on the Pinto-Four Corners 345 kV line.

PACE	SIGURD 230 - SIGURDPS 230	0.0 degrees fixed phase.  Actual schedule is

-250 MW on the Sigurd-Glen Canyon 230 kV line.

SIERRA		BRDRTNPS 345 - BRDRTWN 345		Regulating to hold schedule of 158 MW from the Northwest to Sierra on the Hill Top-Border Town-Valley Road 345 kV line.

SIERRA	CAL SUB 120 - CAL S PS 120	Regulating to hold 0 MW from PG&E to Sierra on the 2 Drum-Summit 120 kV lines and the Drum-Cisco 60 kV line.

SIERRA	FT.CHUR  120 - FT.CH.PS.120	Regulating to hold schedule of 72 MW from PACE and LADWP to Sierra on the Intermountain-Gonder and the Utah Nev-Pavant 230 kV lines.

SIERRA	SLVR PK   60 - SLVR PS   60	Regulating to hold schedule of 13 MW between SPP and SCE on the Control-Nevada Border 55 kV lines.

SIERRA	SLVR PKX  60 - SLVR PK   60	-40.8 degrees fixed phase.  Operated in series with the SLVR PK-SLVR PS 60 kV phase shifter.

SOCALIF	INYO    115 - INYO PS  115		Regulating to hold 50 MW on the Inyo-Owens 230 kV line.

PHASE SHIFTING TRANSFORMER REPRESENTATION

FOR THE 2008 LSP1-SA BASE CASE

AREA   	PHASE SHIFTING TRANSFORMER	                     REPRESENTATION

WAPA L.C.	GLEN PS 230 - GLENCANY 230	0.0 degrees fixed phase.  Not used to control a schedule.

WAPA R.M.	SANJN PS345 - SAN JUAN345	0.0 degrees fixed phase.  Actual schedule is 118 MW on the Hesperus-San Juan 345 kV line.

WAPA R.M.	SHIP PS 230 - SHIPROCK230	0.0 degrees fixed phase.  Actual schedule is 50 MW on the Lost Canyon-Shiprock 230 kV line.

WAPA U.M.	CRSOVRUM230 - CROS.PHA230	Regulating to hold 40 MW on the Crsovrum-Crsover PHA 230 kV line.

2008 LSP1-SA Power Flow

Analysis

The 2008 LSP1-SA base case represents maximum flow from Northwest to California and northern to southern California under SCIT nomogram limits during heavy spring runoff conditions.

Loads:	60% of summer peak loads in California with normal spring conditions elsewhere.  Late April 2008.

Generation:	Hydro	Thermal

Canada	High	--

Northwest	High	Low

Idaho/Montana	Median	Median

Colorado/Wyoming	Median	Median

Northern California Hydro	High	--

California	High	--

Arizona/New Mexico/southern Nevada	--	Median

Interchange (MW):	Condition	Target	% Rating

Canada-Northwest	Low	500	16%

Northwest-CA/NV (COI/RATS)	Maximum	4800	100%

(PDCI)	Maximum	3100	100%

Path 15 S-N		--	--	--

Wyoming/Idaho-Northwest	Low	400	17%

Montana-Northwest		Moderate	1500	68%

Utah/Colorado-Southwest		Moderate	--	--

Southwest-California (EOR/WOR)	Low	3000/4000	40%

Intermountain-Adelanto DC	Heavy	1800	94%

Midway-Vincent		Maximum	3000	100%

Conditions in the 2008 LSP1-SA base case, relative to the specific goals of the case, are summarized below:

Loads:  Loads represented range from 60 percent to 85 percent of summer 2008 peak in California and from 60 percent to 100 percent of spring 2008 peak elsewhere.

Generation:  Desired patterns were achieved.

| Interchange | Desired | Scheduled | Actual |
| --- | --- | --- | --- |
| Canada-Northwest | 500 | 500 | 501 (c) |
| Northwest-CA/NV - (COI/RATS) | 4800 | 4838 | 3919 (c) |
| Path 15 S-N | -- | -- | -793 (b) |
| Wyoming/Idaho-Northwest | 400 | 1812 | 994 (c) |
| Montana-Northwest | 1500 | 902 | 804 (c) |
| Utah/Colorado-Southwest | -- | (a) | 1086 (b) |
| Southwest-California (EOR/WOR) (500/345 kV System) | 3000/4000 | (a) | 3496/5989 (b) |
| Midway-Vincent | 3000 | 3000 | 2049 (c) |

(a)	A total interchange schedule for this path cannot be determined because some transmission lines included in this total are internal 	to an area and schedules for these lines are not available.

(b)	See Supplemental Line Flow Summary.

(c)	See Area Interchange Diagram.