SPECIAL SPECIFICATION

SECTION 14240

HYDRAULIC ELEVATOR

Page

PART 1 - GENERAL

1.01  Summary.	2

1.02  Definitions.	3

1.03  Design Requirements.	3

1.04  Submittals.	4

1.05  Quality Assurance.	4

1.06  Warranty	5

PART 2 - PRODUCTS

2.01  Manufacturers.	6

2.02  Materials and Components..	6

2.03  Control Systems.	6

2.04  Signal Equipment..	8

2.05  Elevator Service Car Enclosure.	10

2.06  Hoistway Entrances.	12

2.07  Components.	12

PART 3 - EXECUTION

3.01  Examination.	13

3.02  Installation of Elevator System.	13

3.03  Installation of Floor Covering.	14

3.04  Field Quality Control.	14

3.05  Protection..	14

3.06  Demonstration.	15

3.07  Elevator Schedule.	15

SPECIAL SPECIFICATION

SECTION 14240

HYDRAULIC ELEVATOR

PART 1 - GENERAL

1.01    SUMMARY

A. 	This Section includes one custom hydraulic elevator used as both Passenger and Freight Service Car

B. 	Related Sections:  The following sections contain requirements that relate to this Section:

1. 		Section 02200 Earthwork - Excavation to accommodate plunger-cylinder assembly.

2. 		Section 03300 - Cast In Place Concrete Setting of sleeves, inserts, and anchoring devices in concrete is specified in a Division 3 section.

3. 		Section 04200 Concrete Unit Masonry - Setting of sleeves, inserts, and anchoring devices in masonry.

4. 		Section 05500 Metal Fabrications Subsills and structural framing of hoistway entrances.

5. 		Section 09660 - Resilient Flooring, for field applied vinyl tile.

6. 		Section 09900 Painting - for field painting of hoistway entrances.

7. 		Ventilation of hoistway(s) and machine room(s) is specified in Division 15.

8. 		Electrical service to each elevator, including fused disconnect switch, is specified in Division 16 sections.

C. 	Products Furnished But Not Installed Under This Section:  Where indicated, furnish steel tube or well and coordinate delivery with related excavation work.

1.02    DEFINITIONS

A. 	Hydraulic elevators are hereby defined to include systems in which cars are hoisted either directly or indirectly by action of a hydraulic plunger and cylinder (jack); with other components of the work including fluid storage tank, pump, piping, valves, car enclosures, hoistway entrances, control systems, signal equipment, guide rails, electrical wiring, roping, buffers, and devices for operating, dispatching, safety, security, leveling, alarm, maintenance, and similar required performances and capabilities.

1.03   DESIGN REQUIREMENTS

A. 	Provide UL or FM approved heat detectors in Elevator Pit and Elevator Shaft.  Run wiring to DGP to obtain smoke alarm signals.  Terminations in DGP to be performed by Fire Alarm Installer.  Refer to Drawing 104609 E5 for placement of smoke alarms.

B. 	The first Floor landing smoke detector will report an independent N/O contact zone to the Elevator Controller,  via the building fire alarm system Data Gathering Panel (DGP).

C. 	All other smoke detectors listed above will be grouped together to report a single N/O contact zone to the elevator controller, via the building fire alarm system Data Gathering Panel (DGP).

D. 	All the heat detectors will be wired in parallel to shunt trip breakers.

E. 	The sequence of operations will be as follows based on triggering devices in sequence: 1) smoke detector, 2) heat detector, 3) sprinkler head.

1. 		If any smoke detector other than the one at the first floor landing triggers the elevator the elevator controller will send the elevator to the first floor, open the doors and then lock out.  The only override being through fireman service switches, either inside the elevator at the first floor landing.

2. 		If the first floor landing smoke detector triggers, the elevator will proceed to the basement floor, open the doors, and then lock out.

3. 		If any of the heat detectors trigger, the shunt trip breakers will disconnect power to the elevator equipment components.

4. 		By the time any sprinkler heads activates, all elevator equipment will be disconnected from power.

1.04    SUBMITTALS

A. 	Submit the following in accordance with provisions of Section 01300.

B. 	Product Data for each principal component or product of each elevator, including certified test reports on required testing.  Indicate capacities, sizes, performance and operating characteristics, features of control system, finishes, and similar information.  Indicate any variations from specified requirements.

C. 	Shop Drawings including dimensioned drawings showing plans, elevations, sections and large-scale details indicating service at each landing, coordination with building structure and relationships with other construction, and details of car enclosures and hoistway entrances.  Include elevatoring diagrams to indicate elevator service to each level and include excavation requirements for jack.

D. Wiring diagram detailing wiring for power, signal and control systems differentiating clearly between manufacturer-installed wiring and field-installed wiring.  Indicate maximum and average power demands.

E. 	Samples of exposed finishes of car enclosures, hoistway entrances, and signal equipment.  Provide 6-inch- to 8-inch-square samples of sheet materials and 10-inch to 12-inch lengths of running trim members.

F. 	Maintenance Manuals:  Provide three bound manual for elevator with operating and maintenance instructions, parts listing, recommended parts inventory listing, purchase source listing for major and critical components, emergency instructions, and similar information.

1.05   QUALITY ASSURANCE

A. 	Installer Qualifications:  Engage the elevator manufacturer or an installer approved by the elevator manufacturer and who has completed elevator installations similar in material, design, and extent to that indicated for Project which have resulted in installations with a record of successful in-service performance.

B. 	nstaller must have a permanent service branch capable of providing service within two hours after notification.

C. 	Regulatory Requirements:  In addition to local governing regulations, comply with applicable requirements of ASME/ANSI A17.1, Safety Code for Elevators and Escalators (hereafter referred to as the "Code").

D. 	Comply with requirements of NFPA 72 for installation of heat detectors.

1.06     WARRANTY

A. 	Special Project Warranty:  Provide special project warranty, signed by Contractor, Installer, and Manufacturer, agreeing to replace, repair, or restore defective materials and workmanship of elevator work during warranty period.  This warranty shall be in addition to, and not a limitation of, other rights the Owner may have against the Contractor under the Contract Documents.

1. 		Defective is hereby defined to include, but not by way of limitation, operation or control system failures, performances below required minimums, excessive wear, unusual deterioration or aging of materials or finishes, unsafe conditions, the need for excessive maintenance, abnormal noise or vibration, and similar unusual, unexpected, and unsatisfactory conditions.

2. 		Warranty period is 12 months starting on date of Substantial Completion.

B. 	Provide coincidental product warranties where available for major components of elevator work.  Submit with maintenance manuals.

PART 2 - PRODUCTS

2.01    MANUFACTURERS

A. 	Manufacturer:  Subject to compliance with requirements, provide products of one of the following:

1. 		Dover Elevator Corp.

2. 		Montgomery Elevator Co.

3. 		Otis Elevator Co.

2.02    MATERIALS AND COMPONENTS

A. 	General Requirement:  Provide custom designed elevator system that will fulfill the requirements listed in Part 2 Products, and Article 3.07 Elevator Schedule.  Utilize standard components wherever possible as required for a complete system.

B. 	Hydraulic Machines and Elevator Equipment:  Provide manufacturer's standard single-acting under-the-car hydraulic plunger-cylinder unit for each elevator, with electric pump-tank-control system equipment in machine room as indicated.

C. 	Piping:  Provide size, type, and weight piping recommended by manufacturer, and provide isolation couplings to prevent sound/vibration transmissions from power unit.

D. 	Inserts:  Furnish required concrete inserts and similar anchorage devices for the installation of guide rails, machinery, and other components of elevator work where installation of devices is indicated as work of another specification section.

E. 	Car Frame and Platform:  Manufacturer's standard welded steel units.

1. 		Provide special heavy-duty units for C-3 loading, designed to withstand impacts and wheel loadings indicated.

2.03    CONTROL SYSTEMS

A. 	Provide manufacturer's standard control system to provide automatic operation indicated and as defined in the Code as "Operations."

B. 	Emergency Return Operation:  Provide a battery operated return device that, in case of failure of normal power supply sends the elevator to the ground floor, stops, open the doors and then shut down with its doors closed, but subject to door operation from within the car.  Pump motors will cease during emergency operation.

C. 	Provide automatic control of the elevator by means of push buttons in the car, numbered to correspond to floor served, for registering car stops and by up-down push buttons at each intermediate landing, and call push buttons at terminal landings. The momentary pressing of one or more buttons shall dispatch the car to the designated landings in the order in which the landings are reached by the car. Irrespective of the sequence in which buttons are pressed.  Each landing call shall be canceled when answered.  When the car is traveling in the up direction, it shall stop at all floors for which car buttons or up hall buttons have been pressed.  It shall not stop at floor with down buttons only have been pressed, unless the stop for that floor has been registered by a car button or unless the down call is at the highest floor for which any buttons have been pressed. Likewise the pressing up button when the car is traveling in the down direction shall not intercept the travel unless the stop for that floor has been registered by a car button, or unless the up call is the lowest for which any button has been pressed.

D. 	Provide elevator control that is microprocessor based and software oriented.  Provide a distributed system with the main microprocessor located behind the swing return.   Locate the microprocessor door operator in the door operator, and place the microprocessor selector on the car top.  Link together for purposes of communication by a serial communications link.

E. 	The System operates on real time response, demand basis, constantly scanning and calculating the most efficient car assignment.   Use hall call assignments on the state of availability of the car based on the principle of the nearest car selection and priority call assignment.  Car availability status is determined based on the following input:

1. 		Car position

2. 		Direction of car travel

3. 		Car calls registered

4. 		Direction and unanticipated delay

5. 		New calculation

6. 		Reassignment:  Performed for each occurrence.

F. 	Auxiliary Operations/Control: In additions to primary control system features, provide the following controls or operational features for passenger/ freight elevator:

1. 		Independent Service.

2. 		Automatic two way leveling.

3. 		Car top inspection operation.

2.04    SIGNAL EQUIPMENT

A. 	General:  Provide signal equipment for each elevator or group of elevators to comply with requirements indicated below.

1. 		Provide illuminated hall-call and car-call buttons that light up when activated and remain lighted until call or other function has been fulfilled; fabricate of acrylic or other permanent translucent plastic.

2. 		Except for buttons and illuminated signal elements, fabricate signal equipment with exposed surfaces of stainless steel with manufacturer's standard directional polish or satin finish.

3. 		Car Control Stations:  Provide car control station in each car with flush-mounted metal faceplates containing call button for each landing served and other buttons, switches, and controls required for specified car operation and control.  Mount as shown or scheduled at height complying with ASME/ANSI A117.1.  If not otherwise indicated, mount in return panel adjacent to car door.  Provide operating device symbols as required by Code.  Mark other buttons and switches with manufacturer's standard identification for required use or function.

a. 	Provide two-car control stations in each passenger elevator; equip only one with required keyed control switches (if any).

b. 	Where indicated, equip each freight elevator with auxiliary car control station mounted on side of car at height to facilitate operation by lift-truck operator without leaving truck.

4. 		Car Position Indicator:  For passenger elevator cars, provide either illuminated-signal type or digital-display type, located near top of each car or in car control station.  Include direction-of-next-travel signal if not provided in car control station.

a. 	In addition to visual indicator, provide audible signal to indicate to passengers that car is either stopping at or passing each of the floors served.

5. 		Hall Push-Button Station:  Provide hall push-button station at each landing for each elevator or group of elevators, but not less than one station for each 4 elevators in a group.

a. 	For each group of passenger elevators, locate between 2 elevators at center of group or at location most convenient for approaching passengers.  Provide unit with flat faceplate designed for flush-mounting on wall with body of unit recessed in wall.

b. 	Provide 2-button station where passengers can travel either direction; 1-button station where only one direction of travel is available and indicate which direction that is.

6. 		Hall Lanterns:  Provide units with illuminated "up" and "down" signal arrows, but provide single arrow where only one direction is possible.  Provide units projecting from faceplate for ease of angular viewing, except provide flush units where a location in hoistway entrance frame is indicated.  Match materials, finishes, and mounting method of hall push-button stations.

a. 	At manufacturer's option, hall lantern signals may be placed either above or beside each hoistway entrance or in both jambs of entrance frame for each elevator.  Mount at minimum of 6'-0" above finished floor.

b.	At manufacturer's option, for single elevators or for only 2 elevators in a group, hall lantern signals may be placed with hall push-button station, except at ground floor.

c. 	Provide special oversized hall lantern signals at ground floor.

d. 	In conjunction with each hall lantern device, provide an audible signal to indicate that a car is arriving in response to a hall call and to indicate direction of car travel.  Signal shall sound once for up direction of travel and twice for down direction.

1) 	At manufacturer's option, audible signal may be placed on each car.

7. 		Hall Position Indicator:  Provide illuminated-signal type or digital-display type, located above each hoistway entrance at ground floor.  Match materials, finishes, and mounting method of hall push-button stations.

a. 	At manufacturer's option, ground-floor hall lantern signals may be integrated with hall position indicators.

8. 		Telephone:  Provide Model 287RP/H92023 Enhanced Emergency Telephone, manufactured by Gai-Tronics Corporation.  Provide fully ADA compliant telephone set, contained in flush-mounted cabinet complete with identification and instructions for use by sight and hearing impaired persons.  Provide wiring pairs for voice and auxiliary output in traveling cable, and provide and wire to an interface terminal block in the elevator equipment room.

9. 		Provide a fireman's telephone cabinet or fireman's telephone jack in main elevator lobby.

10.	Alarm System:  Provide emergency alarm bell properly located within building and audible outside hoistways, equipped to sound automatically in response to emergency stops and in response to "Alarm" button on each car control station.

2.05     ELEVATOR SERVICE CAR ENCLOSURE

A. 	Provide manufacturer's standard car enclosures of the selections indicated.  Include ventilation, lighting, ceiling finish, wall finish, access doors, doors, power door operators, sill (threshold), trim, accessories, and floor finish unless indicated as not work of this Section.  Provide horizontal sliding doors of manufacturer's standard flush panel type, with operation and number of panels as indicated.  Provide manufacturer's standard protective edge trim system for door and wall panels.

1. 		Materials and Fabrication:  Provide manufacturer's standards, as follows:

a. 	Enameled Steel Panels:  Flush hollow-metal construction, fabricated from ASTM A 366 cold-rolled steel, commercial quality, Class 1, matte finish, stretcher leveled.  Provide with factory-applied baked-on enamel finish; colors as selected by SDR.

b. 	Cast iron sills.

c. 	Fabricate car door frame integrally with front wall of car.

d. 	Fabricate car with recesses and cutouts for signal equipment.

e. 	Luminous Ceiling:  Fluorescent light fixtures and ceiling panels of translucent or open egg-crate plastic, of acrylic or other permanent rigid plastic complying with flammability requirements.

B. 	Elevator Doors:

1. 		Size:  9'-0" high x 6'-0" wide

2. 		Opening:  Center opening (four leaves)

3. 		Two Speed

4. 		Finish:  Baked Enamel

5. 		Color: Custom color to be selected by SDR, to match building scheme.

C. 	Protection Pads: Provide two sets of protective pads, to cover entire wall surface, except controls.  Use one set during construction and moving into building.

1. 		Install pad hooks near car ceiling, as inconspicuous as possible.

2. 		Material:  Heavy quality fire-retardant treated canvas, with two layers of cotton batting securely sewn between canvas cover.

3. 		Provide metal eyelets to connect to pad hooks.

D. 	Handrails:  Provide manufacturer's standard stainless steel handrails on side walls and back wall.

E. 	Cab Lighting:  Manufacturers standard fluorescent.

F. 	Floor:  Prepare to receive field installed vinyl tile.  Allow clearance at doors.

G. 	Door Edge Protective Device:  Infrared light curtain from floor to 6 feet of elevator entrance doors that causes doors to stop and re-open upon detecting an obstruction in the entrance.

H. 	Nudging Feature:  After car doors are prevented from closing for a predetermined adjustable time period, through activation of detection device or door edge protective device, a loud buzzer shall sound and doors shall begin to close at reduced rate of speed.  Doors shall continue to close unless door edge protective device is activated, which shall cause doors to reopen.  Process shall repeat continuously until obstruction is removed from entrance.

2.06    HOISTWAY ENTRANCES

A. Provide manufacturer's standard, hollow metal type, sliding, door-and-frame hoistway entrances complete with track systems, hardware, safeties, sills, and accessories.  Match car enclosure doors for size, number of door panels, and door panel movement.  Provide frame-section size and profile to coordinate with hoistway wall construction as indicated.

1. 		Where gypsum-board wall construction is indicated, fabricate frames with reinforced head sections; provide sufficient strength without support from wall lintels.

B. Materials and Fabrication:  Provide selections indicated that comply with manufacturer's standards as follow:

1. 		Stainless Steel Frames:  Formed stainless steel sheet, AISI Type 302/304 with No. 4 satin finish.

2. 		Stainless Steel Door Panels:  Flush stainless steel construction, AISI Type 302/304 with manufacturer's standard directional polish or satin finish.

3. 		Cast iron sills.

C. 	Provide manufacturer's standard entrance bearing UL B label.

2.07    COMPONENTS

A. 	Provide the following items, whether or not shown on the Drawings.

1. 		Sump Pump

2. 		Fire Service Key

3. 		Light in Elevator pit

4. 		Emergency on/off switch, within reach of door.

PART 3 - EXECUTION

3.01    EXAMINATION

A. 	Prior to commencing elevator installation, examine hoistways, hoistway openings, pits, and machine rooms, as constructed; verify all critical dimensions and examine supporting structure and all other conditions under which elevator work is to be installed.   Do not proceed with elevator installation until unsatisfactory conditions have been corrected.

3.02    INSTALLATION OF ELEVATOR SYSTEM

A. 	Comply with manufacturer's instructions and recommendations for work required during installation.

B. 	Excavation for Jack:  Drill excavation in each elevator pit to accommodate installation of plunger-cylinder unit; comply with applicable requirements of Section 02200 - Excavation.

1. 		Install casings with waterproof seals at pit floor and with waterproof, high-pressure seal at bottom of casings.

2. 		Provide a second (inner) casing with welded waterproof, high-pressure seal at bottom and set inside outer (initial) casing.  At Contractor's option, a PVC pipe.

C. 	Install plunger-cylinder units plumb and accurately centered for elevator car position and travel; anchor securely in place, or fill void space under sand, based on manufacturers recommendation.

D. 	Welded Construction:  Provide welded connections for installation of elevator work where bolted connections are not required for subsequent removal or for normal operation, adjustment, inspection, maintenance, and replacement of worn parts.  Comply with AWS standards for workmanship and for qualifications of welding operators.

E. 	Coordination:  Coordinate elevator work with work of other trades for proper time and sequence to avoid construction delays.  Use benchmarks, lines, and levels designated by Contractor to ensure dimensional coordination of the work.

F. 	Sound Isolation:  Mount rotating and vibrating elevator equipment and components on vibration-absorption mounts, designed to effectively prevent transmission of vibrations to structure and thereby to eliminate sources of structure-borne noise from elevator system.

G. 	Install piping without routing underground, where possible.  Where not possible, cover underground piping with permanent protective wrapping before backfilling.

H. 	Lubricate operating parts of systems, including ropes, if any, as recommended by manufacturers.

I. 	Alignment:  Coordinate installation of hoistway entrances with installation of elevator guide rails for accurate alignment of entrances with cars.  Where possible, delay installation of sills and frames until car is operable in shaft.  Reduce clearances to minimum, safe, workable dimension at each landing.

J. 	Leveling Tolerance:  1/2 inch, up or down, regardless of load and direction of travel.

K. 	Set sills flush with finished floor surface at landings.  Coordinate with other trades to facilitate and ensure proper grouting of sills.

3.03    INSTALLATION OF FLOOR COVERING

A. Install floor covering in accordance with Section 09650.

3.04    FIELD QUALITY CONTROL

A. Acceptance Testing:  Upon nominal completion of elevator installation, and before permitting use of elevator, perform acceptance tests as required and recommended by Code and by governing regulations or agencies.

B. Operating Tests:  Load each elevator to its rated capacity and operate continuously for 30 minutes over its full travel distance, stopping at each level and proceeding immediately to the next.  Record temperature rise of pump motor (except submerged pumps) during 30-minute test period.  Record failures of elevator to perform as required.

C. 	Advise Contractor, SDR, and inspection department of governing agencies in advance of dates and times tests are to be performed on elevators.

3.05    PROTECTION

A. 	Elevator may be used for construction purposes.

B.	Provide suitable protective coverings, barriers, devices, signs, or other methods or procedures to protect elevator work from damage or deterioration.  Maintain protective measures throughout remainder of construction period.

3.06    DEMONSTRATION

A. 	Instruct SDR's personnel in proper use, operations, and daily maintenance of elevators.  Review emergency provisions, including emergency access and procedures to be followed at time of failure in operation and other building emergencies.  Train SDR's personnel in normal procedures to be followed in checking for sources of operational failures or malfunctions.

B. 	Make a final check of each elevator operation with SDR's personnel present and just prior to date of Substantial Completion.  Determine that control systems and operating devices are functioning properly.

3.07    ELEVATOR SCHEDULE*

Capacity:   10,000 Pounds (Passenger and Class 3 loading)

Speed:      75 fpm

Travel Distance: 35'-0"

Landings Served:Basement, 1 & 2

Power supplied:480 volts a.c., 3 phase, 60 hertz

Machinery:  Single stage plunger-cylinder unit

Control System:Selective Collective with independent service.

Signal Equipment:  As specified

Car Enclosure:8'-9" wide by 10'-0" deep 87.5 square feet maximum, by 10'-0" high inside dimension.

6'-0" wide by 9'-0" two speed, center opening, steel car doors, w/luminous plastic egg crate ceiling panels with fixtures above.

Hoistway Entrance: 6'-0" wide by 9'-0" two speed, center opening steel entrance

doors and frames, rated and B labled

END OF SECTION