Power Supply Real Time Controller

# PSRTC

# Operations Guide

# Rev. 2

# 4/4/5

1.0 Introduction	3

2.0 System to be Controlled	5

2.1	Power Supplies	5

2.2	Circuits	7

3.0 PSRTC Control Algorithms	18

3.1 Power Supply Control Function	18

3.1.1 Closed Loop Current Control	21

3.1.2 Voltage Control & Current Clamp	21

3.1.3 Voltage to Alpha Conversion	22

3.1.4 Antiparallel Operation	23

4.0 Load Current Measurements	24

5.0 Protection Features	28

6.0 Simulation Mode	38

7.0  Implementation	41

8.0 Input/Output	42

8.1 Inputs	42

8.2 Outputs	48

9.0 PSRTC Operations	48

9.1 Directory Structure	48

9.2 Input Data File Editing	48

9.3 PSRTC Operations	48

9.2.1 Initialization of User Interface	48

9.2.2 Test Shots	48

9.2.3 Plasma Shots	48

9.2.4 Simulations	48

9.2.5 Viewing Output Data	48

9.2.6 Editing c.d or o.d or t.d	48

9.2.8 Moving Output Files To/From Archive	48

9.2.9 Printing Windows	48

# 1.0 Introduction

The purpose of the NSTX Power Supply Real Time Controller (PSRTC) is to provide a means for real time control of the AC/DC converter system which supplies controlled DC power to the NSTX magnet systems.

# Figure 1:  Conceptual Block Diagram of Control System

# The PSRTC supports two modes of operation:

- “Test” Mode

- All NSTX circuits are driven by the PSRTC in closed loop current control or open loop voltage control, unless locked out, in a fully stand-alone fashion

- “Operations” Mode

- One or more circuits are driven by the Plasma Control System (PCS), via real time voltage commands to the PSRTC, during a specified time interval during a pulse, with full control by the PSRTC outside that interval

- Other circuits are driven by the PSRTC in closed loop current control or open loop voltage control, unless locked out, in a fully stand-alone fashion

- PSRTC (or PCS) performs closed loop current control to initiate the TF coil current, precharge the OH coil, and pre-bias other PF coils

- at the start of a pre-programmed time window, the PCS initiates the plasma and controls plasma current, position, shape, etc. via voltage requests to the PSRTC

- Upon termination of the plasma current the PSRTC (or PCS) extinguishes the current in all coil systems according to pre-programmed current derivatives.

# 2.0 System to be Controlled

## Power Supplies

NSTX utilizes the PPPL "Power Supply" (PS) facility originally built for the Tokamak Fusion Test Reactor (TFTR) project, consisting of thirty-nine (39) modular 12-pulse phase controlled thyristor rectifiers.

• Each PS consists of two 6-pulse "Power Supply Sections" (PSS) which are electrically isolated from each other but subject to the same "Firing Generator" (FG).

• Each PSS is equipped with a full rated bypass module which can carry the load current when the rectifiers are suppressed.

• Each PSS is rated to produce a maximum average DC output voltage of 1012.85VDC (≈1kV), no load, with 13.8kV AC input voltage applied to the converter transformer primary.

• Nominal pulse current rating of each PSS is 24kA-6sec/300sec.

• The FG of each PS controls, in effect, the voltage produced by its two PSS by phase controlling the thyristor firing pulses in accordance with a Control Word received as an input from the PSRTC. The Control Word is an 11 bit digital command.

# Power Supply Control Word

# Bits 1 through 8:

# Firing angle, a.k.a. "alpha" command, 0 = 0o, 255 = 165o

# Bit 9:

# "Convert" command,  1= rectifier thyristors gated, a.k.a. "fired",

0 = rectifier thyristors gate blocked, a.k.a. "suppressed"

# Bit 10:

# Unused

# Bit 11:

"Block Bypass" command, 	1 = bypass thyristors gate blocked, 							0 = bypass thyristors gated

## Switching Power Amplifiers

The Resistive Wall Mode (RWM) coils are powered by switching power amplifiers (SPAs). These are 4-quadrant choppers which can switch a DC source capacitor bank on to the terminals of the RWM coils in a pulse width modulation (PWM) fashion.

The SPAs are controlled by a +/- 10V signal generated in the PSRTC which corresponds to the PWM duty cycle +/-100%.

The DC source capacitor bank is charged by a Transrex power supply called P13. The charging voltage is set by a parameter in the PSRTC input data file VP13SPA which can be up  to 1012.85 volts (the max available Transrex output voltage).

There are three SPA sub-units each rated 1kV/3.333kA-6seconds, once every 300 seconds.

## Circuits

Circuit types to be controlled are as depicted in Figure 2, where the boxed thyristor symbol represents one or more PSS connected in series/parallel combination. The lines connecting the circles represent removable bus links.

# Figure 2:  NSTX Circuit Configurations

a. Type I is a "Unipolar", "2-Wire" circuit. Current flows in one direction through one load coil group.

b. Type II is a "Unipolar", "3-Wire" circuit. Current flows in one direction through two load coil groups; the magnitude of the current may be different in the two "twin" load coil groups.

c. Type III is a "Bipolar", "2-Wire" circuit. Current flows in either direction through one load coil group.

d. Type IV is a "Bipolar", "3-Wire" circuit. Current flows in either direction through two load coil groups; the magnitude and polarity of the current may be different in the two "twin" load coil groups.

e. Type V is the RWM-style circuit consisting of a 4-quadrant chopper as depicted in figure 3.

# Figure 3:  RWM Circuit Configuration

A listing of the NSTX circuits along with type, number of DC poles, number of PSS, and V/I rating is given in Table 1.

# Table 1: NSTX Circuit Types, Poles, PSS, and Ratings

| Circuit | Type | DC Poles | Series/ Parallel PSS | Volts (+/-kV) | Peak Amps (kA) | ESW@ Peak Amps (sec) |
| --- | --- | --- | --- | --- | --- | --- |
| TF | I | 2 | 1/4 | 1 | 35.6 | 5.3 |
| OH | III | 2 | 6/2 | 6 | +/-24 | 0.525 |
| PF1a Upper | IV | 3 | 2/2 | 2 | -5/+15 | 5 |
| PF1a Lower |  |  | 2/2 | 2 | -5/+15 | 5 |
| PF1b | I | 2 | 2/1 | 2 | 20 | 1 |
| PF2 Upper | II | 3 | 2/1 | 2 | 20 | 5 |
| PF2 Lower |  |  | 2/1 | 2 | 20 | 5 |
| PF3 Upper | IV | 3 | 2/1 | 2 | -5/+20 | 5 |
| PF3 Lower |  |  | 2/1 | 2 | -5/+20 | 5 |
| PF4 | I | 2 | 2/1 | 2 | 20 | 5 |
| PF5 | I | 2 | 3/1 | 3 | 20 | 5 |
| CHI | I | 2 | 2/2 | 2 | 50 | 0.8 |
| RWM1 | V | 2 | 2 | 1 | 3.333 | 6 |
| RWM2 | V | 2 |  | 1 | 3.333 | 6 |
| RWM3 | V | 2 |  | 1 | 3.333 | 6 |
| Total | 15 ckt | 27 pole | 45 PSS |  |  |  |

• Layout of the PF coils is given in Figure 4. Typical test shot waveforms, which set the envelope for coil currents during plasma operation, are given in Figure 5. All current and field directions are defined to be (+) when Clockwise (CW) viewed from above. For nominal plasma current direction (CCW)...

- initial Ioh is (-)

-	initial PF1A is (+), then swings (-) while Ip is present to increase triangularity

- PF1B (-) for CHI X-point formation

- PF2 usually (-) to increase plasma elongation

- initial PF3 is (-) to cancel OH stray fields at Ro as required to produce field null for plasma initiation,  but later (+) to provide vertical field for radial position control, difference between PF3U and PF3L provides radial field for vertical position control

- PF4 not typically used

- PF5 (+) to provide vertical field for equilibrium in radial position, and to assist PF3 in creating initial field null at Ro

##### Figure 5: PF Coil Utilization

Figure 6: Test Shot Waveforms

• A listing of the Power Supplies connected in the circuits is given in Table 2. In the NSTX naming, the x in “xS” refers to the series connection sequence where x=1 corresponds to the power supply section into which current first enters, and the y in “yP” refers to the parallel number. For anti-parallel circuits, “1P” is the (+) branch, and “2P” is the (-) branch.

# Table 2: PSS Utilization

| Ckt.# | Coil | NSTX Name | TFTR Name |
| --- | --- | --- | --- |
| P1 | TF | TF-PSS-1S-1P | ETF1-PSS-1A |
|  |  | TF-PSS-1S-2P | ETF1-PSS-1B |
|  | TF Spare | TF-PSS-2S-1P | ETF1-PSS-3A |
|  |  | TF-PSS-2S-2P | ETF1-PSS-3B |
| P1 | TF | TF-PSS-1S-3P | ETF1-PSS-2A |
|  |  | TF-PSS-1S-4P | ETF1-PSS-2B |
| P1 | TF Spare | TF-PSS-2S-3P | ETF1-PSS-4A |
|  |  | TF-PSS-2S-4P | ETF1-PSS-4B |
|  |  | TF-PSS-3S-1P | ETF1-PSS-5B |
|  |  | TF-PSS-3S-2P | ETF1-PSS-5A |
|  |  | TF-PSS-4S-1P | ETF1-PSS-7B |
|  |  | TF-PSS-4S-2P | ETF1-PSS-7A |
|  |  | TF-PSS-5S-1P | ETF1-PSS-9B |
|  |  | TF-PSS-5S-2P | ETF1-PSS-9A |
|  |  | TF-PSS-3S-3P | ETF1-PSS-6B |
|  |  | TF-PSS-3S-4P | ETF1-PSS-6A |
|  |  | TF-PSS-4S-3P | ETF1-PSS-8B |
|  |  | TF-PSS-4S-4P | ETF1-PSS-8A |
|  |  | TF-PSS-5S-3P | ETF1-PSS-AB |
|  |  | TF-PSS-5S-4P | ETF1-PSS-AA |
| P2 | OH | OH-PSS-1S-1P | ETF2-PSS-7B |
|  |  | OH-PSS-2S-1P | ETF2-PSS-7A |
|  |  | OH-PSS-3S-1P | ETF2-PSS-5B |
|  |  | OH-PSS-4S-1P | ETF2-PSS-5A |
|  |  | OH-PSS-8S-2P | ETF2-PSS-2A |
|  |  | OH-PSS-7S-2P | ETF2-PSS-2B |
|  |  | OH-PSS-6S-2P | ETF2-PSS-4A |
|  |  | OH-PSS-5S-2P | ETF2-PSS-4B |
|  |  | OH-PSS-5S-1P | ETF2-PSS-3B |
|  |  | OH-PSS-6S-1P | ETF2-PSS-3A |
|  |  | OH-PSS-7S-1P | ETF2-PSS-1B |
|  |  | OH-PSS-8S-1P | ETF2-PSS-1A |
|  |  | OH-PSS-4S-2P | ETF2-PSS-6A |
|  |  | OH-PSS-3S-2P | ETF2-PSS-6B |
|  |  | OH-PSS-2S-2P | ETF2-PSS-8A |
|  |  | OH-PSS-1S-2P | ETF2-PSS-8B |
|  |  | SPARE | ETF2-PSS-9A |
|  |  | SPARE | ETF2-PSS-9B |
|  |  | SPARE | ETF2-PSS-AA |
|  |  | SPARE | ETF2-PSS-AB |
| P3 | PF1aU | PF1AU-PSS-1S-1P | EEF4-PSS-2B |
|  |  | PF1AU-PSS-2S-1P | EEF4-PSS-2A |
|  |  | PF1AU-PSS-1S-2P | EOH3-PSS-2B |
|  |  | PF1AU-PSS-2S-2P | EOH3-PSS-2A |
| P4 | PF1aL | PF1AL-PSS-1S-1P | EEF3-PSS-1B |
|  |  | PF1AL-PSS-2S-1P | EEF3-PSS-1A |
|  |  | PF1AL-PSS-1S-2P | EEF3-PSS-2B |
|  |  | PF1AL-PSS-2S-2P | EEF3-PSS-2A |
| P5 | PF1b | PF1B-PSS-1S | EEF4-PSS-1B |
|  |  | PF1B-PSS-2S | EEF4-PSS-1A |
| P6 | PF2U | PF2U-PSS-1S | EOH5-PSS-1B |
|  |  | PF2U-PSS-2S | EOH5-PSS-1A |
| P7 | PF2L | PF2L-PSS-1S | EOH3-PSS-1B |
|  |  | PF2L-PSS-2S | EOH3-PSS-1A |
| P8 | PF3U | PF3U-PSS-1S-1P | EOH2-PSS-1B |
|  |  | PF3U-PSS-2S-1P | EOH2-PSS-1A |
|  |  | PF3U-PSS-1S-2P | EEF1-PSS-1B |
|  |  | PF3U-PSS-2S-2P | EEF1-PSS-1A |
| P9 | PF3L | PF3L-PSS-1S-1P | EOH4-PSS-1B |
|  |  | PF3L-PSS-2S-1P | EOH4-PSS-1A |
|  |  | PF3L-PSS-1S-2P | EEF1-PSS-2B |
|  |  | PF3L-PSS-2S-2P | EEF1-PSS-2A |
| P10 | PF5 | PF5-PSS-1S | EOH6-PSS-1B |
|  |  | PF5-PSS-3S | EOH6-PSS-1A |
|  |  | PF5-PSS-2S | EOH5-PSS-2B |
| P11 | CHI | CHI-PSS-1S-1P | EOH1-PSS-1B |
|  |  | CHI-PSS-1S-2P | EOH1-PSS-2B |
|  |  | CHI-PSS-2S-1P | EOH1-PSS-2A |
|  |  | CHI-PSS-2S-2P | EOH1-PSS-1A |
| P12 | PF4 | PF4-PSS-1S | EEF2-PSS-1B |
|  |  | PF4-PSS-2S | EEF2-PSS-1A |
| P13 | RWM | P13-PSS-1S | EEF2-PSS-2B |
|  |  | P13-PSS-2S | EEF2-PSS-2A |

| Ckt.# Coil NSTX Name TFTR Name Type Init P1 TF TF-PSS-1S-1P ETF1-PSS-1A UP TF-PSS-1S-2P ETF1-PSS-1B TF Spare TF-PSS-2S-1P ETF1-PSS-3A UP TF-PSS-2S-2P ETF1-PSS-3B P1 TF TF-PSS-1S-3P ETF1-PSS-2A UP TF-PSS-1S-4P ETF1-PSS-2B P1 TF Spare TF-PSS-2S-3P ETF1-PSS-4A UP TF-PSS-2S-4P ETF1-PSS-4B TF-PSS-3S-1P ETF1-PSS-5B UP TF-PSS-3S-2P ETF1-PSS-5A TF-PSS-4S-1P ETF1-PSS-7B UP TF-PSS-4S-2P ETF1-PSS-7A TF-PSS-5S-1P ETF1-PSS-9B UP TF-PSS-5S-2P ETF1-PSS-9A TF-PSS-3S-3P ETF1-PSS-6B UP TF-PSS-3S-4P ETF1-PSS-6A TF-PSS-4S-3P ETF1-PSS-8B UP TF-PSS-4S-4P ETF1-PSS-8A TF-PSS-5S-3P ETF1-PSS-AB UP TF-PSS-5S-4P ETF1-PSS-AA P2 OH OH-PSS-1S-1P ETF2-PSS-7B BP(+) OH-PSS-2S-1P ETF2-PSS-7A OH-PSS-3S-1P ETF2-PSS-5B BP(+) OH-PSS-4S-1P ETF2-PSS-5A OH-PSS-8S-2P ETF2-PSS-2A BP(-) OH-PSS-7S-2P ETF2-PSS-2B OH-PSS-6S-2P ETF2-PSS-4A BP(-) OH-PSS-5S-2P ETF2-PSS-4B OH-PSS-5S-1P ETF2-PSS-3B BP(+) OH-PSS-6S-1P ETF2-PSS-3A OH-PSS-7S-1P ETF2-PSS-1B BP(+) OH-PSS-8S-1P ETF2-PSS-1A OH-PSS-4S-2P ETF2-PSS-6A BP(-) OH-PSS-3S-2P ETF2-PSS-6B OH-PSS-2S-2P ETF2-PSS-8A BP(-) OH-PSS-1S-2P ETF2-PSS-8B SPARE ETF2-PSS-9A SPARE ETF2-PSS-9B SPARE ETF2-PSS-AA SPARE ETF2-PSS-AB P3 PF1aU PF1AU-PSS-1S-1P EEF4-PSS-2B BP(+) PF1AU-PSS-2S-1P EEF4-PSS-2A PF1AU-PSS-1S-2P EOH3-PSS-2B BP(-) PF1AU-PSS-2S-2P EOH3-PSS-2A P4 PF1aL PF1AL-PSS-1S-1P EEF3-PSS-1B BP(+) PF1AL-PSS-2S-1P EEF3-PSS-1A PF1AL-PSS-1S-2P EEF3-PSS-2B BP(-) PF1AL-PSS-2S-2P EEF3-PSS-2A P5 PF1b PF1B-PSS-1S EEF4-PSS-1B UP PF1B-PSS-2S EEF4-PSS-1A P6 PF2U PF2U-PSS-1S EOH5-PSS-1B UP PF2U-PSS-2S EOH5-PSS-1A P7 PF2L PF2L-PSS-1S EOH3-PSS-1B UP PF2L-PSS-2S EOH3-PSS-1A P8 PF3U PF3U-PSS-1S-1P EOH2-PSS-1B BP(+) PF3U-PSS-2S-1P EOH2-PSS-1A PF3U-PSS-1S-2P EEF1-PSS-1B BP(-) PF3U-PSS-2S-2P EEF1-PSS-1A P9 PF3L PF3L-PSS-1S-1P EOH4-PSS-1B BP(+) PF3L-PSS-2S-1P EOH4-PSS-1A PF3L-PSS-1S-2P EEF1-PSS-2B BP(-) PF3L-PSS-2S-2P EEF1-PSS-2A P10 PF5 PF5-PSS-1S EOH6-PSS-1B UP PF5-PSS-3S EOH6-PSS-1A PF5-PSS-2S EOH5-PSS-2B UP P11 CHI CHI-PSS-1S-1P EOH1-PSS-1B UP CHI-PSS-1S-2P EOH1-PSS-2B CHI-PSS-2S-1P EOH1-PSS-2A UP CHI-PSS-2S-2P EOH1-PSS-1A P12 PF4 PF4-PSS-1S EEF2-PSS-1B UP PF4-PSS-2S EEF2-PSS-1A UP P13 RWM P13-PSS-1S EEF2-PSS-2B Soft Start P13-PSS-2S EEF2-PSS-2A Ckt.# Coil NSTX Name TFTR Name Type Init P1 TF TF-PSS-1S-1P ETF1-PSS-1A UP TF-PSS-1S-2P ETF1-PSS-1B TF Spare TF-PSS-2S-1P ETF1-PSS-3A UP TF-PSS-2S-2P ETF1-PSS-3B P1 TF TF-PSS-1S-3P ETF1-PSS-2A UP TF-PSS-1S-4P ETF1-PSS-2B P1 TF Spare TF-PSS-2S-3P ETF1-PSS-4A UP TF-PSS-2S-4P ETF1-PSS-4B TF-PSS-3S-1P ETF1-PSS-5B UP TF-PSS-3S-2P ETF1-PSS-5A TF-PSS-4S-1P ETF1-PSS-7B UP TF-PSS-4S-2P ETF1-PSS-7A TF-PSS-5S-1P ETF1-PSS-9B UP TF-PSS-5S-2P ETF1-PSS-9A TF-PSS-3S-3P ETF1-PSS-6B UP TF-PSS-3S-4P ETF1-PSS-6A TF-PSS-4S-3P ETF1-PSS-8B UP TF-PSS-4S-4P ETF1-PSS-8A TF-PSS-5S-3P ETF1-PSS-AB UP TF-PSS-5S-4P ETF1-PSS-AA P2 OH OH-PSS-1S-1P ETF2-PSS-7B BP(+) OH-PSS-2S-1P ETF2-PSS-7A OH-PSS-3S-1P ETF2-PSS-5B BP(+) OH-PSS-4S-1P ETF2-PSS-5A OH-PSS-8S-2P ETF2-PSS-2A BP(-) OH-PSS-7S-2P ETF2-PSS-2B OH-PSS-6S-2P ETF2-PSS-4A BP(-) OH-PSS-5S-2P ETF2-PSS-4B OH-PSS-5S-1P ETF2-PSS-3B BP(+) OH-PSS-6S-1P ETF2-PSS-3A OH-PSS-7S-1P ETF2-PSS-1B BP(+) OH-PSS-8S-1P ETF2-PSS-1A OH-PSS-4S-2P ETF2-PSS-6A BP(-) OH-PSS-3S-2P ETF2-PSS-6B OH-PSS-2S-2P ETF2-PSS-8A BP(-) OH-PSS-1S-2P ETF2-PSS-8B SPARE ETF2-PSS-9A SPARE ETF2-PSS-9B SPARE ETF2-PSS-AA SPARE ETF2-PSS-AB P3 PF1aU PF1AU-PSS-1S-1P EEF4-PSS-2B BP(+) PF1AU-PSS-2S-1P EEF4-PSS-2A PF1AU-PSS-1S-2P EOH3-PSS-2B BP(-) PF1AU-PSS-2S-2P EOH3-PSS-2A P4 PF1aL PF1AL-PSS-1S-1P EEF3-PSS-1B BP(+) PF1AL-PSS-2S-1P EEF3-PSS-1A PF1AL-PSS-1S-2P EEF3-PSS-2B BP(-) PF1AL-PSS-2S-2P EEF3-PSS-2A P5 PF1b PF1B-PSS-1S EEF4-PSS-1B UP PF1B-PSS-2S EEF4-PSS-1A P6 PF2U PF2U-PSS-1S EOH5-PSS-1B UP PF2U-PSS-2S EOH5-PSS-1A P7 PF2L PF2L-PSS-1S EOH3-PSS-1B UP PF2L-PSS-2S EOH3-PSS-1A P8 PF3U PF3U-PSS-1S-1P EOH2-PSS-1B BP(+) PF3U-PSS-2S-1P EOH2-PSS-1A PF3U-PSS-1S-2P EEF1-PSS-1B BP(-) PF3U-PSS-2S-2P EEF1-PSS-1A P9 PF3L PF3L-PSS-1S-1P EOH4-PSS-1B BP(+) PF3L-PSS-2S-1P EOH4-PSS-1A PF3L-PSS-1S-2P EEF1-PSS-2B BP(-) PF3L-PSS-2S-2P EEF1-PSS-2A P10 PF5 PF5-PSS-1S EOH6-PSS-1B UP PF5-PSS-3S EOH6-PSS-1A PF5-PSS-2S EOH5-PSS-2B UP P11 CHI CHI-PSS-1S-1P EOH1-PSS-1B UP CHI-PSS-1S-2P EOH1-PSS-2B CHI-PSS-2S-1P EOH1-PSS-2A UP CHI-PSS-2S-2P EOH1-PSS-1A P12 PF4 PF4-PSS-1S EEF2-PSS-1B UP PF4-PSS-2S EEF2-PSS-1A UP P13 RWM P13-PSS-1S EEF2-PSS-2B Soft Start P13-PSS-2S EEF2-PSS-2A |  |
| --- | --- |

# It is noted that:

•  a total of 20 PS Groups are explicitly controlled

• The voltage applied to, or the current produced in, each of the circuits must be explicitly controlled. Therefore, eleven (15) separate circuit control loops are required.

• However, if the bus links are not installed in the Type II and Type IV circuits, then they reduce to Type I and Type III, respectively. In this case, either the U or L part shall be locked out in the control data file and the remaining part used to control the circuit.

e.g. if no link in midpoint of PF1AU and PF1AL, lock out PF1AL and refer all control to PF1AU

# 3.0 PSRTC Control Algorithms

## 3.1 Power Supply Control Function

The Power Supply Control Function is depicted in Figure 7.

• The same basic function is applied to all of the circuits via "do loops". A minor difference is that the final output to the thyristor rectifiers is the firing angle (), whereas the final output to the SPAs is the PWM duty factor (d).

• The output of the control function consists of the firing angle () or duty factor (d) and convert bit commands which are delivered to the PS in the form of the PS Control Words. Since these commands are related to the voltage they are, essentially, voltage commands.

• The voltage commands are derived either from closed loop proportional - integral (PI) current control against a programmable reference, or from a direct voltage request.

• The direct voltage request is obtained from either a programmable reference, or a signal supplied in real time by the PRTC.

• When in the voltage control mode, a current clamp feature is applied if the current approaches a programmable limit. Additional features include rate limiting, and control of anti-parallel rectifiers, including the required  limiting.

##### Figure 7:  Power Supply Control Function

### 3.1.1 Closed Loop Current Control

• Iload is subtracted from pre-programmed Ireference. The difference is the error Ierror.

• Ierror is multiplied by proportional gain Gp, and is integrated and multiplied by integral gain Gi. The sum of these two terms is the voltage requested by current control Vcurrent.

• Integral term is only applied when |Ierror| falls below 2.5% of the reference and is reset each time |Ierror| exceeds 2.5%

### 3.1.2 Voltage Control & Current Clamp

•  Vcommand can be either the programmable reference Vreference or a real time signal provided by the PRTC (VPRTC).

• Time window for VPRTC is set by preprogrammed plasma start and end times.

• Two types of current clamping are imposed when in voltage control mode.

- The first type is based on PI control which generates a voltage Vclamp whenever the load current Iload passes outside input values Iclamp>0 and Iclamp<0

- When the current returns to the allowable range the clamp integrator is reset

  - The net voltage request based on voltage control Vvoltage is the result of the addition of Vcommand and Vclamp

- The second type takes effect when the load current comes within ~2% of the circuit overcurrent setting. In this case a voltage limit V0max is calculated each time step such that the current after the next time step Ii+1 can reach no more than 98% or the overcurrent setting, based on 0.98*Ioc= Ii*exp(-dt/tau)+ V0max/R*( 1-exp(-dt/tau))

### 3.1.3 Voltage to Alpha Conversion

• selection of the source of the voltage request V0 from either voltage control Vvoltage or current control Vcurrent is a function of time.

• V1 is the per unit version of V0 based on V1=V0/Vmax, where Vmax is the maximum no-load voltage available for the circuit in question. Vmax is based on the  programmable number of series PSS (NS), and the primary side AC rms line-to-line source voltage E (nominally 13.8kV at D-site).

• V2 is a rate and magnitude limited version of V1, where the rate limit is  programmable for each circuit and the magnitude limit is -1 to 1 per unit. The rate limit is only applied when the antiparallel mode is in effect (see next section).

• 0 is the firing angle request, and 1 is the firing angle after limiting. If antiparallel operation is not in effect, then the allowable range of 1 is 0 to max , where max is the maximum permissible delay angle. It is calculated based on the load current per PSS, equal to Iload/NP where NP is the number of parallel PSS branches in the circuit being controlled,  the AC source frequency , the commutating inductance Lc, and the AC source voltage E, along with a  programmable inversion margin angle .

• If antiparallel operation is in effect, then the minimum permissible delay angle min is set equal to 180 - max , so that the allowable range of alpha is therefore min ≤ 1 ≤ max in the antiparallel mode.

• In the case of the RWM/SPA circuits, 1 is set directly equal to V2 which is equivalent to the PWM duty cycle “d”.  Furthermore, the RWM1 2 storage location is used for the SPA DC source P13 firing angle, and RWM1 ncvt2 for the convert bit.

### 3.1.4 Antiparallel Operation

• permits bipolar current flow in the load without delay around current zero

• antiparallel converters (a.k.a. the (#1) and (#2) converters) must be operated at symmetric (about 90 degrees) delay angles min and max, i.e.

 2 = 180 -  1

• this is required to minimize the circulating current which is impeded only by the Current Limiting Reactors (CLRs).

• the antiparallel mode is declared when the magnitude of the load current Iload falls below a threshold Ithresh

• conditioned by a hysteresis function which only declares the mode to be true if the previous magnitude exceeded the threshold

• switch is provided to enable/disable antiparallel operation for each circuit.

# 4.0 Load Current Measurements

• PSS branch currents are measured by two types of DC current transducers

- Halmar “zero flux” type

- high accuracy (0.1%) if well calibrated and installed

- excellent frequency response

- Shunt “leaf” type

- Simple and reliable

- good accuracy (0.5%)

- moderate frequency response

• Redundant measurements are (ideally) provided in each branch

- except PF1A and PF3, which are lacking a complete set of branch currents

- via control input data, PF1A and PF3 the total current is substituted for the branch current with scaling factor reduced by 1/2

- in some cases (low inductance circuits) it has been found necessary to drop the shunt measurement due to amplification of power supply ripple (Lshunt * dIload/dt, and consequential control loop response), and substitute the Halmar (loss of redundancy)

• RWM currents are measured by tranducers built into the SPA units

• Signal processing (buffer and fan out) by “Halmar Signal Conditioner” (HSC)

• Interface with control computer via “Data Acquisition System” (DAS)

• Interface with EPICs (and MDS+) via CAMAC digitizers

• List of DCCT signals is given in Table 4

| Table 4: Current Measurements |  |  |
| --- | --- | --- |
| Imeas | Ckt/Sys | kA | D-site Identifier | SKY Ch. | Dig. | Comment |
| 1 | OH (+) Branch | 25 | ETF2-MN1-MH1-I | 5 | pc_oh_br_1_cur_1 |  |
| 2 | OH (-) Branch | 25 | ETF2-MN3-MH1-I | 6 | pc_oh_br_2_cur_1 |  |
| 3 | PF1a Upper (+) Branch | 25 | PF1AU-CTD-MH1 | 8 | pc_pf1au_cur_1 | ∑Current substituting for PSRTC branch current |
| 4 | PF1a Upper (-) Branch | na | na | na | na |  |
| 5 | PF1a Lower (+) Branch | 50 | EFVC-MN2-MH1-I | 7 | pc_pf1al_cur_1 | ∑Current substituting for PSRTC branch current |
| 6 | PF1a Lower (-) Branch | na | na | na | na |  |
| 7 | PF1b | 25 | EEF1-MN1-MH1-I | 9 | pc_pf1b_cur_1 |  |
| 8 | PF2 Upper | 50 | EOH5-CTD-MH1-I | 27 | pc_pf2u_cur_1 |  |
| 9 | PF2 Lower | 50 | EOH3-CTD-MH1-I | 26 | pc_pf2l_cur_1 |  |
| 10 | PF3 Upper (+) Branch | 50 | EOH2-CTD-MH1-I | 29 | pc_pf3u_cur_1 | ∑Current substituting for PSRTC branch current |
| 11 | PF3 Upper (-) Branch | 25 | EOH2-MN2-MH1-I | 34 | pc_pf3u_br_2_cur_1 |  |
| 12 | PF3 Lower (+) Branch | 25 | EOH4-CTD-MH1-I | 28 | pc_pf3l_cur_1 | ∑Current substituting for PSRTC branch current |
| 13 | PF3 Lower (-) Branch | 25 | EOH4-MN2-MH1-I | 33 | pc_pf3l_br_2_cur_1 |  |
| 14 | PF5 | 50 | EOH6-CTD-MH1-I | 30 | pc_pf5_cur_1 |  |
| 15 | CHI Branch 1 | 25 | EOH1-MN2-MH1-I | 36 | pc_chi_br_1_cur_1 |  |
| 16 | CHI Branch 2 | 25 | EOH1-MN3-MH1-I | 35 | pc_chi_br_2_cur_1 |  |
| 17 | TF Branch 1 | 25 | ETF1-MN1-MH1-I | 1 | pc_tf_br_1_cur_1 |  |
| 18 | TF Branch 2 | 25 | ETF1-MN2-MH1-I | 2 | pc_tf_br_2_cur_1 |  |
| 19 | TF Branch 3 | 25 | ETF1-MN3-MH1-I | 3 | pc_tf_br_3_cur_1 |  |
| 20 | TF Branch 4 | 25 | ETF1-MN4-MH1-I | 4 | pc_tf_br_4_cur_1 |  |
| 21 | PF4 | 30 | PF4-MN1 | 16 | pc_pf4_cur_1 |  |
| 22 | SPA1 | 3.333 |  | 65 |  |  |
| 23 | SPA2 | 3.333 |  | 67 |  |  |
| 24 | SPA3 | 3.333 |  | 69 |  |  |
| 1 | OH (+) Branch | 25 | ETF2-CTD-MH1-I | 21 | pc_oh_br_1_cur_2 |  |
| 2 | OH (-) Branch | 25 | ETF2-CTD-MH2-I | 22 | pc_oh_br_2_cur_2 |  |
| 3 | PF1a Upper (+) Branch | 25 | PF1AU-CTD-MH2 | 24 | pc_pf1au_cur_2 | ∑Current substituting for PSRTC branch current |
| 4 | PF1a Upper (-) Branch |  |  |  |  |  |
| 5 | PF1a Lower (+) Branch | 50 | EFVC-CTD-MH1-I | 23 | pc_pf1al_cur_2 | ∑Current substituting for PSRTC branch current |
| 6 | PF1a Lower (-) Branch |  |  |  |  |  |
| 7 | PF1b | 25 | EEF1-CTD-MH1-I | 25 | pc_pf1b_cur_2 |  |
| 8 | PF2 Upper | 25 | ESHUNT-OH5 | 11 | pc_pf2u_cur_2 |  |
| 9 | PF2 Lower | 25 | ESHUNT-OH3 | 10 | pc_pf2l_cur_2 |  |
| 10 | PF3 Upper (+) Branch | 25 | ESHUNT-OH2 | 13 | pc_pf3u_cur_2 | ∑Current substituting for PSRTC branch current |
| 11 | PF3 Upper (-) Branch | 25 | Future |  |  |  |
| 12 | PF3 Upper (+) Branch | 25 | ESHUNT-OH4 | 12 | pc_pf3l_cur_2 | ∑Current substituting for PSRTC branch current |
| 13 | PF3 Lower (-) Branch | 25 | Future |  |  |  |
| 14 | PF5 | 25 | ESHUNT-OH6 | 14 | pc_pf5_cur_2 |  |
| 15 | CHI Branch 1 | 50 | Future |  |  |  |
| 16 | CHI Branch 2 | 25 | Future |  |  |  |
| 17 | TF Branch 1 | 25 | ETF1-CTD-MH1-I | 17 | pc_tf_br_1_cur_2 |  |
| 18 | TF Branch 2 | 25 | ETF1-CTD-MH2-I | 18 | pc_tf_br_2_cur_2 |  |
| 19 | TF Branch 3 | 25 | ETF1-CTD-MH3-I | 19 | pc_tf_br_3_cur_2 |  |
| 20 | TF Branch 4 | 25 | ETF1-CTD-MH4-I | 20 | pc_tf_br_4_cur_2 |  |
| 21 | PF4 | 30 | PF4-MN2 | 32 | pc_pf4_cur_2 |  |
| 22 | SPA1 | 3.333 |  | 66 |  |  |
| 23 | SPA2 | 3.333 |  | 68 |  |  |
| 24 | SPA3 | 3.333 |  | 70 |  |  |
|  | CHI ∑ Current | 50 | EOH1-MN1-XT1-I | 15 | pc_chi_tot_cur_1 |  |
|  | CHI ∑ Current | 50 | EOH1-CTD-MH1-I | 31 | pc_chi_tot_cur_1 |  |

• Polarity considerations

- all coil currents defined as (+) when clockwise viewed from above

- some DCCTs are installed backwards, but inverted via a control input variable

- some DCCTs are on coil side of the bus links, others on power supply side (and subject to polarity reversal (w.r.t. coil) when links are reversed; the software accounts for this

• Offset subtraction

- 	just prior to each pulse, average of last 100 samples of current is taken as the offset and subtracted from measurements during pulse

• During pulse, at each time step, the difference between the magnitude of the two redundant measurements is calculated and compared to a programmable allowable as a check for the validity of the measurements.

- The measurement with the larger magnitude taken as the branch current, corrected for polarity, and used for further processing.

• 	The coil currents Iload are obtained from the sum of the individual branch measurements, and are always handled with respect to the formal definition of current direction

# 5.0 Protection Features

# Following protection features are provided in the PSRTC:

• instantaneous overcurrent protection

- branch (during standby and pulse modes)

- load (pulse mode only)

• single pulse ∫i2(t)dt protection

• adiabatic coil temperature rise

• axial force protection for PF coils

• axial force protection for PF coils

Table 5: Coil Parameters

| Coil | R (center) | ∆R | Z (center) | ∆Z | Turns | Fill | Turn CSA | R(12C) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | (in) | (in) | (in) | (in) |  |  | (in^2) | (mOhm) |
| OH | 5.2088 | 1.7335 | 41.7490 | 83.4980 | 482 | 0.7403 | 0.2223 | 93.17 |
| PF1a | 7.2403 | 1.6265 | 62.6215 | 9.1820 | 20 | 0.6956 | 0.9987 | 1.15 |
| PF1b | 11.9768 | 3.3055 | 71.8570 | 7.5030 | 32 | 0.6702 | 0.5195 | 3.04 |
| PF2a | 31.4634 | 6.4060 | 76.1225 | 2.6760 | 14 | 0.7409 | 0.5195 | 4.01 |
| PF2b | 31.4634 | 6.4060 | 72.9385 | 2.6760 | 14 | 0.7409 | 0.9072 |  |
| PF3a | 58.8370 | 7.3400 | 64.3114 | 2.6760 | 15 | 0.6928 | 0.9072 | 8.03 |
| PF3b | 58.8370 | 7.3400 | 61.1274 | 2.6760 | 15 | 0.6928 | 0.9072 |  |
| PF4b | 70.6540 | 3.6040 | 31.7800 | 2.6760 | 8 | 0.7525 | 0.9072 | 10.96 |
| PF4c | 71.1210 | 4.5380 | 34.9640 | 2.6760 | 9 | 0.6723 | 0.9072 |  |
| PF5a | 78.5280 | 5.3500 | 25.6840 | 2.6980 | 12 | 0.7689 | 0.9072 | 16.81 |
| PF5b | 78.5280 | 5.3500 | 22.7440 | 2.6980 | 12 | 0.7689 | 0.9248 |  |
| TF Inner | 1.1090 | 2.2180 | 55.7500 | 111.5000 | 12 |  | 1.0540 | 6.32 |
| TF Outer | 3.0750 | 1.5460 | 49.6875 | 99.3750 | 24 |  | 1.0530 |  |

| Table 6: Coil Ratings Circuit | Iesw | Tesw | I2T |
| --- | --- | --- | --- |
|  | (kA) | (sec) | (ka^2-sec) |
| OH | 24.0 | 0.53 | 302 |
| PF1aU,L | 24.0 | 2.50 | 1440 |
| PF1b | 20.0 | 1.00 | 400 |
| PF2U,L | 20.0 | 5.00 | 2000 |
| PF3U,L | 20.0 | 5.00 | 2000 |
| PF4 | 20.0 | 5.00 | 2000 |
| PF5 | 20.0 | 5.00 | 2000 |
| RWM1,2,3 | 5.0 | 2.50 | 63 |
| TF | 71.2 | 1.32 | 6700 |
| CHI | 50.0 | 1.0 | 2400 |

Table 7: Coil Thermal Parameters

| Circuit | Thermal Res | Heat Cap | Thermal Tau |
| --- | --- | --- | --- |
|  | (degC/kW) | (kJ/degC) | (sec) |
| OH | 0.65 | 397 | 258 |
| PF1aU,L | 1.23 | 27 | 33 |
| PF1b | 1.22 | 71 | 86 |
| PF2U,L | 0.70 | 284 | 200 |
| PF3U,L | 1.05 | 569 | 596 |
| PF4 | 0.81 | 364 | 296 |
| PF5 | 0.18 | 1239 | 220 |
| RWM1,2,3 | 293.33 | 15 | 4288 |
| TF | 0.054 | 486 | 26 |

• RMS current checks (based on continuous simulation of heating (during pulse) and cooling (between pulses) of DC cable systems. Cable parameters are given in Table 8.

# Table 8: DC Cable Parameters

| System | Cable Size | #Parallel | Resistance | Cp | Tr | Tau |
| --- | --- | --- | --- | --- | --- | --- |
|  | MCM |  | µΩ/in | J/degC-in | degC/W-in | minute |
| OH | 1000 | 1 | 0.866 | 44.2 | 39.0 | 28.6 |
| PF1a U &L | 1000 | 2 | 0.433 | 88.3 | 19.4 | 28.6 |
| PF1a Midpoint | 1000 | 2 | 0.433 | 88.3 | 19.4 | 28.6 |
| PF1b | 750 | 2 | 0.577 | 66.2 | 20.8 | 23.0 |
| PF2 U&L | 1000 | 3 | 0.289 | 132.5 | 12.9 | 28.6 |
| PF2 Midpoint | 1000 | 3 | 0.289 | 132.5 | 12.9 | 28.6 |
| PF3 U&L (+) | 750 | 1 | 1.155 | 33.1 | 68.6 | 37.9 |
| PF3 U&L (-) | 1000 | 3 | 0.289 | 132.5 | 12.9 | 28.6 |
| PF3 U&L Midpoint | 1000 | 3 | 0.289 | 132.5 | 12.9 | 28.6 |
| PF4 |  |  |  |  |  |  |
| PF5 | 1000 | 3 | 0.289 | 132.5 | 12.9 | 28.6 |
| RWM | 500 | 1 | 2.16 | 22.1 | 22.9 | 17.2 |
| TF | 1000 | 5 | 0.173 | 220.8 | 7.8 | 28.6 |
| CHI | 750 | 3 | 0.385 | 99.4 | 22.9 | 37.9 |

• Launching load (product of Ioh and Ipf1b shall be ≥ preprogrammed level) (Note: this interlock is still present but not used)

• CHI/TF Interlock (CHI suppressed unless |Itf| ≥ preprogrammed level)

Axial Loads

Influence coefficients given in are used to calculate the force on PF coil x due to its current and the forces in the other y coils as follows…

This calculation is performed once each time step for each of the PF coils, namely OH, PF1aU, PF1aL, PF1b, PF2U, PF2L, PF3U, PF3L, PF4, PF5. Limits are included in the PSRTC c.d file for each coil. If the sign of the limit is positive, then a positive force greater than the limit causes a trip, and if the sign of the limit is negative, then a negative force less than the limit causes a trip. The influence coefficients are hard coded into the “rtc_init.f” program. The data generated for the forces on each coil is available as an output which can be selected in the “o.d” file and viewed after each pulse via “readrtc”.

Peak Pressure on TF Joint

The first step in calculating the pressure is to calculate the prospective moments in-plane (IP) and out-of-plane (OOP). The in-plane moment is assumed proportional to the square of the TF current. A moment of 70653 in-lbf is generated on the outer layer flags and links at 6kG (71.166kA). So the applied EM moment at any value of  current is…

The amount of moment which ends up a the joint depends on how much is reacted by the structure. Structural coefficients are based on analysis of field measurements. These are used to estimate the amount of the moment which is reacted by the joint…

Similar calculations are performed for the out-of-plane moment based on the influence matrix given for the our-of-plane moment, and on structural coefficients based on analysis of field measurements. These take the following form…

The coefficients Cx_OOP are the product of the aforementioned influence matrix coefficients and the structural coefficients, and are hard coded into “rtc_init.f”

The data generated for the in-plane and out-of-plane moments is available as an output which can be selected in the “o.d” file and viewed after each pulse via “readrtc”..

Once the moments are known then peak pressure at the joint can be calculated based on the linear pressure distribution model shown in figures 8 and 9 .

Figure 8

Figure 9

The maximum pressure is compared each time step to an allowable value which is entered in the “c.d” file.

Force On Friction Interface Between Flag Box and Hub

A simplified model is used to estimate the friction shear load on the TF flag box-to-hub interface as shown in figure 10.

Figure 10

Prior analysis showed that the innermost stud location (F1) on the outer layer flag box interface with the middle hub disk is the one most highly stressed. For this case the PSRTC calculations for the out-of-plane shear load are as follows…

…where Fbundle, Flateral ,and Mlateral are forces and moments calculated via the influence matricies given in [1].

The in-plane shear load is based on the shear load calculated per square ampere of TF current at 6kG…

Finally the net load is the vector sum of the in-plane and out-of-plane loads…

The calculated force is compared to a limit value set in the “c.d” file. The data generated for the force is available as an output which can be selected in the “o.d” file and viewed after each pulse via “readrtc”.

# 6.0 Simulation Mode

In order to test the PSRTC, a simulation package is included which interfaces with the real time control code at the same points of input and output as in normal operation (the inputs being the PSS branch currents and the outputs being the a commands to the power supplies.

# PPPL’s LRSIM code is used.

# Following features are included:

• Transient solution of mutually coupled L/R circuits

- at present, only the coils are included

- a more extensive filament model of passive structure may be added in the future

• 10 simulation time steps per control system time step

• Simulation of latency of input data by utilization of simulation results obtained midway between control system time steps  as inputs to control algorithm

• Simulation of transient heating of coils and its effect on ohmic resistance

• Simulation of delays and limits of power supplies; however individual thyristor commutations are not modeled

Nominal mutual inductance matrix, and resistance vector, is given in Table 8.

Table 8: Mutual Inductances (mH)

and Resistances (mΩ)

|  | OH | 1aU | 1aL | 1b | 2U | 2L | 3U | 3L | 5 | CHI | TF |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| OH | 13.000 | 3.511 | 3.511 | 0.374 | 0.276 | 0.276 | 0.295 | 0.295 | 0.527 | 0.000 | 0.000 |
| 1aU | 3.511 | 4.470 | 0.000 | 0.000 | 0.072 | 0.001 | 0.060 | 0.005 | 0.042 | 0.000 | 0.000 |
| 1aL | 3.511 | 0.000 | 4.470 | 0.090 | 0.001 | 0.072 | 0.005 | 0.060 | 0.042 | 0.000 | 0.000 |
| 1b | 0.374 | 0.000 | 0.090 | 0.536 | 0.002 | 0.186 | 0.007 | 0.101 | 0.054 | 0.000 | 0.000 |
| 2U | 0.276 | 0.072 | 0.001 | 0.002 | 1.980 | 0.010 | 0.731 | 0.041 | 0.346 | 0.000 | 0.000 |
| 2L | 0.276 | 0.001 | 0.072 | 0.186 | 0.010 | 1.980 | 0.041 | 0.731 | 0.346 | 0.000 | 0.000 |
| 3U | 0.295 | 0.060 | 0.005 | 0.007 | 0.731 | 0.041 | 5.180 | 0.166 | 1.490 | 0.000 | 0.000 |
| 3L | 0.295 | 0.005 | 0.060 | 0.101 | 0.041 | 0.731 | 0.166 | 5.180 | 1.490 | 0.000 | 0.000 |
| 5 | 0.527 | 0.042 | 0.042 | 0.054 | 0.346 | 0.346 | 1.490 | 1.490 | 12.300 | 0.000 | 0.000 |
| CHI | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.080 | 0.000 |
| TF | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 4.180 |
| Resist | 97.400 | 2.800 | 2.800 | 2.760 | 4.170 | 4.170 | 8.340 | 8.340 | 17.400 | 7.000 | 4.690 |

Note: PF1A smoothing reactor inductances are included in the above.

• External Circuit Resistances (ECR in c.d file), due to the cabling within the power supply building, and that from the power supply building, as measured by PTP-ECS-029, is listed in Table 9.

# Table 9: External Circuit Resistances

| Circuit | Resistance (mOhm) |
| --- | --- |
| OH | 3.32 |
| 1aU | 10.0 |
| 1aL | 10.0 |
| 1b | 5.86 |
| 2U | 2.61 |
| 2L | 2.35 |
| 3U | 4.85 |
| 3L | 4.84 |
| 5 | 2.82 |
| CHI | 3.76 |
| TF (2 parallels) | 1.21 |
| TF (4 parallels) | 1.02 |

Note: PF1A smoothing reactor resistances are included in the above.

# 7.0  Implementation

The PSRTC is written primarily in FORTRAN. Some hardware specific adjuncts required for real time execution are written in C. The FORTRAN part can run on any platform.

# System consists of…..

• Force host computer

- ethernet connectivity

- user interface

• Skybolt II real time computer

- four parallel G4 processors on motherboard with Front Panel Data Port (FPDP)

• VME based acquisition system (DAS)

- two crates in NSTX Test Cell

- one crate in junction area

- Fiber Optic Interface Boards (FOIBS) connecting the crates

• Power Conversion (PC) Link driver

- interface to serial command link which distributes commands to power supplies

• The PSRTC occupies one of the four parallel processors; the other three are available to the PRTC.

• The control system update rate is 1kHz (once per millisecond).

# 8.0 Input/Output

## 8.1 Inputs

# PSRTC requires the following input files:

c.d – contains control data (Table 10)

t.d – contains timing data (Table 11)

s.d – contains simulation data (Table 12)

o.d – contains selection of variables to be stored in output file (maximum of 50 may be saved during any particular shot). For each variable listed, a “1” indicates save, a “0” indicates do not save

cntmtx.d – contains mutual inductance matrix and resistance vector (see Table 8 in prior section of this document)

Table 10: Input File c.d

| Name | i | j | k | Description |
| --- | --- | --- | --- | --- |
| NMODE |  |  |  | Mode (0=norm, 1=test) |
| NSUBMODE |  |  |  | Submode (0=ops, 1=simulation) |
| NLOCK | 1-12 |  |  | Lockout (0=in, 1=out); locked out circuits not controlled, only suppress/bypass command is given |
| NPC | 1-12 |  |  | Plasma Control Enable (0=disabled, 1=enabled); this controls whether or not a circuit will accept voltage reference from plasma control |
| GAIN | 1-12 | 1-2 | 1 | Proportional Gain during a pulse, in ohms (volts per amp error) |
| GAIN | 1-12 | 1-2 | 1 | Integral Gain during a pulse, in farads (volts per amp-sec error) |
| GAIN | 1-12 | 1-2 | 2 | Prop Gain, Clamp |
| GAIN | 1-12 | 1-2 | 2 | Int Gain, Clamp |
| NMEAS | 1-19 | 1-2 |  | Measurement #'s (1 to 38) of two redundant branch current measurements) |
| NPMEAS | 1-19 | 1-2 |  | Measurement Polarity w.r.t Coil with bus links in normal position |
| NLMEAS | 1-19 | 1-2 |  | Measurement Location 1=SDS side (does not change polarity with link reversal), -1=PS Side (changes polarity with link reversal) |
| FSMEAS | 1-19 | 1-2 |  | Full Scale of Measurement in kA |
| NCB | 1-19 | 1-2 |  | Circuit # of in which branch is located |
| KPB | 1-19 |  |  | Branch Polarity & Multiplier, used in simulation only; if KPB>0, current can only be positive in branch, if KPB<0, current can only be negative in branch; current in branch = KPB*ILOAD/NP |
| DIMAX | 1-19 |  |  | Allowable DCCT Discrepancy (difference between redundant measurements) in kA |
| NPLINK | 1-12 |  |  | Bus Link Polarity (1=normal, -1=reverse) |
| NP | 1-12 |  |  | # Parallel branches feeding circuit |
| NS | 1-12 |  |  | # Series power supply sections feeding circuit |
| ICLP | 1-12 |  |  | (+) Current Clamp Level in kA |
| ICLN | 1-12 |  |  | (-) Current Clamp Level in kA |
| VAC |  |  |  | AC Source Voltage (13.8kV Level) in kV |
| FAC |  |  |  | AC Source Frequency in Hz |
| GAMMA | 1-12 |  |  | Margin angle gamma (max alpha = 180 - gamma - commutation angle) in degrees |

# Table 9: Input File c.d (con’t)

| Name | i | j | k | Description |
| --- | --- | --- | --- | --- |
| LC | 1-12 |  |  | Commutating Inductance (nominal value = 22 microhenries) in microhenries |
| VDOTMAX | 1-12 |  |  | Maximum dVpu/radian for rate limiting; normal sine wave as maximum of 0.637 per unit per radian |
| NAP | 1-12 |  |  | Antiparallel Enable (0=disable, 1=enable) |
| NAPBLOCK | 1-12 |  |  | Antiparallel Initial State Block (0=no block, 1=block antiparallel until first zero crossing) |
| ITHRESH | 1-12 |  |  | Antiparallel Current Magnitude Threshold in kA |
| IBOC | 1-19 | 1-2 |  | Branch Overcurrent Standby State in kA |
| IBOC | 1-19 | 1-2 |  | Branch Overcurrent Pulse State in kA |
| ILOC | 1-12 |  |  | Load Overcurrent Pulse State in kA |
| I2TMAX | 1-12 |  |  | I2T Limit in kA^2-sec |
| NPSUM | 1-22 | 1-2 |  | Circuit # of ILOAD in to DC Pole |
| NPSUM | 1-22 | 1-2 |  | Circuit # of ILOAD out of DC Pole |
| R20POLE | 1-22 |  |  | Pole 20C Electrical Resistance in mircoohm/inch |
| TRPOLE | 1-22 |  |  | Pole Thermal Resistance in degC-inch/watt |
| TCPOLE | 1-22 |  |  | Pole Thermal Capacitance in Joule/degC-in |
| NPPOLE | 1-22 |  |  | Polarity Constraint on Pole (0=no constraint, 1=(+) only, -1=(-) only) |
| T0POLE |  |  |  | Ambient Temperature for Cables in degC |
| TMPOLE |  |  |  | Allowable Temperature for Cables in deg C |
| ALAUNCH |  |  |  | Allowable Ioh*Ipf1b in kA^2 |
| ITFMIN |  |  |  | Minimum ¦Itf¦ for CHI in kA |
| ICHI0 |  |  |  | Minimum ¦Ichi¦ for ITFMIN check in kA |
| SCD | 1-12 |  |  | Shutdown Current Derivative, takes effect after plasma control drops out (NPCON=0) in kA/mS |
| TCCOIL | 1-12 |  |  | Coil Thermal Capacity in kJoule/degC |
| COEFF |  |  |  | Copper Thermal Coefficient of Resistance, nominally 0.0041 |
| T0COIL | 1-12 |  |  | Coil Water Inlet Temperature, nominally 10 deg C |
| FINV |  |  |  | Max invert voltage fraction, nominally -0.666 |
| ECR | 1-12 |  |  | External Circuit Resistance, exc'l CLR, in mOhm |
| ECL | 1-12 |  |  | External Circuit Inductance, exc'l CLR, in microhenry |
| RPSS | 1-12 |  |  | Power Supply Section Equiv Resistance, nominally 16 mOhm |

# Table 10: Input File t.d

| Name | Circuit | Description |
| --- | --- | --- |
| TSOP |  | Time of SOP clock event, relative to t0 |
| TPCSTART |  | Time to start plasma control, relative to t0 |
| TPCEND |  | Time to end plasma control, relative to t0 |
| TIRESET | 1-12 | No Longer Used |
| NBPOINT | 1-12 | Number of breakpoints to follow for each circuit |
| BPOINT |  | Time (relative to t0), data (kA or kV), and mode (0=current control, 1=voltage control) |

# Table 11: Input File s.d

| Name | Description |
| --- | --- |
| NCHIDSO | Simulate bit which =1 if CHI SDS open, =0 if closed |
| NHCSTF | Simulate status of TF HCS, 0 = no fault, 1 = fault |
| NHCSOH | Simulate status of OH HCS, 0 = no fault, 1 = fault |
| NHCSPFCHI | Simulate status of PFCHI HCS, 0 = no fault, 1 = fault |
| FMG | Simulate status of MG frequency, in Hz |
| VMG | Simulate status of MG voltage, in volts |
| NPCREADY | Simulate status of ready flag from plasma control, 0 = not ready, 1 = ready |
| NOUTDT | No longer used |

## 8.2 Outputs

# PSRTC produces an output file called o_*.d, where * may be…

- a numeric sequence

- date and time

- shot number

o_*.d contains the data collected for the variables identified in o.d (up to 50), for each millisecond, followed by a list of alarms and faults which may have occurred, followed by a list of the names of the collected data