Vessel Sanitation Program Construction Guidelines

TURKU DRAFT

July 2005

Department of Health and Human Services

Centers for Disease Control and Prevention

National Center for Environmental Health

Vessel Sanitation Program

Atlanta, GA and Ft Lauderdale, FL

Proposed Edits/Changes are Highlighted in yellow.

Proposed Deletions have a strikethrough mark.

Proposed changes from Turku are in Blue with Yellow Highlighting

Comments or Questions are in Blue

Vessel Sanitation Program

Centers for Disease Control and Prevention

4770 Buford Highway, NE F-23

Atlanta, GA 30341-3724

Phone: (770) 488-7070

Fax: (770) 488-4127

E-mail: vsp@cdc.gov

Vessel Sanitation Program

Centers for Disease Control and Prevention

1850 Eller Drive, Suite 101

Ft Lauderdale, FL 33316-4201

Phone: (800) 323-2132 or (954) 356-6650

Fax: (954) 356-6671

E-mail: vsp@cdc.gov

The VSP Construction Guidelines and updates are available at www.cdc.gov/nceh/vsp

# 1.0 Background and Purpose

The Centers for Disease Control and Prevention (CDC) established the Vessel Sanitation Program (VSP) in 1975 as a cooperative endeavor with the cruise vessel industry. VSP’s goal is to assist the industry to develop and implement comprehensive sanitation programs to protect the health of passengers and crew aboard cruise vessels.

Every cruise vessel that has a foreign itinerary, carries 13 or more passengers, and calls on a U.S. port is subject to biannual operational inspections and when necessary, re-inspection by VSP. The vessel owner pays a fee, based on gross registered tonnage (GRT) of the vessel, for all operational inspections. The Vessel Sanitation Program Operations Manual (VSP Operations Manual), which is available on the VSP Web site (www.cdc.gov/nceh/vsp), covers details of these inspections.

Additionally, cruise vessel owners or shipyards that build or renovate cruise vessels may voluntarily request plan reviews, on-site shipyard construction inspections and/or final construction inspections of new or remodeled vessels before their first or next operational inspection. The vessel owner or shipyard pays a fee, based on GRT of the vessel, for on-site and final construction inspections. VSP does not charge a fee for plan reviews or consultations. Section 3.0, Procedures for Making Requests for Plan Reviews and Construction-Related Inspections covers details pertaining to plan reviews, consultations, or construction inspections.

The Recommended Shipbuilding Construction Guidelines for Cruise Vessels Destined to Call on U.S. Ports, has been renamed as the Vessel Sanitation Program Construction Manual (referred to in this documents as “these guidelines”). The main purpose of these guidelines is to provide a framework of consistent construction and design guidelines that protect passenger and crew health. CDC is committed to promoting high construction standards to protect the public’s health. Compliance with these guidelines will help to ensure a healthy environment on cruise vessels.

CDC reviewed many references from a variety of sources to develop this document. These references are indicated in Section 32.2, Standards, Codes and Other References Reviewed for Guidance.

These guidelines cover various components of the vessel’s facilities related to public health, including food storage, preparation, and service; water bunkering, storage, disinfection, and distribution. Vessel owners and operators may select the design and equipment that best meets their needs. However, the design and equipment must also meet the sanitary design criteria of the American National Standards Institute (ANSI) or equivalent organization, and VSP’s routine operational inspection requirements.

These guidelines are not meant to limit the introduction of new designs, materials or technology for shipbuilding. A shipbuilder, owner, manufacturer, or other interested party may request VSP to periodically review or revise these guidelines in relation to new information or technology. VSP reviews such requests in accordance with the criteria described in Section 2.0, “Revisions and Recommended Changes.”

New cruise vessels must comply with all international code requirements (e.g., International Maritime Organization [IMO] Conventions). Those include requirements of the Safety of Life-at-Sea Convention (SOLAS), International Convention for the Prevention of Pollution from Ships (MARPOL), Tonnage and Load Line Convention, International Electrical Code (IEC), International Plumbing Code (IPC), and International Standards Organization (ISO). This document does not cross-reference related and sometimes overlapping standards that new cruise vessels must meet.

These guidelines went into effect on June 1, 2005. They apply to vessels that lay keel or perform any major renovation (e.g., any changes to the structural elements of the vessel covered by these guidelines) after this date. The guidelines do not apply to minor renovations such as the installation or removal of single pieces of equipment, (refrigerator units, bains-marie units, etc.) or single pipe runs. These guidelines will apply to all areas of the vessel affected by a renovation. VSP will inspect the entire vessel in accordance with the VSP Operations Manual during routine vessel sanitation inspections and re-inspections.

# 2.0 Revisions and Changes

VSP periodically reviews and revises these recommendations in coordination with industry representatives and other interested parties to stay abreast with industry innovations. A shipbuilder, owner, manufacturer, or other interested parties may ask VSP to review a construction guideline on the basics of new technologies, concepts, or methods. Recommendations for changes or additions to these guidelines must be submitted in writing, to the Chief, VSP (see Section 33.2 for contact information). The recommendation should:

- identify the section to be revised,

- describe the proposed change or addition,

- state the reason for recommending the change or addition, and

- include research or test results and any other pertinent information that support change or addition.

VSP will coordinate a professional evaluation and consult with industry to determine whether to include the recommendation in the next revision.

VSP gives special consideration to shipyards and owners of vessels that have had plan reviews conducted before an effective date of a revision of these guidelines. This helps limit any burden placed on the shipyards and owners to make excessive changes to previously agreed upon plans.

VSP will ask industry representatives and other knowledgeable parties to meet with VSP representatives periodically to review the guidelines and determine whether changes are necessary to keep up with the innovations in the industry.

# 3.0 Procedures for requesting Plan Reviews, Consultations, and Construction-Related Inspections

To coordinate or schedule a plan review or construction-related inspection submit an official written request to the VSP Chief as early as possible in the planning, construction, or renovation process.  Requests that require foreign travel must be received in writing at least 60 days before the intended visit.  The request will be honored, depending on VSP staff availability.  A complete listing of contact addresses and telephone numbers can be found in Section 33.2.

After the initial contact, VSP assigns primary and secondary officers to coordinate with the vessel owner and shipyard.  Normally two officers will be assigned. These officers are the points of contact for the vessel from the time the plan review and subsequent consultations take place through the final construction inspection.

The vessel representatives should provide points of contact to represent the owners, the shipyard, and key subcontractors.  All parties will use these points of contact during consultations between any of the parties and VSP to ensure awareness of all consultative activities after conducting the plan review.

## 3.1 Plan Reviews and Consultations

VSP normally conducts plan reviews for new construction a minimum of 18-24 months before the vessel is scheduled for delivery. The time required for major renovations varies. To allow time for any necessary changes, VSP coordinates the plan reviews for such projects well before the work begins. Plan reviews normally take two working days. They are conducted in Atlanta, Georgia; Fort Lauderdale, Florida; or other agreed upon sites. Normally, two VSP officers will be assigned to the project. Representatives from the shipyard, the vessel owner, and the subcontractor(s) who will be doing most of the work should attend the review. They should bring all pertinent plans or drawings, any available menus, equipment specifications, and samples for decorative materials for use in food areas for the areas covered in these guidelines. That includes but is not limited to the following:

- general arrangement plans;

- decorative materials for food areas and bars;

- all food-related storage, preparation, and service area plans;

- level and type of food service (e.g. concept menus, staffing plans, etc.)

- potable and non-potable water system plans with details on water inlets, (e.g., sea chests, overboard discharge points, and backflow protection devices);

- ventilation system plans; and, if applicable;

- plans for all recreational water facilities.  swimming pool and whirlpool spa plans.

VSP will prepare a Plan Review Report summarizing the recommendations made during the plan review and will submit the report to the shipyard and owner representatives.

Following the plan review, the shipyard will provide:

1) a complete set of plans or drawings and specifications for the vessel;

2) any redrawn plans and;

3) a statement of corrective action outlining how each of the items identified in the Plan Review Report will be corrected, and

4) copies of any major change orders in the areas covered by these guidelines that are made after the plan review.

While the vessel is being built, shipyard representatives, the owner or other vessel representatives may direct questions or requests for consultative services to the VSP project officers. Direct these questions or requests in writing to the officer(s) assigned to the project. Include fax number(s) and an e-mail address(es) for appropriate contacts. VSP officer(s) will coordinate the request with the owner and shipyard points of contact designated during the plan review.

## 3.2 On-Site Construction Inspections

VSP conducts most on-site or shipyard construction inspections in shipyards outside the United States. A formal written request must be submitted to the VSP Chief 60 days before the inspection date so that VSP can process the required foreign travel orders for VSP officers (see Section 3.0). A sample of a request is shown in Section 33.1. VSP encourages shipyards to contact the Chief, VSP to and coordinate on-site construction inspections well before the 60 day minimum to better plan the actual inspection dates. If a shipyard requests an on-site construction inspection, VSP will advise the vessel owner of the inspection dates so that the owner’s representatives are present. An on-site construction inspection normally requires the expertise of one to three officers, depending on the size of the vessel and whether it is the first of a hull design class or a subsequent hull in a series of the same class of vessels. The inspection, including travel, generally takes 5 working days. The on-site inspection should be conducted approximately 4 to 5 weeks before delivery of the vessel when 90% of the areas of the vessel to be inspected are completed. VSP will provide a written report to the party that requested the inspection. After the inspection, and before the ship’s arrival in the United States, the shipyard will submit to VSP a statement of corrective action outlining how it will address and correct each item identified in the inspection report.

## 3.3 Final Construction Inspections

At the request of a vessel owner or shipyard, VSP may conduct a final construction inspection.  The final construction inspection is to be conducted only after construction is 100% complete and the ship is fully operational.  This inspection is for evaluating the findings of the previous yard inspection, assessment of all areas which were incomplete in the previous yard inspection, and to evaluate performance tests on those systems which could not be tested in the previous yard visit.  Those systems include but are not limited to ventilation for cooking, holding, and warewashing areas, artificial light levels, temperatures in cold or hot holding equipment, halogen and other chemistry measures for potable water or recreational water systems. To schedule the inspection, the vessel owner or shipyard will submit a formal, written request the Chief, VSP as soon as possible after the vessel is completed, or a minimum of 10 days before its arrival in the United States. At the request of a vessel owner or shipyard and provided the vessel is not entering the United States market immediately, VSP may conduct final construction inspections outside the United States (see requirements for foreign travel in section 3.2 On-Site Construction Inspections). If a final construction inspection is not requested, VSP generally will conduct an unannounced operational inspection within 4 weeks following the vessel’s arrival in the United States. VSP conducts operational inspections in accordance with the VSP Operations Manual.

As soon as possible after the final construction inspection, the vessel owner or shipyard will submit a statement of corrective action to VSP. The statement will outline how they will address each item cited in the inspection report, including the projected date of completion. VSP generally schedules vessels that undergo final construction inspection in the United States for an unannounced operational inspection within 6 weeks of the vessel’s final construction inspection. VSP conducts operational inspections in accordance with the VSP Operations Manual.

# 4.0 Equipment Standards, Testing, and Certification

Although these guidelines establish certain standards for equipment and materials installed on cruise vessels, VSP does not test, certify, or otherwise endorse or approve any equipment or materials used by the cruise industry. Instead, VSP recognizes certification from independent testing laboratories such as NSF International, Underwriter’s Laboratories (UL), the American National Standards Institute (ANSI), and, or other independent international accredited  testing institutions.

In most cases, independent testing laboratories test equipment and materials to certain minimum standards which generally, but not always meet the recommended standards established by these guidelines. Equipment built to questionable standards will be reviewed by a committee consisting of the VSP, the cruise ship industry and independent testing organization participants. The committee will determine if the equipment meets the recommended standards established in these guidelines. Copies of test or certification standards are available from the independent testing laboratories. Equipment manufacturers and suppliers should will not contact refer the VSP to approve their products.

# 5.0 General Definitions

Accessible - Can be e Exposed for cleaning and inspection with the use of simple tools such as a screwdriver, pliers, o or an open-end wrench.

Adequate - Sufficient in number, features or capacity to accomplish the purpose for which something is intended and to such a degree that there is no unreasonable risk to health or safety.

Air-break - A piping arrangement in which a drain from a fixture, appliance, or device discharges indirectly into another fixture, receptacle, or interceptor at a point below the flood-level rim. (Figure 1)

Air-gap (AG) - The unobstructed vertical distance through the free atmosphere between the lowest opening from any pipe or faucet supplying water to a tank, plumbing fixture, or other device and the flood-level rim of the receptacle or receiving fixture. The air-gap must be at least twice the inside diameter of the supply pipe or faucet or and not less than 25 mm (1 inch). (Figure 2)  Manufactured air-gaps must be certified by a recognized certification organization.

Approved - Acceptable based on a determination of conformity with principles, practices, and generally recognized standards that protect public health such as ANSI/NSF standards, ASSE standards, federal regulations or equivalent international standards and regulations.

Aquatic Play Feature Pools – means wave pools, activity pools, catch pools, water slides, interactive play systems, leisure rivers, action rivers, vortex pools, and continuous surface pools.

Aquatic Spray Pad Facility - All devices, plumbing, pumps, make-up tank, equipment and features that are used to operate the recreational water facility specifically designed for children in diapers or who are not completely toilet trained.

Atmospheric vacuum breaker (AVB) -This device consists of an air inlet valve, a check seat or float valve and air inlet ports.  The device is not approved for use under continuous water pressure and shall be installed downstream of the last valve.

Backflow - The reversal of flow of water or other liquids, mixtures, or substances into the distribution pipes of a potable supply of water from any source or sources other than the potable water supply. Backsiphonage and backpressure are forms of backflow.

Backflow, check, or non-return valve — A mechanical device installed in a waste line to prevent the reversal of flow under conditions of back-pressure. In check-valves, the flap should swing into a recess when the line is flowing full so that it does not obstruct the flow.

Backflow preventer prevention device - An approved backflow prevention plumbing device that must be used on potable water distribution lines where there is a direct connection or a potential connection between the potable water distribution system and other liquids, mixtures, or substances from any source other than the potable water supply. Some devices are designed for use under continuous water pressure, whereas others are non-continuous pressure types. Perform a thorough review of the water system to ensure proper protection of the water supply, to confirm that the appropriate device is selected for each specific application.

The following are general types of backflow preventers and their uses:

Backpressure - An elevation of pressure in the downstream piping system ( by pump, elevation of piping, or steam and/or air pressure) above the supply pressure at the point of consideration which would cause, a reversal of normal direction of flow.

Barometric loop – A barometric loop is a continuous section of supply piping that rises at least 35 feet above  the supply point and returns back down to the supply.  Typically the loop will be in the shape of an upside-down “U”.  A barometric loop only protects against backsiphonage as it operates under the principle that a water column cannot rise above 33.9 feet at sea level pressure.

- Atmospheric vacuum breaker - An approved backflow prevention plumbing device used on potable water lines where shut-off valves do not exist downstream from the device. The device is not approved for use under continuous water pressure.  An atmospheric vacuum breaker must be installed at least 152 mm (6 inches) above the flood level rim of the fixture or container to which it is supplying water.

Blast Chiller - means a A unit specifically designed for rapid intermediate cooling of food products. from 60 °C (140 °F) to 21 °C (70 °F) within two hours and 21 °C (70 °F) to 5 °C (41 °F) within an additional 4 hours.

Continuous pressure backflow preventer - An approved backflow prevention plumbing device with two check valves and an intermediate atmospheric vent.  It is designed and approved for use under continuous water pressure (e.g., when shut-off valves are located downstream from the device).

Hose bib connection vacuum breaker - An approved backflow prevention plumbing device that attaches directly to a hose bib by way of a threaded head. This device uses a single check valve and vacuum breaker vent. It is not approved for use under continuous pressure (e.g., when a shut-off valve is located downstream from the device).

Reduced Pressure Principle Backflow Prevention Assembly (RP assembly) - An assembly containing two independently acting approved check valves together with a hydraulically operating, mechanically independent pressure differential relief valve located between the check valves and at the same time below the first check valve. The unit must include properly located resilient seated test cocks and tightly closing resilient seated shutoff valves at each end of the assembly.

Backsiphonage - The reversal of backward flow of used, contaminated, or polluted water from a plumbing fixture or vessel or other source into a water supply pipe as a result of negative pressure in the pipe.

Black water - Wastewater from toilets, urinals, medical sinks, and similar facilities.

Blast chiller - A unit specifically designed for rapid intermediate chilling of food products. to 21°C (70°F) within 2 hours and 5°C (41°F) within an additional 4 hours.

Cild activity facility - A designated area for use by children who do not require assistance using toilet rooms and who may be old enough to come and go on their own.

Child Activity Center - A facility for child related activities where children under the age of 6 are placed to be cared for by vessel staff.

Children’s Pool - A pool that has a depth of 1 m (3 feet) or less and is intended for use by children who are toilet trained.

Child care facility - A designated area for use by children who are not yet out of diapers or require supervision when using the toilet rooms, and who are cared for by vessel staff.

Child-sized toilet - Toilets whose toilet seat height is no more than between 280 –380 mm (11–15 inches) and the toilet seat opening is between 305–380 mm (12–15 inches). This can be achieved by installing a smaller water closet or by providing a deck platform at the front of the water closet and variably sized, fold-down toilet seats.

Cleaning room - A room specifically designed for storage of cleaning equipment such as mops, brooms, floor scrubbing machines, and cleaning chemicals. The room may or may not include a sink for filling buckets and washing mops.

Continuous pressure backflow prevention device - A device generally consisting of two check valves and an intermediate atmospheric vent which has been specifically designed to be used under conditions of continuous pressure (greater than 12 hours out of a 24 hour period).

Corrosion-resistant Non-corroding - Material that maintains its original surface characteristics through prolonged influence by the use environment, food contact, and normal use of cleaning compounds and sanitizing solutions.

Coved - A curved or concave surface, molding, or other design that eliminates the usual joint angles of 90° or less.  A single piece of stainless steel bent to an angle not less than 90° is acceptable. (Figures 3 and 4)  Rename figures to indicate coving vs. open design.

Crew toilet room - Those toilets located near food preparation areas and intended for use by food service personnel.

Cross-connection - Any unprotected, actual or potential connection or structural arrangement between a public or a consumer’s potable water system and any other source or system through which it is possible to introduce into any part of the potable system any used water, industrial fluid, gas, or substance other than the intended potable water with which the system is supplied. Bypass arrangements, jumper connection, removable section, swivel or change-over devices and other temporary or permanent devices which or because of which backflow can occur are considered to be cross-connections.

Deck drain - The physical connection between decks, scuppers, or deck sinks to the gray or black water systems.

Deck sink - A sink recessed into the deck, sized to contain waste liquids from tilting kettles and tilting pans.

Disinfection - the Destruction of all vegetative cells (not spores) in or on inanimate objects.

Distillate Water - water condensed from vapor during the evaporation process.

Double Check Valve Assembly (DC) - A backflow prevention assembly consisting of two internally loaded, independently operating check valves that are located between two resilient-seated shut-off valves.  These assemblies include four resilient-seated test cocks.  These devices do not have an intermediate vent to the atmosphere and are not approved for use on cruise vessel where a backflow prevention device is required.

Double Check with an Intermediate Atmospheric Vent (DCIV) - a backflow prevention device with double check valves and an intermediate atmospheric vent located between the two check valves.

Drip tray - Readily removable tray to collect dripping fluids or food from a food dispensing mechanism equipment.

Dry storage area - A room or area designated for the storage of packaged or containerized bulk food that is not potentially hazardous and dry goods such as single-service items.

Easily cleanable - Fabricated with a material, finish, and design that allows for cleaning by normal methods.

Easily movable:

(a) Portable; mounted on casters, gliders, or rollers; or provided with a mechanical means to safely tilt a unit of equipment for cleaning; and

(b) Having no utility connection, a utility connection that disconnects quickly, or a flexible utility connection line of sufficient length to allow the equipment to be moved for cleaning of the equipment and adjacent area.

Food Area – Includes food and beverage display/handling/preparation/service/storage areas as well as warewash areas and clean equipment/table linen storage and handling areas.  (linen storage?  Can vinyl deck covering be used in linen storage?  Which linen storage?  No vinyl in food areas.

Food contact surfaces - Surfaces (food zone, splash zone) of equipment and utensils with which food normally comes in contact and surfaces from which food may drain, drip, or splash back onto into a food or surfaces normally in contact with food. This includes those areas of ice-making machines where the ice is produced and above the connecting chute between the maker and the storage bin. It does not include the technical compartment where the compressor is located. (figure 5)

Food display areas - Any area where food is displayed for consumption by passengers and/or crew.  Applies to displays that are served by food service staff or that are self-service.

Food handling areas - Any area where food is stored, processed, prepared, or served.

Food preparation areas - Any area where food is processed, cooked, or prepared for service.

Food service areas - Any area where food is presented to passengers or crew members (excluding individual cabin service).

Food storage areas - Any area where food or food products are stored.

Food transport areas - Any area through which unprepared or prepared food is transported during food storage, preparation, and service operations (excluding public areas and individual cabin service). ??????

Food waste system - Food waste transport system (e.g., pulper, vacuum system).

Fresh Sanitary Water - Water that has not been chlorinated or pH controlled and originates from the evaporators or reverse osmosis plant and is intended for the technical water system.

Gap - An open juncture that is more than 3 mm (1/8 of an inch).

Gray water - All wastewater including drainage from galleys, dishwashers, showers, laundries, bath, washbasin, deck drains, and recreational water facilities. swimming pool and whirlpool spas. It does not include black water or bilge water from the machinery spaces.

Gutterway - See scupper

Halogen - means t The group of elements including fluorine, chlorine, bromine, and iodine used for the disinfection of water.

Hose bib connection vacuum breaker (HVB) - A backflow prevention device that attaches directly to a hose bib by way of a threaded head. This device uses a single check valve and vacuum breaker vent. It is not approved for use under continuous pressure (e.g., when a shut-off valve is located downstream from the device).  This device is a form of an AVB specifically designed for a hose connection.

Interactive play systems – can be zero depth structures that provide a variety of water features such as flowing, misting, sprinkling, jetting, and water falls.

Keel laying -The date at which construction identifiable with a specific ship begins and when assembly of that ship comprises at least 50 tons or 1% of the estimated mass of all structural material, whichever is less.

mg/L - means milligrams per liter, which is the metric equivalent of parts per million (ppm).

Non-food contact surfaces (non-food zone) - All exposed surfaces, other than food contact or splash contact surfaces, of equipment located in food storage, preparation and service areas.  (figure 5)

Non-potable water (Technical Water) - Fresh water that may not be halogenated and is intended for use in technical and other areas where potable water is not required (e.g., laundries, engine room, toilets, waste-treatment areas, and for washing decks in areas other than the vessel's hospital, food service, preparation, or storage areas).

NTU - Nephelometric Turbidity Unit which is a means of measuring the water turbidity.

ORP - Oxidation reduction potential which is an electrical measurement in millivolts (mV) of the strength of the disinfectant (oxidizer). A higher ORP means a higher disinfecting potential.

pH – means Protens hydrogen.  The symbol for the negative logarithm of the hydrogen ion concentration, which is a measure of the degree of acidity or basicity of a solution.

Plumbing system - means The water supply and distribution pipes; plumbing fixtures and traps; soil, waste, and vent pipes; sanitary sewer drains and vessel drains, including their respective connections, devices, and appurtenances within the vessel; and water-treating equipment.

Portable - A description of equipment that is readily removable or mounted on casters, gliders, or rollers; provided with a mechanical means so that it can be tilted safely for cleaning; or readily movable by one person.

Potable water - Fresh water that is free from impurities in amounts sufficient to cause disease or harmful physiological effects.  The water quality shall conform to requirements of the USEPA National Primary Drinking Water Regulations or a similarly recognized international drinking water standards.  Potable water is intended for drinking, washing, bathing, or showering; for use in fresh water swimming pools and whirlpool spas; for use in the vessel’s hospital; for handling, preparing, or cooking food; and for cleaning food storage and preparation areas, utensils, and equipment.

Potable water tanks - All tanks in which potable water is stored. from bunkering and production for distribution and use as potable water

Pressure Vacuum Breaker Assembly (PVB) - A device consisting of an independently loaded internal check valve and a spring loaded air inlet valve.  In addition this device is equipped with two resilient seated gate valves and test cocks.

Readily accessible - Exposed or capable of being exposed for cleaning or inspection without the use of tools.

Readily removable - Capable of being detached from the main unit without the use of tools.

Recreational water facility -

Reduced Pressure Principle Backflow Prevention Assembly (RP assembly) - An assembly containing two independently acting internally loaded check valves together with a hydraulically operating, mechanically independent pressure differential relief valve located between the check valves and at the same time below the first check valve. The unit must include properly located resilient seated test cocks and tightly closing resilient seated shutoff valves at each end of the assembly.

Removable - Capable of being detached from the main unit with the use of simple tools such as a screwdriver, pliers, or an open end wrench.

Safe material - An article or material that would not be expected to become a component of any food or otherwise affect the characteristics of any food. Also, an additive or other materials used as specified in Section 409 or 706 of the Federal Food, Drug, and Cosmetic Act or in conformity with applicable regulations of the U.S. Food and Drug Administration (FDA).

Sanitary Sea water - Seawater that is intended for use in the potable water production systems or in recreational water facilities.  This water is collected from a sea chest for the sole purpose of supplying potable water or recreational water facilities.

Scupper - A conduit or collection basin that channels liquid runoff to a deck drain.

Sealant - Material used to fill seams. to prevent the entry or leakage of liquid or moisture.

Sealed - Having no openings present that will permit the entry of soiled material or seepage of liquids.

Sealed seam - A seam that has no openings that would permit the entry of soil or liquid seepage.

Seam - An open juncture that is greater than 0.8 mm (1/32 an inch) but less than 3 mm (1/8 inch).  between two similar or dissimilar materials. Continuously welded junctures, ground and polished smooth, are not considered seams.

Sewage (black water) - Any liquid waste that contains animal or vegetable matter in suspension or solution, including liquids that contain chemicals in solution.

Smooth - means:

a) A food contact surface that is free of pits and inclusions with a cleanability equal to or exceeding that of a No. 3 finish (100 grit) on stainless steel;

b) A non-food contact surface of equipment that is equal to commercial grade hot-rolled steel and is free of visible scale; and

c) A deck, bulkhead, or deckhead that has an even or level surface with no roughness or projections that renders it difficult to clean.

Spa pool - A fresh or saltwater supplied pool with temperatures and turbulence comparable to a whirlpool spa., but with a water depth and volume more comparable to a swimming pool.

General characteristics are

  - water temperature of 30°C–40°C or 86°F–104°F

  - bubbling or jetted water effects that originate from under that physically break at the water surface,

  - depth of more than 1 m (3 feet), and shape is normally non-circular, and

  - volume exceeds 6 tons of water.

Spill-resistant Vacuum Breaker (SVB) - A specific modification to a PVB to minimize water spillage.

Splash contact surfaces (non-food zone) - Surfaces that are subject to routine splash, spillage or other soiling during normal use.

Spray Pad – The play and water contact area of the aquatic spray pad facility.

Swimming Pool - A recreational water facility greater than 1 meter in depth.

Direct splash surfaces - Areas adjacent to food contact surfaces that are subject to splash, drainage, or drippage onto food contact surfaces. Considered food contact surfaces.

Indirect splash surfaces - Areas adjacent to food contact surfaces that are subject to splash, drainage, drippage, condensation, or spillage from food preparation and storage.  Considered non-food contact surfaces.

Technical water - see Fresh Sanitary Water Fresh water NOT intended for drinking, washing, bathing, or showering; use in the vessel’s hospital; handling, preparing, or cooking food; or cleaning food storage and preparation areas, utensils, and equipment.

Temperature measuring devices (TMDs) - Thermometers or other instruments that measure relative heat and cold according to an established scale. TMDs that are scaled in Celsius, Fahrenheit, or both must be designed to be easily readable and accurate to ± 1.5°C or 3°F.

Transportation corridors - Areas primarily intended to move unprepared or prepared food during food preparation, storage, and service operations (e.g., service lift (elevator) vestibules to food preparation service and storage areas, and corridors connecting preparation areas and service areas). Marshalling, provisions areas, passenger/corridors, public areas, and dining rooms connected to galleys are excluded.  Corridors within a galley are to be constructed to galley standards. (Provision corridors should be built to transportation corridor standards)  This definition should be clarified.

TMD — See temperature measuring device.

Turbidity - A measure of the clarity or cloudiness of water.

Turnover - The circulation, through the recirculation system, of a quantity of water equal to the pool volume.

Utility sink - Any sink located in a food service area not intended for handwashing and/or warewashing.

Wading Pool (Children’s Pool or Splash Pool) - A recreational water facility designed for use by children with a maximum depth of 2 feet.

Whirlpool spa - A freshwater  or seawater pool designed to operate at water a minimum temperatures of 4030°C (10486°F) and equipped with either water or air jets.  The volume of this facility is less than 6 tons.  See spa pool definition.

# 6.0 General Facilities Requirements

## 6.1 Size and Flow

Many factors determine and influence the size of rooms and work areas, and the flow of food through a vessel. Those can include the size of the vessel, the number of passengers and crew, the types of foods and menus, the number of meals and mealtimes, the service or presentation of meals, the itinerary, and the vessel owner’s experience. In general, food storage, preparation, and service areas; warewashing areas; and waste management areas must be sized to accommodate the vessel’s full capacity of passengers and crew.  Bulk food storage areas or provision rooms (e.g., frozen stores, refrigerated stores, and dry stores) must be sized to prevent the storage of bulk foods from being stored in provisions passageways unless the passageways are specifically designed to meet provision room standards (Section 15.0).  Refrigeration and hot-food holding facilities, including temporary storage facilities, must be available for all food preparation and service areas and for foods being transported to remote areas.

6.1.1 Arrange the flow of food through a vessel in a logical sequence that eliminates or minimizes cross-traffic or backtracking and that allows .

    - Provide a clear separation of clean and soiled operations. When a common corridor is used for movement of both clean and soiled operations the minimum size from bulkhead to bulkhead must be considered.

    - Provide an orderly, functional flow of food from the suppliers purveyor at dockside through the food storage, preparation, and finishing areas to the service areas and finally, to the waste management area.  The goal is to reduce the risk of cross-contamination and prepare and serve food smoothly and rapidly in accordance with strict time and temperature-control requirements and to minimize time and handling.

    - Provide for each food area, including provisions, galleys, pantries, warewash, and storage a size profile in square meters of space shall be designated for that area.  The size profile should be an established standard for each cruise line which is based on their review of the area size for the same food area in their existing vessels.  As the ship size and passenger and crew totals change, there shall be a directly proportional change in each food area size based on the profile to ensure the service needs are met for each area.  Advances in technology can be used in part to address size limitations.

VSP evaluates the size of a particular room or area and the flow of food through the vessel to those rooms or areas initially and primarily during the plan review process.  VSP will also use the results of operational inspections to review the size profiles submitted by individual cruise lines.

## 6.2 Equipment Requirements

6.2.1 The following is a list of equipment is required in galleys, depending on the level and type of service, with recommendations for other areas:

6.2.1.1 Blast chillers incorporated into the design of passenger and crew galleys. More than one unit may be necessary depending on the size of the vessel; the unit’s intended application, and the distances between the blast chillers and the storage and service areas.

6.2.1.1a The size and type of blast chillers installed for each food preparation area is to be based on the concept/menu, operational requirements to satisfy that menu, and the volume of food requiring cooling.

6.2.1.2 Food preparation culinary sinks in as many areas as necessary (e.g., in all meat, fish, and vegetable preparation rooms; cold pantries or garde mangers; and in any other areas where personnel wash or soak food.

6.2.1.2.a  An automatic vegetable washing machine may be used in addition to food preparation culinary sinks in vegetable preparation rooms.;

6.2.1.3 Storage of cabinets, shelves, or racks for food products condiments and equipment in food storage, preparation, and service areas, including bars and pantries;

6.2.1.4 Portable tables, carts,  or pallets in areas where food or ice is dispensed from cooking equipment, such as from soup kettles, steamers, braising pans, tilting pans, or ice storage bins.

6.2.1.4.a Provide a storage cabinet or rack for large items such as ladles, paddles, whisks, spatulas, and to allow the vertical storage of cutting boards;

6.2.1.5 Knife lockers, or other designated knife storage facilities (e.g., drawers) that are easily cleanable and meet food contact standards;

6.2.1.6 Storage areas, cabinets, or shelves for waiter trays;

6.2.1.7 Dishware lowerators or similar dish storage and dispensing cabinets;

6.2.1.8 Glass rack storage shelving;

6.2.1.9 Work counters or food preparation counters that provide sufficient work space;

6.2.1.10 Drinking fountains that allow for hands free operation, if available, and without a filling spout in food areas;

6.2.1.11 Cleaning lockers (See Section 26.0 for specific cleaning locker construction requirements).

6.2.2 Equip the main galley, crew galley, and lido service area/galley pot washing areas, that serves the full galley operation, with a minimum of a three-compartment sink with a and prewash station or a four-compartment sink with an insert pan and an overhead spray.  Install a sink with compartments that are large enough to accommodate the largest piece of equipment (pots, tableware, etc.) used in its designated serving area. If desired, use An automatic warewashing machine with separate prewash stations in addition to the may be added but can not be substituted for a three or four compartment sinks. if the machines are sized to accommodate the equipment being washed. A front-loading, pass-through, or conveyor type warewashing machine is preferable to an under counter model.

6.2.3 Provide additional three-compartment sinks with prewash stations or four-compartment sinks with insert pans and overhead spray in heavy-use areas. These areas may include pastry/bakery, butcher shop, buffet pantry and other preparation areas where the size of the facility or distance the location makes the use of a central pot washing area impractical.

6.2.4 Equip all food preparation areas with easy access to a three-compartment sink, or a warewashing machine with an adjacent dump sink and pre-wash hose.

6.2.5 Furnish beverage dispensing equipment with readily removable drip trays or built-in drains in the tabletop. Furnish bulk milk dispensers with readily removable drip trays.

6.2.6 Provide readily removable drip trays for condiment dispensing equipment.

6.2.7 Design storage areas to accommodate all equipment and utensils used in food preparation areas such as ladles and cutting blades.

6.2.8 Ensure that the design of installed equipment directs food and wash water drainage into a deck drain, scupper, or deck sink,  and not directly or indirectly onto a deck.

6.2.9 Provide a utility sink in areas such as beverage stations and bars where it is necessary to refill serving pitchers or dispensers or discard liquids such as coffee beverages.

6.2.10 For hand scooped ice cream, sherbet or a similar product, provide dipper wells with running water and proper drainage.

6.2.11 Provide tight-fitting doors or other protective closures to ice bins, food display cases, and other food and ice holding units to prevent contamination of stored products.

6.2.12 Protect countertop openings and rims of food cold tops, bains-marie, ice wells, and other drop-in type food and ice holding units with a raised integral edge or rim of at least 5 mm (3/16 inch) above the counter level around the opening.

## 6.3 Equipment Surfaces

6.3.1 Ensure that material used for food contact, food splash contact and exposed non-food contact surfaces are smooth, durable, and non-corroding. They should be easily cleanable and designed without unnecessary edges, projections, or crevices.

6.3.2 Use only materials approved for contact with food on food contact surfaces.

6.3.2.1 Make all food contact surfaces smooth, durable, non-corroding, easily cleanable, readily accessible, and maintainable.

6.3.2.2 Provide coved preferable and seamless corners. in accordance with current sanitary standards for food service equipment. Form external corners and angles with a sufficient radius to permit proper drainage and without sharp edges.

6.3.2.3 Use only sealants approved for food contact surfaces (certified to ANSI/NSF Standard 51, or equivalent criteria) on food contact and food splash contact surfaces. Use approved sealants in limited application when practical function or design requires, such as the joining surfaces between ice makers and bins. Avoid excessive use of sealant.

6.3.3 Use materials approved for food contact surfaces for and food splash contact surfaces. Design surfaces so they are to be smooth, with no sharp edges, durable, non-corroding, readily accessible, and easily cleanable.

6.3.4 Use durable and non-corroding material for non-food contact surfaces.

6.3.4.a Design non-food contact surfaces so that they are smooth and easily cleanable. Ensure that non-food contact surfaces are accessible material for cleaning and maintenance.

6.3.4.b  Ensure that non-food contact surfaces subject to food or beverage spills have no sharp internal corners and angles.  These areas may include but are not limited to:  waiter station work surfaces, beverage stations, technical compartments with drain lines, mess room soiled drop-off stations and bus stations

## 6.4 Bulkheads, Deckheads and Decks

6.4.1 Do not use exposed fasteners in bulkhead and deckhead construction.

6.4.1.1  Seal all seams between adjoining bulkhead panels, deckhead panels, and between bulkhead and deckhead panels.

6.4.1.1.a  Seal seams greater than 0.8 mm (1/32 inch), but less than 3 mm (⅛ inch), with an appropriate sealant or appropriate profile strips.

6.4.1.1.b  Cover all seams greater than 3 mm (⅛ inch) with appropriate profile strips.

6.4.1.1.c Seal all bulkhead, deckhead, and deck penetrations through which pipes or other conduits pass, including those located inside technical compartments. Use durable and corrosion-resistant non-corroding collars where gaps are greater than 3 mm (⅛ inch).

6.4.2 Reinforce all bulkheads sufficiently to prevent panels from buckling or becoming detached under normal operating conditions.

6.4.3 Weld door penetrations indentations completely so that there are no open exposed voids. (provide diagram/schematic here) Ensure that locking/latch pins insert into inverted nipple recesses. This also applies to the penetrations around fire doors, in thresholds, and bulkhead openings.

6.4.4 Install durable coving of at least a 9.5 mm (3/8 inch) radius or open design (> 90 degrees [see definition]) as an integral part of the deck and bulkhead interface and at the juncture between decks and equipment foundations.

6.4.4.1 Ensure coving has at least a 9.5 mm (3/8 inch) radius or open design (> 90 degrees).  See coving definition (figures 3 & 4).  (In our new definition for coving, we would accept a bent piece of stainless steel at an angle not less than 90 degrees in a galley.

6.4.4.2 Provide coving that is hard, durable, easily cleanable, and of sufficient thickness and securely fastened to withstand normal wear.

6.4.4.3 Securely fasten coving.

6.4.5 Use material for decks that is hard, durable, easily cleanable, non-skid, and non-absorbent. 6.4.5.1 Install durable Vinyl or linoleum deck coverings in staff, crew or officer dining areas only are not acceptable in food areas.

6.4.5.2 Seal all pipe and conduit deck penetrations. (Already stated in 6.4.1.1.c)

6.4.6 Use compatible metals to minimize corrosion due to galvanic action or provide effective insulation techniques between dissimilar metals to protect them from corrosion.

## 6.5 Deck Drains, Deck Sinks and Scuppers

6.5.1 Construct deck drains, scuppers, and deck sinks from stainless steel.

6.5.1.1 Ensure deck drains, scuppers, and deck sinks have smooth finished surfaces, are accessible for cleaning, designed to drain completely, and large enough to prevent overflow to adjacent deck surfaces.

6.5.2 Construct scupper, and deck sink cover grates from stainless steel or other materials that:

- meet the requirements for a smooth, easily cleanable surface;

- are strong enough to maintain the original shape; and

- exhibit no sharp edges.

6.5.2.1 Install Provide scupper and deck sink cover grates that are tight-fitting, readily removable for cleaning, and uniform in length where practical (e.g., 1,000 mm or 40 inches), so that they are interchangeable.

6.5.3 Place deck drains, and deck sinks in low-traffic areas such as in front of soup kettles, boilers, tilting pans, or braising pans.

6.5.3.1 Size the deck drains, scuppers, and sinks in order to eliminate spillage and overflow to adjacent deck surfaces.

6.5.4 Provide sufficient deck drainage and design deck and scupper drain lines  in all food service and warewash areas to prevent liquids from pooling on the decks.

6.5.5 Design deck and scupper drain lines to drain at a sufficient rate, relative to nearby water supplies, to avoid pooling. Provide cross-drain connections to prevent ponding pooling and spillage from the scupper when the vessel is listing.

6.5.6 Do not use deck sinks as substitutes for deck drains. Independent deck drains are required.

If a non-removable coaming is provided around a deck drain, ensure that the juncture with the deck is coved.

## 6.6 Ramps

6.6.1 Ensure that Install ramps over thresholds and ensure that they are easily removable or sealed in place sloped. Slope ramps for easy roll-in and roll-out of trolleys. Ensure ramps are strong enough to maintain their shape. If ramps over scupper covers are built as an integral part of the scupper system, construct them of smooth, durable, and easily cleanable and durable materials.

## 6.7 Gray and black water drain lines

6.7.1 Limit the installation of drain lines, that carry sewage or other liquid wastes, directly overhead or horizontally through spaces used for food preparation or storage. That includes areas for washing or storage of utensils and equipment, such as (e.g. bars, deck pantries, and over buffet counters). If installation of waste lines is unavoidable in these area, sleeve-weld, or butt weld steel piping; and heat fuse, or chemically weld plastic piping. Do not use push-fit or press-fit piping over these areas.

# 7.0 General Hygiene Facilities Requirements For Food Service and Warewash Areas

## 7.1 Handwashing Stations

7.1.1 Provide hot and cold potable water to all handwashing sinks.

7.1.1.a Equip handwashing sinks to Provide hot water at a temperature between 38°C (100°F) and 49°C (120°F) 43°C (110°F) and 52°C (125°F)  through a mixing valve or combination faucet.

7.1.2 Construct handwashing sinks of stainless steel in food handling, preparation and storage areas. (food areas) Construct handwashing sinks in food service areas of stainless steel or similar, smooth, durable materials.

7.1.3 Provide handwashing stations that include a suitable soap dispenser, paper towel dispenser, corrosion-resistant waste receptacle, and where necessary, splash panels to protect adjoining equipment, clean utensils, food storage or food preparation surfaces. If attached to the bulkhead, permanently seal or make readily removable for cleaning soap dispensers, paper towel dispensers and waste towel receptacles or make removable for cleaning.  Air hand dryers are not permitted.

Install soap dispensers and paper towel dispensers so that they are not over adjoining equipment, clean utensil storage, food storage, food preparation surfaces, bar counters, or water fountains.

7.1.4 Provide at least one bucket filling station in each area of the galleys (e.g., cold galley, hot galley, bakery, etc.), food storage, and food preparation areas. below the handwashing sinks.

Supply hot and cold potable water through a mixing valve to a faucet with the appropriate backflow protection at each bucket filling station.

Provide appropriate deck drainage (e.g., scupper or sloping deck to deck drain) under all bucket filling stations to eliminate any pooling of water on the decks below the bucket filling station.

7.1.5 Locate handwashing stations throughout food handling, preparation, and warewash areas, so that no employee must walk more than 8000 mm (25 8m (26 feet) to reach a station or pass through a normally closed door that requires touching a handle to open.

7.1.5.a Install handwash sinks approximately 750 mm (30 inches) above the deck, 7.1.5.b Position the handwash sink so and so that employees do not have to squat or reach excessively to wash their hands.  Establish a minimum size/depth for handwash basins.

7.1.5.b Provide a handwashing station at food dispensing waiter stations (e.g., soups, ice, etc.), where the staff does not routinely return to an area with a handwashing station.

7.1.5.c Provide a handwashing station in provision areas where bulk raw foods are handled by provisioning staff.

7.1.5.d Provide at least one handwashing station for every 100 seats, (e.g., 1–100 seats = one handwashing station, 101–200 seats = two handwashing stations, etc.) at near the entrance of all officer/staff/crew mess areas where food service lines are “self-service.”

7.1.6 Install a sufficient number of handwashing sinks stations at the soiled dish drop-off area(s) in the main galley, to allow quick turn-around time specialty galleys, and pantries for employees bringing soiled dishware from the dining rooms or other food service areas and to prevent long waiting lines at handwashing stations.  Provide one sink or one faucet on a multiple-station sink for every 10 waiters assigned to a food service area during maximum capacity.

7.1.7 Provide at least one handwashing station at soiled linen handling areas of the main laundry.

7.1.8 Install easy-to-operate, sanitary faucet handles, (e.g. large elephant ear handles, foot pedals, knee pedals, or electronic sensors) on handwashing sinks in food service areas. in food areas. If a faucet is self-closing, slow-closing, or metering, provide a water flow of at least 15 seconds without the need to reactivate the faucet.

7.1.9 Install permanent signs in English, and in other languages where appropriate, stating at a minimum, “wash hands often.”

Move this to a General Hygiene Section after the food section.

Install at least one handwashing station near the exit of waste water treatment areas.  (We need to further clarify which areas – black water, collecting units, transfer pumps, treatment areas, etc.)  There was a suggestion that there be one inside each water tight compartment in these type spaces.

Install at least one handwashing station at soiled linen handling areas of the main laundry.

Install handwash stations in housekeeping areas as described in section 29.0.

## 7.2 Crew Toilet Rooms for Food Service Employees

7.2.1 Install at least one employee toilet room in close proximity to the work area of all food preparation areas.  Provide one toilet per 15 employees and provide separate facilities for males and females if more than 15 employees are assigned to a food preparation area.  Urinals may be installed, but do not count toward the toilet/employee ratio. The group agrees on the need for a ratio of toilets to workers, but cannot agree on the correct number required.  A ratio of 1/25 was suggested.  One suggested that a changing room be available in addition to toilet rooms are as part of the toilet rooms.

For main galleys and crew galleys, locate toilet rooms inside the food preparation area or in a passageway immediately outside the area.  If a main galley has multiple levels and there is stairwell access between the galleys, toilet rooms may be located near the stairwell within one deck above or below.

For other food service outlets (lido galley, specialty galley, etc.), do not locate toilet rooms more than two decks above/below in the same fire zone or on the same deck , more than one fire zone away (within the same fire zone or an adjacent fire zone).  If more than one food service outlet is located on the same deck, the toilet room may be located on the same deck between the outlets and within two fire zones of each outlet.

For provisions, use the distance requirement described in 7.2.1.b (paragraph above) to locate toilet rooms for personnel working in the preparation rooms that are in the provision area.

7.2.2 Install exhaust ventilation and equip them with handwashing facilities in each toilet room.  Air hand dryers are not permitted in these toilet rooms. Install permanent signs in English, and other languages where appropriate, stating at a minimum “wash hands after using the toilet.”

Ensure hands-free exit for toilet rooms, as described in section 30.0.  Ensure handwashing facilities have sanitary faucet handles as in section 7.1.8.

7.2.3 Install tight-fitting, self-closing doors. to control insects/vermin and odors in toilet rooms or water closets inside toilet rooms.

7.2.4 Construct decks of hard, durable materials and cove the bulkhead-deck juncture.

7.2.5 Install easily cleanable deckheads and bulkheads.

# 8.0 Equipment Placement and Mounting

8.1 Seal fixed, non- equipment that is not portable to the bulkhead, table-top, countertop, or adjacent equipment.

(Be more clear that this is counter-mounted equipment and not deck mounted)

If the equipment is not sealed, provide access sufficient, unobstructed space for cleaning under and around and between fixed equipment listed in Section 8.1.1-8.1.4. The access space provided is dependent upon the distance from either end a position directly in front or from either side of the equipment to the farthest point requiring cleaning as described in the table below. These requirements do not apply to open racks or other equipment of open design or portable equipment. easily movable equipment mounted on wheels or slides.

(look at 8.1 in the 2001 manual)

8.1.1 Provide at least 150 mm (6 inches) of clear, unobstructed space between adjacent equipment, and between the equipment and bulkheads, when the distance to be cleaned is less than 600 mm (24 inches).

8.1.2 Provide at least 200 mm (8 inches) of clear, unobstructed space between adjacent equipment and between the equipment and bulkheads when the distance to be cleaned is greater than 600 mm (24 inches) but less than 1200 mm (48 inches) long.

8.1.3 Provide at least 300 mm (12 inches) of clear, unobstructed space between adjacent equipment and between the equipment and bulkheads when the distance to be cleaned is greater than 1200 mm (48 inches) but less than 1800 mm (72 inches) long.

8.1.4 Provide at least 460 mm (18 inches) of clear, unobstructed space between adjacent equipment and between the equipment and bulkheads when the distance to be cleaned is greater than 1800 mm (72 inches).

| Section | Distance to be cleaned | Unobstructed space |
| --- | --- | --- |
| 8.1.1 | Less than 600 mm (24 inches) | 150 mm (6 inches) |
| 8.1.2 | 600 mm to 1200 mm (48 inches) | 200 mm (8 inches) |
| 8.1.3 | 1200 mm to 1800 mm (72 inches) | 300 mm (12 inches) |
| 8.1.4 | Greater than 1800 mm | 460 mm (18 inches) |

8.2 Continuous weld all equipment that is not classified as portable to stainless steel pads or plates on the deck. Make Ensure the welds have smooth edges, rounded corners, and no gaps.

Attach deck-mounted equipment as an integral part of the deck surface with glue, epoxy, or other durable, approved adhesive product. Ensure that the arrangement is attached surfaces are smooth and easily cleanable.

8.3 Seal deck-mounted equipment that is not easily movable portable to the deck or elevate it on legs that provide at least a 150 mm (6 inch) clearance between the deck and the equipment.  If no part of the deck under the deck-mounted equipment is more than 150 mm (6 inches) from the point of cleaning access, the clearance space may be only 100 mm (4 inches).

Exceptions also to the equipment requirements may be granted if there are no barriers to cleanability cleaning, (e.g., equipment, such as waste handling systems and warewashing machines with pipelines, motors, and cables) below whiche  where a 150 mm [6 inches] clearance from the deck may not be practical.

8.4 Provide a minimum of at least 150 mm (6 inches) between equipment and the deckheads. If proper this clearance cannot be achieved, extend the equipment through to the deckhead panels and seal appropriately.

8.5 Mount equipment that is on a foundation or coaming at least 100 mm (4 inches) above the finished deck. Use cement or a continuous weld to seal equipment to the foundation or coaming.

Provide a sealed-type foundation or coaming for equipment not mounted on legs.  Do not allow equipment to overhang the foundation or coaming by more than 100 mm (4 inches). Completely seal any overhanging equipment along the bottom (Figure 6).

8.6 Seal table-mounted equipment, unless portable, to the tabletop or mount on legs.

8.6.1 The length of the legs is dependent upon the horizontal distance of the table top under the equipment from either end to the farthest point requiring cleaning, based on the table below.

8.6.1.a Mount the equipment on legs at least 100 mm (4 inches) above the tabletop if the horizontal distance of the table top under the equipment is 500 mm (20 inches) or greater from the point of access for cleaning.

8.6.1.b Mount the equipment on legs at least 75 mm (3 inches) above the tabletop if the horizontal distance of the table top under the equipment is less than 500 mm (20 inches) or greater than 75 mm (3 inches) from the point of access for cleaning.

8.6.1.c Mount the equipment on legs at least 50 mm (2 inches) above the tabletop if the horizontal distance of the table top under the equipment less than 75 mm (3 inches) from the point of access for cleaning.

| Section | Horizontal Distance | Equipment Leg Length |
| --- | --- | --- |
| 8.6.1.a | 500 mm (20 inches) | At least 100 mm (4 inches) |
| 8.6.1.b | 75 mm (3 inches) to 500 mm | At least 75 mm |
| 8.6.1.c | Less than 75 mm | 50 mm (2 inches) |

8.6.2 Provide access behind and between all tabletop-mounted equipment, including beverage line equipment, to allow access for cleaning. Use the distances found in the table of section 8.1. (Repeating what is contained in 8.1 and suggest we delete this)

# 9.0 Fasteners and Requirements for Securing and Sealing Equipment

## 9.1 Food Contact Surfaces

(We need to change food contact/splash zone terminology to make consistent in definitions and throughout the manual)

9.1.1 Attach all food contact surfaces or connections from food contact surfaces to adjacent splash zones to ensure a seamless, coved corner.

9.1.1.1 Reinforce all bulkheads, deckheads, or decks receiving such attachments.

9.1.2 Use low profile, non-slotted, non-corroding, and easy to clean fasteners on food contact surfaces and in food splash zones. The use of exposed slotted screws, Phillips head screws or pot pop rivets in these areas is prohibited.

## 9.2 Non-Food Contact Surfaces

9.2.1 Seal non-food contact surfaces of equipment gaps, and seams less than 3 mm (⅛ inch) with an appropriate sealant. See seam definition. Avoid excessive use of sealant.

9.2.1.1 Use only stainless steel profile strips on surfaces exposed to extreme temperatures (e.g., freezers, and above cook tops, grills, and fryers) or for gaps greater than 3 mm (⅛ inch). Avoid excessive use of sealant Do not use sealants to close gaps. See gap definition.

9.2.2 Construct slotted or Phillips head screws, pop rivets, and other fasteners used in non-food contact areas of corrosion-resistant non-corroding materials.

## 9.3 Use of Sealants

9.3.1 Use approved (certified to ANSI/NSF Standard 51, or equivalent criteria) food grade sealants on food contact and food splash zones surfaces.  Avoid excessive use of sealant.  Once cured, sealants shall be smooth, semi-hard or hard, durable and easy to clean.  Provide product manufacturer’s literature and certification listing for sealants used.

# 10.0 Latches, Hinges, and Handles

10.1 Use durable, non-corroding, and easily cleanable built-in equipment latches, hinges, and handles. Do not use piano hinges in food contact or splash zones.

# 11.0 Gaskets

11.1 Use smooth, non-absorbent, non-porous materials for equipment gaskets in reach-in refrigerators, steamers, ice bins, ice cream freezers, and similar equipment.

11.2 Close and seal exposed surfaces of gaskets at their ends and corners.

11.3 Use refrigerator door gaskets that are designed to be removable.

11.4 Follow the requirements in Section 9.0 when using fasteners to install gaskets.

# 12.0 Equipment Drain Lines:

12.1 Connect drain lines from to the following to appropriate waste system by means of an air-gap or air-break from all fixtures, sinks, appliances, compartments, refrigeration units, or devices other equipment that are used, designed for, or intended to be used in the preparation, processing, storage, or handling of food, ice, or drinks.

12.1.1 Use stainless steel or other durable, non-corroding and easily cleanable rigid or flexible material in the construction of drain lines. Do not use ribbed materials in areas subject to splash or soiling unless coated with a smooth and easily cleanable material.

12.1.1.1 Size drain lines appropriately, with a minimum interior diameter of 25 mm (1 inch) for custom-built equipment.

12.1.2 Slope walk-in refrigerator and freezer evaporator drain lines, and extend them through the bulkhead or deck.

12.1.2.1 Direct walk-in refrigerator and freezer evaporator drain lines through an accessible air-break to a deck scupper or drain below the deck level or to a scupper outside the unit.  Direct drain lines from deck drains and scuppers in walk-in refrigerator and freezer units through an indirect connection to the waste water system.

12.1.3 Install drain lines to minimize the horizontal distance from the source of the drainage to the discharge.

12.1.4 Install horizontal drain lines at least 100 mm (4 inches) above the deck and slope to drain.

12.2 All drain lines (except condensate drain lines) from hood washing systems, cold top tables, bains-marie, dipper wells, food preparation  sinks and warewashing sinks or machines must:

12.2.1 be less than 1000 mm (40 inches) and free of sharp angles or corners, if designed to be cleaned in place by a brush.

12.2.2 be readily removable for cleaning, if greater than 1000 mm (40 inches).

12.2.3 drain through an air-break to a drain or scupper. Already stated in 12.1

12.3 Extend all installed fixed equipment drain lines in a vertical line vertically to a scupper, or deck drain, when possible. If not possible, keep the horizontal distance of the line to a minimum.

12.4 Handwashing sinks, mop sinks and drinking fountains are not required to drain through an air-break.

# 13.0 Electrical Connections, Pipelines, Service Lines and other Attached Equipment

13.1 Encase electrical wiring from permanently installed equipment in durable and easily cleanable material. Do not use braided or woven stainless steel electrical conduit outside of technical spaces or where it is subject to splash or soiling, unless encased in easily cleanable plastic or similar easily cleanable material. Do not use ribbed metal or plastic conduit.

For equipment that is not permanently mounted, adjust the length of electrical cords install or fasten them service lines in a manner that prevents the cords lines from lying on contacting decks or countertops.

13.2 Tightly seal bulkhead or deckhead-mounted equipment (phones, speakers, electrical control panels, outlet boxes, etc.) with the bulkhead or deckhead panels. Do not locate such equipment in areas exposed to food splash.

13.3 Tightly seal any areas where electrical lines, steam or water pipelines, etc., penetrate the panels or tiles of the deck, bulkhead, or deckhead, including inside technical spaces located above or below equipment or work surfaces. Seal any openings or voids around the electrical lines or the steam or water pipelines and the surrounding conduit or pipelines.

13.4 Enclose steam and water pipelines to kettles and boilers in stainless steel cabinets or position the pipelines behind bulkhead panels. Minimize the number of exposed pipelines. Cover any exposed, insulated pipelines with stainless steel or other durable, easily cleanable material.

# 14.0 Hood Systems

14.1 Install hood systems or direct duct exhaust systems over warewashing equipment (except undercounter warewashing machines) and over three-compartment sinks in pot wash areas where hot water is used for sanitizing.

14.1.1 Directly connect warewashing machines that have a direct duct exhaust to the hood exhaust trunk.

14.1.2 Design Provide canopy exhaust hoods over warewashing equipment or three-compartment sinks to have a minimum 150 mm (6 inches) overhang from the edge of equipment to capture excess steam and heat and prevent condensate from collecting on surfaces.

14.1.3 Install a clean-out ports in the direct exhaust ducts of the ventilation systems between the top of the warewashing machine and the hood system or deckhead.

14.1.4 Provide accessible and removable flat condensate drip trays in the ducts from the warewashing machine ventilation ducts.

14.2 Install hood or canopy systems above cooking equipment in accordance with SOLAS requirements to ensure that they adequately remove excess steam and grease-laden vapors and prevent condensate from collecting on surfaces.

14.2.1 Install a hood or canopy systems or dedicated local exhaust ventilation directly above bains marie or steam tables to control excess heat and steam. from bains-marie or steam tables and prevent condensate from collecting on surfaces.

14.2.2  Install a hood or canopy system or dedicated local exhaust when SOLAS requirements do not require or specify an exhaust system for countertop cooking appliances or where portable appliances are used.  The exhaust system should remove excess steam and grease-laden vapors and prevent collection of the cooking byproducts or condensate on surfaces above.

14.3 Select proper sized Properly size all exhaust and supply vents.

14.3.1 Position and balance them appropriately for expected operating conditions all exhaust and supply vents to ensure proper air conditioning, and capture/exhaust of heat and steam.

14.4 Where used, provide readily removable and cleanable filters.

14.5 Provide access for cleaning vents and ductwork. Automatic clean-in-place systems are recommended for removal of grease generated from cooking equipment.

14.6 Locate automatic clean-in-place hood wash control panels, that have a detergent chemical reservoirs, so they are not over food preparation equipment or counters.

14.7 Construct hood systems of stainless steel with coved corners of at least 9.5 mm (3/8 inch) radius.

14.7.1 Use continuous welds or profile strips on adjoining pieces of stainless steel.

14.7.2 A drainage system is not required for normal grease and condensate hoods, or if cleaning solutions are applied manually to hood assemblies.

14.7.3 Install drainage system for automatic, clean-in-place hood washing systems.

14.8 Install all ventilation systems in accordance with the manufacturer’s recommendations.

14.8.1 Test each system by utilizing a method that determines if the system is properly balanced for normal operating conditions. Provide written documentation of the test results.

# 15.0 Provision Rooms, Walk-in Refrigerators and Freezers, and Transportation Corridors

## 15.1 Bulkheads  Deckheads

(It was decided by the attendees that any corridor inside the galley should be built to galley standards)

15.1.1 Provide tight-fitting, stainless steel bulkheads in walk-in refrigerators and freezers. Line doors with stainless steel.

15.1.2.a Light colored painted steel is acceptable for provision passageways and transportation corridors.

15.1.2.b Stainless steel panels are preferable but not required in dry storage areas.

15.1.3 Provide protection to prevent damage to bulkheads from pallet handling equipment (e.g., forklifts, pallet jacks, etc.) in areas through which food is stored or transferred.

15.1.4 Close deckhead-mounted cable trays, piping or other difficult to clean deckhead-mounted equipment, or close the deckhead to prevent food contamination from dust and debris falling from deckheads and deckhead-mounted equipment and utilities (painted sheet metal ceilings are acceptable in these areas).

## 15.2 Decks

15.2.1 Use hard, durable, non-absorbent decking, (e.g., tiles, or diamond plate corrugated stainless steel deck panels) in refrigerated provision rooms. Install durable coving   as an integral part of the deck and bulkhead interface and at the juncture between decks and equipment foundations.  If installed, use a sufficient thickness on stainless steel or other coving to make durable and secure. Sufficiently reinforce stainless steel decking to prevent buckling if pallet handling equipment will be used in these areas.

15.2.2 Steel decking is acceptable in provisions passageways, transportation corridors, and dry-stores areas.

## 15.3 Cold Room Evaporators, Drip Pan, and Drain Lines

15.3.1 Enclose piping, wiring, coils, and other difficult-to-clean components of evaporators in walk-in refrigerators, freezers, and dry store rooms with stainless steel panels.

15.3.2 Use stainless steel evaporator drip pans that have coved corners, are sloped to drain, strong enough to maintain slope and are readily accessible for cleaning.

15.3.3 Place non-corroding spacers between the drip pan brackets and the interior edges of the pans.

15.3.4 Follow all fastener guidelines in Section 9.0.

15.3.5 Provide a heater coil for freezer drip pan. Attach the coil to a stainless steel insert panel or to the underside of the drip pan. Use easily removable coils so that the drip pan can be cleaned. Make sure that heating coils provided for drain lines are installed inside of the lines.

15.3.6 Position and size the evaporator drip pan to collect all condensate dripping from the evaporator unit.

15.3.7 Encase thermometer probes in a stainless steel conduit. Position probes in the warmest part of the room where food is normally stored.

# 16.0 Galleys, Food Preparation Rooms, and Pantries

## 16.1 Bulkheads and Deckheads

16.1.1 Construct bulkheads and deckheads (including doors, door frames, and columns) with a high quality, corrosion-resistant stainless steel. Use a thick enough gauge so that the panels do not warp, flex, or separate under normal conditions. Use an appropriate sealant for seams greater than 1 mm (1/32 inch), but less than 3 mm (⅛ inch). Use only stainless steel or other non-corroding, but equally durable, materials for profile strips for on bulkhead and deckhead seams greater than 3 mm (⅛ inch) gaps.

16.1.1.a Minimize gaps around fire shutters, sliding doors, and pass-through-windows.

16.1.1.b Provide cleaning sufficiently sized access panels to void spaces of around sliding doors and sliding pass-through windows to allow for cleaning.

16.1.2 Construct bulkheads of sufficient thickness or reinforce the areas where equipment is installed to allow the use of fasteners or welding without compromising the quality and construction of the panels.

16.1.3 Install utility line connections through a stainless steel or other easily cleanable, food service approved conduit that is mounted away from bulkheads for ease in cleaning and deckheads.

16.1.4 Attach backsplashes to the bulkhead with low profile, non-slotted fasteners, or continuous- or tack- welds and tack welds that are polished smooth. Use an appropriate sealant to make the backsplash attachment watertight.

16.1.5 Seal Close all openings where piping and other items penetrate the bulkheads and deckheads, including inside technical compartments.

## 16.2 Decks

16.2.1 Construct decks from hard, durable, non-absorbent, non-skid material. Install durable coving as an integral part of the deck and bulkhead interface and at the juncture between decks and equipment foundations.

16.2.2 Seal all deck tiling with a durable, water-tight grouting material. Seal stainless steel deck plate panels with a continuous, non-corroding weld.

16.2.3 Use durable, non-absorbent, easily cleanable surfaces such as tile or stainless steel in technical spaces below undercounter cabinets, counters, or refrigerators. Do not use painted steel and concrete decking.

16.2.4 Seal all openings where piping and other items penetrate through the deck.

# 17.0 Buffet Lines, Waiter Stations, Bars, Bar Pantries and Other Similar Food Service Areas

Follow construction guidelines referenced in Sections 6.0 - 16.2.4 for all pantries.

## 17.1 Bulkheads and Deckheads

17.1.1 Construct bulkheads and deckheads of hard, durable, non-corroding materials. Decorative tiles, pressed metal panels, and etc. are acceptable provide they are , non-absorbent and easily cleanable materials.

Follow bar and bar pantry construction guidelines referenced in Sections 6.0 - 16.2.4

*For buffet service areas where food preparation occurs galley standards for construction must be followed.

*Slots for ventilation plenum spaces are not allowed directly over food preparation, food storage or clean equipment storage. (cross reference in ventilation section as well)

## 17.2 Decks

17.2.1 Install hard, durable, non-absorbent decks at all buffet lines that are at least 1000 mm (40 inches) in width measured from the edge of the service counter or, if present, from the outside edge of the tray rail (if such a rail is present). Vinyl and linoleum deck materials are not acceptable.

17.2.2 Install hard, durable, non-absorbent decks (e.g., tile, sealed granite, or marble) that extend at least 600 mm (24 inches) from the edge of the working side of the dining room service stations.  Vinyl and linoleum deck materials are not acceptable.

17.2.3 Construct and cove decks behind service counters, under equipment, and in technical spaces of hard, durable, non-absorbent materials (e.g., tiles, epoxy resin or stainless steel). Do not use painted steel or concrete decking.

17.2.4 Durable linoleum, vinyl tile, or deck covering may be used only in staff, crew, or officers dining areas.

17.2.5 Cove and tightly seal all Install durable coving as an integral part of the deck/bulkhead and deck junctures/cabinet foundation juncture when on the worker only side of deck/buffet, worker side of the deck/bar, and working sides of the deck/waiter station.  Install durable coving at the passenger side of deck buffet service counters and those shared with worker activities (islands).

*For buffet service areas where food preparation occurs galley standards for construction must be followed.

## 17.3 Food Display Protection

17.3.1 Provide effective means to protect food (e.g., sneeze shields or display cases) in all areas where food is on display for self-service.  Insert text regarding shield or guard protection where preparation is made at the front counter.  What is the height requirement?  Height difference whether the consumer stands or sits.  Specify exceptions for cooking surfaces.

17.3.2 Following these Sneeze guard criteria for sneeze guards:

17.3.2.1 Sneeze guards may be temporary (portable) or built-in and integral parts of display tables, bains marie, or cold-top tables.

17.3.2.2 Sneeze guard panels must be durable plastic or glass that is smooth and easily cleanable. Use sections that are easily manageable lengths that are and  removable for cleaning.

17.3.2.2.a  Sneeze guards must be transparent and designed to minimize obstruction of the customer’s view of the food. To protect against chipping, protect exposed edges of glass with tight fitting channels, stripping material, or rounding the edges of tempered glass.

17.3.2.3 Position sneeze guards so that the panels intercept a line between the average consumer’s mouth and the displayed foods, in accordance with ANSI/NSF Standard 2 for food equipment. Take into account factors such as the height of the food display counter, the presence or absence of a tray rail, and the distance between the edge of the display counter and the actual placement of the food (Figure 7). (ANSI/NSF Standard 2).  Also include other figures from the FDA plan review guidelines.  (Ensure there is a mouth height for the elementary school/child buffet shielding.)

If the buffet is built to the calculations in figure 7:

17.3.2.3.a  The maximum vertical distance between a counter top and the bottom leading edge of a food shield shall be 14 in (350 mm) 350 mm (14 in).

17.3.2.3.b  The bottom leading edge of the food shield shall extend a minimum horizontal distance of 7.0 in (175 mm) 175 mm (7 in) beyond the front inside edge of a food well.

17.3.2.3.c  The sum of a food shield’s protected horizontal plane (X) and its protected vertical plane (Y) shall equal a minimum of 18 in (450 mm) 450 mm (18 in) (see figure 11). Either X or Y may equal 0.

17.3.2.3.d Install side protection for sneeze guards if the distance between exposed food and where people are expected to stand is less than 1000 mm (40 inches).

17.3.3 Use tray rail surfaces that are sealed, coved, or have an open design and are easily cleanable in accordance with guidelines for food splash zones.

Consideration should be given to the length of the food pans in relation to the distance a consumer must reach to obtain food.

## 17.4 Beverage Delivery System

17.4.1 Install a stainless steel, vented, double-check valve backflow prevention device that is approved for use on carbonation systems with for systems that contain brass or copper fittings (e.g., multi-flow beverage dispensing systems). Install the device before the carbonator and downstream from any copper of brass or copper-alloy (e.g., brass) fittings in the potable water-supply line.

17.4.2 Encase supply lines to the dispensing guns in a single tube. If the tube penetrates through any bulkhead or countertop, seal the penetration with a grommet.

17.4.3 Incorporate, into the design of For bulk dispensers of beverage delivery systems, incorporate a clean-in-place system that provides a means of flushing, and sanitizing the entire interior of the dispensing lines in accordance with the manufacturers’ instructions.

  - Passenger Self-Service Buffet Handwashing Stations

Provide one handwashing station per 100 passenger seating or fraction thereof.  The stations should be equally distributed between the major entry points to the buffet area according to the layout and should be separate from a toilet room.    Any mechanism where a passenger can wash their hands with the use of soap and water is sufficient (decorative is okay).  Add some text describing the type of station that would be allowed.

Provide at least one handwash station at the entrance of each self-service station that is outside of the main buffet.

Provide some description for minor entries, such as one HW per entry (including minor entries). Stations can be installed just outside of the entry if allowed by SOLAS and Coast Guard.

# 18.0 Warewashing

18.1 Provide rinse hoses for prewashing (not required but recommended in bar and deck pantries). If a sink is to be used for pre-rinsing, provide a removable strainer.

18.1a Installation of a splash panel may be required if a clean utensil/glass storage rack or preparation counter is near a prewash area.

18.2 Provide space for trash cans, garbage grinder, or food waste handling systems.  Grinders are optional in pantries and bars.

18.3 Provide a food waste trough that extends the full length of soiled landing tables with food waste handling systems.

18.4 Seal the back edge of the soiled landing table to the bulkhead or provide a minimum of 460 mm (18.4 inches) clearance between the table and the bulkhead.  Refer to (8.0).

18.5 Design soiled landing tables to drain waste liquids and prevent contamination of adjacent clean surfaces.

18.6 Provide across-the-counter gutters with drains and slope the clean landing tables to the gutters at the exit from the warewashing machines to prevent water from pooling. If the first gutter does not effectively remove the pooled water, install additional gutter(s) and drain line(s). Minimize the length of drain lines and when possible direct them in a straight line to the deck scupper.

18.7 Provide sufficient space for cleaning around and behind equipment (e.g., food waste systems and warewashing machines). Refer to section 8.0 for spacing requirements.

18.8 Encase Enclose food waste system wiring in a durable and easy to clean stainless steel or non-metallic watertight conduit and raise it at least 150 mm (6 inches) above the deck. Elevate all warewashing machine components at least 150 mm (6 inches) above the deck, except as noted in Section 8.3.

18.9 Construct removable splash panels of stainless steel to protect the food waste system and technical areas.

18.10 Construct grinder cones, food waste system tables and dish-landing tables from stainless steel with continuous welding. Construct platforms for supporting warewashing equipment from stainless steel.

18.11 Design and Size warewashing machines for their intended use and install them according to the manufacturer’s recommendations.

18.11.1 Equip warewashing machines with a device an audible or visual alarm that audibly or visually indicates that the sanitizing temperature or the chemical sanitizer level has dropped below the levels stated on the machine data plate.

18.12 Display the data plate affixed to warewashing machines by the manufacturer so that the information is easily accessible and readable. easy to read. The data plate will provide the following information:

18.12 a) temperatures required for washing, rinsing, and sanitizing;

18.12 b) pressure required for the fresh water sanitizing rinse unless the machine is designed to use only a pumped sanitizing rinse;

18.12 c) conveyor speed for conveyor machines or cycle time for stationary rack machines; and

18.12 d) chemical concentration (if chemical sanitizers are used).

18.13 Correctly size three-compartment warewashing and potwashing sinks for their intended use. Use sinks that are large enough to submerge the largest piece of equipment used in the area that is served. Use sinks that have coved, continuously welded integral internal corners that are integral to the interior surfaces.

18.14 Install one of the following arrangements to prevent excessive contamination of wash water with pre-wash water (only a or b) and rinse water with wash water splash:

18.14 a) an across-the-counter gutter with a drain that divides the wash compartment from the rinse compartment

18.14 b) a splash shield at least 100 mm (4 inches) above the flood level rim of the sink between the wash and rinse compartments

18.14 c) an overflow drain in the wash compartment 100 mm (4 inches) below the flood level.

Add some text to address the space between the back edge of the wash sink and the back bulkhead and the front edge of the wash sink and the table edge.  Close this with a SS wedge piece.

18.15 Equip hot water sanitizing sinks with accessible and easily readable easy to read thermometers, a utensil retrieval system (e.g., long-handled stainless steel wire basket, or other retrieval system), a jacketed or coiled steam supply with a temperature control valve to control water temperature, or electric heating system. (Three-compartment sinks that utilize chemical sanitizers for the sanitization step do not require those items).

18.15.a Provide pot and utensil washing facilities as listed in Section 6.2.2 and 6.2.3

18.16 Provide sufficient shelving for storage of soiled and clean ware. Use either solid or open round tubular shelving or racks. Design solid overhead shelves to drain away from clean surfaces.  Sufficient space shall be determined by the initial sizing of the warewash area, as based on the profile or reference size from an existing vessel of the same cruise line as per 6.1.4. The VSP will verify the submitted reference vessel capacity during operational inspections.

18.17 Provide adequate ventilation to prevent condensation condensate from collecting on the deckhead or adjacent bulkheads. Ensure that any filters installed over warewashing equipment are easily removable and fans are accessible for cleaning.  Make sure the text identifying condensation is noted in all such ventilation text, such as 14.1.2.  Suggested this text be deleted or incorporated in 14.1, then only state see 14.1 for ventilation requirements.

# 19.0 Lighting

19.1 Provide a minimum of 220 lux (20 foot candles) of light at the work surface level in all food preparation, food service, and warewashing areas when all equipment is installed. Provide 220 lux (20 foot candles) of lighting for equipment storage, garbage and food lifts, garbage rooms, and toilet rooms, measured at 760 mm (30 inches) above the deck.

19.1.1 Provide a minimum light level of 110 lux (10 foot-candles) behind and around equipment measured at a distance of 760 mm (30 inches) above the deck (e.g., ice machines, combi-ovens, etc.).

19.1.2 Provide a minimum light level of 220 lux (20 foot-candles) at counter tops (e.g., beverage lines, etc.).

19.2 For effective illumination, place the deckhead mounted light fixtures above the work surfaces and positioned them in an "L" pattern rather than a straight line pattern.

19.3 Install light fixtures tightly against the bulkhead and deckhead panels. Completely seal electrical penetrations to permit easy cleaning around the fixtures.

19.4 Use shatter-resistant and removable light shields for light fixtures. Completely enclose the entire light bulb or fluorescent light tube(s).

19.5 Provide lighting levels of at least of 220 lux (20 foot candles) in provision rooms, measured at 760 mm (30 inches) above the deck while the rooms are empty. During normal operations when foods are stored in the rooms, provide lighting levels of at least 110 lux (10 foot candles), measured at a distance of 760 mm (30 inches) above the deck.

19.6 In bars and over dining room waiters’ stations designed for lowered lighting during normal operations, provide lighting that can be raised to 220 lux (20 foot candles) during cleaning operations, as measured at 760 mm (30 inches) above the deck.

19.7 Use shielded, coated, or otherwise shatter-resistant light bulbs in areas where there is exposed food; clean equipment, utensils, and linens; or unwrapped single-service, and single-use articles.  This includes lights above waiter stations.

19.8 Use shields that surround and extend beyond bulbs on infrared or other heat lamps to protect against breakage. Allow only the face of the bulb to be exposed.

19.9 Decorative track or recessed deckhead-mounted lights above bar countertops, buffets, and other similar areas may be mounted on, or recessed within the deckhead panels without being shielded. However, install specially-coated, shatter-resistant bulbs in the light fixtures in this area.

# 20.0 Waste Management

## 20.1 Food and Garbage Lifts

20.1.1 Provide food and garbage lifts whose with interiors that are constructed of stainless steel and meet the same standards as Section 16.0.

20.1.2 Construct decks of a durable, non-absorbent, non-corroding material and with an integral cove.

20.1.3 Position bulkhead-mounted air vents in the upper portion of the bulkhead panels or in the deckhead.

20.1.4 Install a drain at the bottom of all lift shafts, including provision platform lifts and dumbwaiters.

20.1.5 Construct the interiors of dumbwaiters of stainless steel with coved bulkhead and deck junctures that meets the standards of Section 16.0.

20.1.6 Provide light fixtures that are recessed or fitted with stainless steel guards to prevent breakage.

20.1.7 If installed, construct garbage chutes of stainless steel and with coved junctures. Install an automatic washing system, and in accordance with for the garbage chute. And ensure that the garbage chute meets all SOLAS and classification society requirements.

## 20.2 Trolley, Waste Container, and Cleaning Equipment Wash Rooms

20.2.1 Construct bulkheads, deckheads, and decks to the same standards as Section 16.0.

20.2.2 Provide a bulkhead-mounted pressure washing system with a deck sink and drain. (An enclosed automatic equipment washing machine or room may be used in place of the pressure washing system and deck sink).

20.2.3 Provide an easily accessible handwashing station with potable hot and cold water, a hose connection, and a deck drain that meets the requirements of section 7.0.

20.2.4 Provide adequate ventilation for the extraction of steam and heat.

## 20.3 Garbage Holding Facilities

20.3.1 Construct the garbage and refuse storage or holding rooms sized of sufficient size to hold unprocessed waste for the longest expected time period when between off-loading of waste is not possible. loadings. Separate the refuse-storage room from all food preparation and storage areas.

20.3.2 Provide adequate supply and exhaust ventilation to control odors, temperature, and humidity.  Refer to 27.2.1 for other requirements related to ventilation

20.3.3 Provide a sealed, refrigerated storage space for storing wet garbage that meets the standards requirements of 15.0. and 16.0

20.3.4 Provide an easily accessible handwashing station with potable hot and cold water, a hose connection, and a deck drainthat meets the requirements of section 7.0.

20.3.5 Provide sufficient adequate deck drainage to prevent pooling of any water liquids.

20.3.6 Ensure that all bulkheads and decks are durable and easily cleanable.

## 20.4 Garbage Processing Areas

20.4.1 Appropriately size the garbage processing area for the operation and supply a sufficient number of sorting tables. A size profile in square meters of space shall be designated for the garbage sorting room.  The size profile should be an established standard for each cruise line which is based on their review of the area size for this room in their existing vessels.  As the ship size and passenger and crew totals change, there shall be a directly proportional change in the garbage sorting room size based on the profile to ensure the service needs are met for each area.  Advances in technology can be used in part to address size limitations.

20.4.2 Provide stainless steel sorting tables with coved corners. If provided, use deck coaming that is at least 80 mm (3 inches) and coved. If the tables have drains, Provide a table drain and direct the table drains it to a strainer-protected deck drain. and install a strainer in the deck drain

20.4.3 Provide an easily accessible handwashing station with potable hot and cold water, a hose connection, and a deck drain. that meets the requirements of section 7.0.

20.4.4 Provide a storage locker for cleaning materials. Follow storage locker guidelines in that meets the requirements of Section old section 26.1.

20.4.5 Ensure that bulkheads and decks are durable, non-corroding corrosion-resistant and easily cleanable.

20.4.5a Provide deck drains to prevent liquids from pooling on the decks. Provide berm/coaming around all waste-processing equipment and ensure there is proper adequate deck drainage inside the berms.  Request owner and yard identification of which equipment or other method to control liquids from waste-processing equipment (e.g., coaming on 3 sides only, sloping deck to nearby drain), and specify a distance for the nearby drain.

20.4.6 Provide light levels of at least 220 lux (20 foot candles) at the work surface levels.

20.4.7 Equip a sink with a pressure washer or an automatic washing machine for washing garbage/refuse handing equipment, garbage/refuse storage containers, and garbage barrels.

## 20.5 Sewage Systems

20.5.1 Limit the installation of drain lines that carry sewage or other liquid waste directly overhead or horizontally through spaces used for food preparation or storage. That includes areas for washing or storage of utensils and equipment, such as bars, deck pantries, and over buffet counters. Sleeve-weld, or butt weld steel pipe; and heat fuse, or chemically weld plastic pipe. It was suggested by owners that this be for all food areas (not just preparation and storage).  Yard disagrees (concern regarding table linen storage – what about in laundry areas).

20.5.1a Do not use push-fit or press-fit piping over these areas.

20.5.2 Design Ensure that black and gray water drain drainage systems from cabins, food areas, and public spaces are designed and installed to prevent the back-up of waste and the emission of odors or gases into these areas or any other areas of the vessel.

20.5.3 Vent sewage-holding tanks to the outside of the vessel and ensure that vented gases do not enter the vessel through any air intakes.

20.5.3.a  Construct sewage-holding tank vents so that they are independent of all other tanks and are away from any air intakes.

# 21.0 Potable Water System

21.0.1 Stripe or paint the following lines in accordance with the color designation in ISO 14726: fresh sanitary water, potable water, distillate directed to the potable water system, and sanitary seawater.  Stripe or paint permeate from the reverse osmosis unit that is directed to the potable water system as per the color designation for distillate.

21.0.2  Paint or stripe these lines at 5 m (15 feet) intervals and on each side of partitions, decks, and bulkheads except where decor would be marred by such markings.

## 21.1 Bunker Stations

21.1.1 Position the filling line hose connections at least 450 mm (18 inches) above the deck; paint or stripe them auxiliary blue or in accordance with ISO 14726.

21.1.2 Equip filling line hose connections with tight-fitting caps that are fastened by a non-corroding chain so that the cap does not touch the deck when hanging.

21.1.3 Use unique screw connections for the hose attachments that only fit potable water hoses.

21.1.4 Label the filling lines "POTABLE WATER FILLING" with at least 13 26 mm (change all locations of 26 mm labeling to 25 mm as it is the standard size) (½1 inch) high lettering stamped, stenciled, or painted on the filling lines or on the bulkhead at the area of the bunker filling line.

21.1.5 If used, Locate any filters used in the bunkering line before the process ahead of the halogenation injection point, accessible for inspection and removable for cleaning.

21.1.5.1 Ensure any filters used in the bunkering process are easily accessible and removable for inspection and cleaning.

## 21.2 Filling Hoses

21.2.1 Provide hoses designed approved for potable water use that are durable with.  Hoses shall be smooth, durable , have an impervious lining, caps on each end, and fittings unique to the potable water connections (See 21.1.3).

21.2.2 Provide at least two 15 m (50 feet) hoses per bunker station.

21.2.3 Label potable water hoses “POTABLE WATER ONLY” with at least 26 mm (1 inch) high lettering stamped, stenciled, or painted at each connection end.

## 21.3 Filling Potable Water Hose Storage

21.3.1 Construct potable water hose lockers from smooth, non-toxic, corrosion-resistantnon-corroding, and easily cleanable materials.

21.3.2 Mount potable water hose lockers at least 450 mm (18 inches) above the deck.

21.3.2.1 Design potable water hose lockers to be self-draining.

21.3.3 Label potable water hose lockers “POTABLE WATER HOSE AND FITTING STORAGE” in letters at least 13 26 25 mm (½1 inch) high.

21.3.4 Provide storage space for at least four 15 m (50 feet) potable water bunker hoses per bunker station.

## 21.4 International Fire Shore Connections and Fire Sprinkler Shore Connections

21.4.1 Install an RP assembly at all connections where hoses from shore-side potable water supplies on shore will be connected to non-potable systems onboard the vessel.

## 21.5 Storage and Production Capacity for Potable Water

21.5.1.a Provide a minimum of 2 days storage capacity that assumes 120 liters (30 gallons) of water per day per person for the maximum capacity of crew and provide passengers on the vessel .

21.5.2, Provide potable water production capacity of 120 liters (30 gallons) per day per person for the maximum capacity of crew and passengers on the vessel.

## 21.6 Potable Water Storage Tanks

### 21.6.1 General Requirements

21.6.1.1 Ensure that potable water storage tanks are independent of the shell hull of the vessel.  (hull of the vessel includes the decks, shell does not)

21.6.1.1.a Ensure that potable water storage tanks do not share a common wall with other tanks containing non-potable water or other liquids.

21.6.1.1.b Provide a 450 mm (18 inch) cofferdam above and between potable water tanks and tanks that are not for storage of potable water and also between potable water tanks and the hull shell. Skin or double-bottom tanks are not allowed for potable water storage.  (There was a discussion about whether or not the top of the tank could be a deck with no final decision.  Yard says more piping will be run over tanks if there are cofferdams between tanks and the deck [if top is deck, then pipes are run around the tanks instead of over].  Owners have a concern that welding may be done on a deck without realizing there is a potable water tank below and damage could be done to the tank surface.  Should we specify that a cofferdam be present above all PW tanks, so the tank top cannot be the deck above?  In 21.6.1.1 we state that tanks must be independent of hull, which includes decks.)

21.6.1.1.c Do not install tanks containing non-potable liquid directly over potable water tanks.

21.6.1.2 Use approved potable water tank coatings.

21.6.1.2.a Follow all of the manufacturers' recommendations for applying, drying, and curing the tank coatings.

21.6.1.2.b Provide written documentation of tank coating approvals from a recognized certification organization.  Provide written documentation that the manufacturer’s recommendations have been followed for these application, drying and curing for the tank coatings used.

21.6.1.3 Coat all items that penetrate the tank (e.g., bolts, pipes, pipe flanges) with the same product used for the tank’s interior.

21.6.1.4 Design tanks to be super-chlorinated one tank at a time.

21.6.1.5 Ensure that lines for non-potable liquids do not pass through potable water tanks.

21.6.1.5.a Minimize the use of non-potable lines above potable water tanks. Do If non-potable water lines are installed above potable water tanks, do not use mechanical couplings on lines above tanks..

21.6.1.5.b If coaming is present along the edges or top of the tank, provide slots along the top of the tank coaming to allow leaking liquids to run off and be detected.

21.6.1.6 Treat welded pipes over the potable water storage tanks in order to make them corrosion-resistant.

21.6.1.7 Treat all potable water lines inside potable water tanks so as to make them jointless and non-corroding corrosion-resistant.

21.6.1.8 Label each potable water tank on its side and where clearly visible, with a number and the words "POTABLE WATER" in letters a minimum of 13 26 25 mm (½1 inch) high.

21.6.1.9 Install at least one sample cock located above the deck plating on each tank.

21.6.1.9.a Point sample cocks down; identify and number them for each with the appropriate tank number.

### 21.6.2 Storage Tank Access Holes Hatch

21.6.2.1 Install access holes hatch for entry on the sides of potable water tanks.

### 21.6.3 Storage Tank Water Level

21.6.3.1 Provide an automatic method for determining the water level of potable water tanks.

21.6.3.1.a Visual site glasses are acceptable.

### 21.6.4 Storage Tank Vents

21.6.4.1 Ensure that air-relief vents end at least 1000 mm (40 inches) above the maximum load level of the vessel.

21.6.4.1.a Make the cross-sectional area of the vent equal to or greater than that of the filling line to the tank.

21.6.4.1.b Position the end of the vent so that its opening faces down or is otherwise protected, and install a 16-mesh corrosion-resistant screen.

21.6.4.2 A single pipe may be used as a combination vent and overflow.

21.6.4.3 Do not connect the vent of a potable water tank to the vent of a non-potable water any other tank or system.

### 21.6.5 Storage Tank Drains

21.6.5.1 Design the tanks to drain completely.

21.6.5.2 Provide a drain opening that is at least 100 mm (4 inches) in diameter and preferably matches the diameter of the inlet pipe.

21.6.5.3 If drained by a suction pump, provide a sump and install the pump suction port in the bottom of the sump.

21.6.5.3.a Use separate pumps to drain the for draining tanks from those used to supply potable water to the distribution system.

21.6.5.3.b Locate the tank drain in the pump discharge line ahead of any branch take-offs to the distribution system. Provide a valve on the distribution main immediately beyond the drain line take-off. (Figure 8).

This statement and the diagram below directly conflicts with 21.6.5.3.a. and 21.7.1.

IMO and classification society rules regarding recesses in double bottoms.  Maybe no sump is allowed.  This diagram is incorrect.  Make a corrected diagram.  Aker Yards will submit a proposal for a change.

## 21.7 Suction Lines

21.7.1 Place suction lines at least 150 mm (6 inches) from the tank bottom or sump bottom.

## 21.8 Potable Water Distribution System

21.8.1 Locate distribution lines at least 450 mm (18 inches) above the deck plating or the normal bilge water level.

*Does this include the lines exiting the tanks.  If so, it is impossible to meet this requirement if the line exits the bottom of the tank and the tank is only 18” above the deck (cofferdam)  Not a problem according to yards.  Distribution lines do not normally come from the bottom of the tank – there are suction lines bringing water to a higher point and then post chlorination occurs for distribution.

21.8.2 Do not cross connect potable water distribution lines with the piping of any non-potable water system lines.

21.8.3 Do not use lead, cadmium or other hazardous materials for pipes, fittings, or solder.

21.8.4 Install Supply only potable water taps in to food areas, the hospital, and themedical facilities, drinking fountains, and all cabin showers and sinks (not just in cabins).  Utility sinks for engine/mechanical spaces are excluded.

21.8.4.a Supply only potable water to handwash sinks, emergency showers and eye wash stations, regardless of the locations of these fixtures on the vessel.

21.8.5 Paint or stripe potable water piping and fittings in auxiliary blue, or in accordance with ISO 14726 at 5000 mm (15 feet) intervals and on each side of partitions, decks, and bulkheads except where decor would be marred by such markings.  This is not required in cabin technical compartments “pilot lockers” where potable water piping is easily identifiable.

21.8.6 Use only potable water for to generate steam that is applied directly to food and food contact surfaces. Generate the steam locally from food service equipment designed for this purpose (e.g., vegetable steamers, combination-ovens, etc.). Only apply non-potable water

21.8.6.a Non-potable water generated steam may be applied indirectly to food or food equipment. Route that steam if routed through coils, tubes, or separate chambers.

21.8.7 Ensure that an air-gap or approved backflow prevention device is present if potable water is supplied to a bilge, waste, ballast, or laundry tank.

Disinfection of the Potable Water System

21.8.8 Clean, disinfect, and flush potable water tanks and any all parts of the potable water distribution system with potable water before the system is placed in service.

21.8.8.a  Ensure that disinfection is accomplished by using 50 mg/l (50 ppm) free chlorine solution for a minimum of 4 hours.  Ensure that only potable water is used for these procedures.

21.8.8.b  Provide written documentation showing that a representative sampling was conducted at various plumbing fixtures on each deck throughout the vessel (forward, aft, port and starboard) to ensure that the 50 mg/l (ppm) free chlorine residual has circulated throughout the distribution system to include the distant sampling point(s).

## 21.9 Potable Water Pressure Tanks

21.9.1 Do not cross-connect potable water hydrophore tanks to non-potable water tanks through the main air compressor.

21.9.2 Provide a filtered air supply from a dedicated compressor or through a non-permanent, quick disconnect or independent for a portable compressor. The compressor shall not emit oil into the final air product.

## 21.10 Potable Water Pumps

21.10.1 Size potable water pumps to meet the vessel’s maximum capacity service demands; do not use them the potable water pumps for any other purpose.

21.10.2 Use non-priming potable water pumps or potable water pumps that prime automatically and not manually. Use a direct connection, not an air-gap, when supplying priming water to a potable water pump.

21.10.3 Properly size potable water pumps and distribution lines so that pressure is maintained at all times and at levels adequate levels to properly operate all equipment.

## 21.11 Evaporators and Reverse Osmosis Plants

21.11.1 Locate the seawater inlets (sea chests) forward of all overboard waste water, swimming pool and whirlpool spa, and ballast tank discharge outlets such as: emergency and routine discharge lines from waste water treatment facilities, the bilge, recreational water facilities, and ballast tanks.  This item requires further discussion, both on what emergency discharges must be located around the ship for safety and stability and if certain lines such as cooling are acceptable forward of sea chests.

21.11.2 Use only direct connections from the evaporators and reverse osmosis plants to the potable water system. Do not use swing lines.

21.11.3 Provide an air-gap or RP assembly between the potable water system and the non-potable water system. (Fresh water produced by an evaporator, or reverse osmosis plant is not considered potable until after it has been pH adjusted to the proper level.)

21.11.3 If an evaporator or reverse osmosis plant makes water for both the potable water system and a non-potable water system, install an air-gap or RP assembly on the line supplying the non-potable water system.

21.11.4 Post narrative, step-by-step operating instructions for manually operated the evaporators, or  and any reverse osmosis plants near the units.

21.11.5 Ensure that high and low-pressurewater production units, connected directly to the potable water lines system have the ability to discharge to the waste system if the distillate is not fit for use.

21.11.6 Install units that have a low-range salinity indicator, an operationoperating temperature indicator, automatic discharge to waste system, and alarm with trip setting on water production equipment.

21.11.7 Route theIf routed for discharge, direct high-saline discharge from evaporators to the bilge or overboard through an air-gap or RP assembly.

## 21.12 Halogenation

### 21.12.1 Bunkering and Production

21.12.1.1 Provide labeled potable water taps with appropriate backflow preventers prevention at the halogen supply tanks.

21.12.1.2 Provide a labeled sample cock at least 3000 mm (120 inches) 3 m (10 feet) downstream of the halogen injection point.

21.12.1.3 Control halogen injection by a flow meter or analyzer.

21.12.1.4 Provide pH adjustment equipment for water bunkering and production. Install analyzer, controller, and dosing pumps that are designed to accommodate changes in flow rates.

### 21.12.2 Distribution

21.12.2.1 Provide a completelyan analyzer controlled, automatic halogenation system that is analyzer controlled.

21.12.2.2 Use halogenation probes that to measure free halogen; link them to the analyzer/controller and chemical dosing pumps.

21.12.2.3 Provide a back-up halogenation system pump, with an automatic switchover, that begins pumping halogen when the primary (in-use) pump fails or cannot meet the preset halogenation level demand.

21.12.2.4 Locate halogen analyzer probe at a distant point in the distribution system where significant water flow exists.

21.12.2.4.a When supplying potable water throughout the distribution network with more than one ring or loop (lower to upper decks or forward to aft) there shall be pipe connections which link those loops and a single distant point monitoring analyzer, or there shall be individual analyzers on each ring or loop.  A single return line which connects to only one ring or loop is not acceptable.  One chart recorder may be used to record two analyzer loop readings.

21.12.2.5 Provide an audible alarm in a continually occupied watch station, (e.g., the engine control room or bridge), to indicate low or high free halogen readings at the each distant point analyzer

21.12.2.6 Provide labeled potable water taps with appropriate backflow preventers preventions at halogen supply tanks.

21.12.2.7 Locate a labeled sample cock at least 3000 mm (120 inches) 3 m (10 feet) downstream of the halogen injection point.

21.12.2.8 Provide continuous recording free halogen analyzer-chart recorder(s) with ranges of 0.0 to 5.0 mg/l (ppm) and continuous recording periods indicating the level of free halogen for 24 hour time periods, (e.g., circular 24 hour charts).

21.12.8.a Electronic data loggers with certified data security features may be installed in lieu of chart recorders. Acceptable data loggers produce records that conform to the principles of operation and data display required of the analog charts, including printing the records. Use electronic data loggers that log times in increments of <15 minutes.

## 21.13 Disinfection of the Potable Water System

21.13.1 Disinfect the entire distribution system with a free halogen concentration of at least 50 mg/L (ppm) for at least 4 hours. Prior VSP agreement is required if alternative approved disinfection practices are used.

21.13.2 Provide written documentation of the distribution system disinfection.

# 22.0 Backflow Prevention Cross-Connection Control

22.1 Use appropriate backflow prevention at all non-potable cross-connections (e.g., air-gaps, RP assemblies, pressure vacuum breakers, atmospheric vacuum beakers, pressure-type backflow preventers, or double-check valves with intermediate atmospheric vent) for in the potable water system.

22.2 Use air-gaps that are at least twice the diameter of the supply pipe measured vertically above the flood level rim of the receiving vessel. The air-gap must at least 25 mm (1 inch).

22.3 Install RP assemblies in high-hazard situations where air-gaps are not practical.

22.4 If RP backflow prevention assemblies are used, provide a test kit for testing the devices.

22.4.a Test all RP’s after installation.

22.5 Use mechanical backflow prevention devices when water must be supplied under pressure.

This may include non-mechanical protection such as an air-gap or a mechanical backflow prevention device.

Air-gaps should be used where feasible and when water under pressure is not required.

A mechanical backflow prevention device must have an atmospheric vent.

22.3 Ensure that connections where there is a potential of a health hazard  are protected by air-gaps or backflow prevention device designed to protect against health hazards.

22.4 For all testable devices provide an appropriate test kit .

22.4.a Test all testable devices after installation and provide pressure differential test results for each device.

22.6 When used, install an atmospheric vacuum breaker (AVB) 150 mm (6 inches) above the fixture flood level rim with no valves downstream from of the device.

22.7 Connect potable water through an air-gap when it is directed to a black water tank for rinse down or other such uses. RP assemblies are inadequate in this high hazard condition

Ensure an AVB or hose-bib connected vacuum breaker (HVB) is not installed at a connection where it can be subjected to continuous pressure for more than 12 hours out of a 24 hour period.

22.7 Ensure that any connection between the potable water system and the black water system is through an air-gap.   When feasible, water required for the black water system should be from the technical water system.

22.8 Protect the following connections to the potable water system against backflow or (back-siphonage or back-pressure)  by with air-gaps or mechanical backflow prevention devices:

22.8.1 Potable water supply lines to Recreational water facilities such as swimming pools, chidlren’s pools, whirlpool spas, hot tubs, bathtubs, showers, and similar facilities.

Decorative water features/fountains.

Cabin shower hoses, toilets, whirlpool tubs, and similar facilities

22.8.2 Photographic laboratory developing machines and utility sinks.

22.8.3 Beauty and barber shop spray-rinse hoses.

22.8.4 Potable water faucets where hoses maybe connected.  Spa steam generators where essential oils can be added

22.8.4 Hose-bib connections.

22.8.5 Garbage grinders and food waste systems.

22.8.   Automatic galley hood washing systems

22.8  Food service equipment such as coffee machines, ice machines, juice dispensers, combination ovens and similar equipment.

22.8.6 Mechanical warewashing machines

22.8 Detergent dispensers.

22.8.7 Hospital and laundry equipment.

22.8.8 Air conditioning expansion tanks.

22.8.9 Boiler feed water tanks.

22.8.10 Fire system.

22.8.11 Public toilets, urinals and shower hoses.

22.8.12 Potable water, bilge, and sanitary pumps that require priming.

22.8.13 Freshwater or saltwater ballast systems.

22.8.14 International fire and fire sprinkler water connections.  An RP is the only allowable device for this connection.

22.8.15 The potable water supply to automatic window washing systems which utilize can be used with chemicals or chemical mix tanks.

22.8.16 Water softeners for non-potable fresh water if located before an air-gap.

22.8.17 Water softener and mineralizer drain lines must be protected by an air-gap or RP assembly including backwash drain lines.  An AG or RP are the only allowable protections for these lines.

22.8.18 High saline discharge line from evaporators.  An AG or RP are the only allowable protections for these lines.

22.8.   Chemical tanks

22.8.19 Any other connection between the potable water system and a non-potable water system such as the grey water system, laundry system or technical water system.  An AG or RP are the only allowable forms of protection for these connections

22.8.20  Black water or combined gray water/black water systems.  An AG is the only allowable protection for these connections.

22.8.21 Any other connection to the potable water system where contamination or backflow can occur.

## 22.9 Heat Exchangers Used for Cooling or Heating Potable Water

22.9.1 Fabricate heat exchangers, using, or for cooling or heating potable water so a single failure of any barrier will not cause a cross-connection or permit back-siphonage of contaminants into the potable water system.

22.9.2 Design heat exchangers where both potable water and any non-potable liquid are used to protect the potable water from contamination by one of the following designs;

22.9.2.a Double-wall construction between the potable and non-potable liquids, with a void space to allow any leaking liquid to drain away; and

22.9.2.a.1 An alarm system to indicate a leak in the double wall.

22.9.2.b Single-wall construction with the following safety features:

22.9.2.b.1 Higher pressure of at least 1 bar on the potable water side of the heat exchanger; and

22.9.2.b.2 An automatic diverter valve that directs potable water from the heat exchanger when the pressure difference is less than 1 bar; and

22.9.2.b.3 An alarm system that sounds when the diverter valve directs potable water from the heat exchanger.

22.10.  Provide an air-gap or backflow prevention device at connections to the distillate line intended for the potable water system.

Annex for back of Guidelines:

Participants are invited to make recommendations for additions to this section.

Add backflow protection selection key, diagrams of devices, blank form for a cross-connection control listing, RP testing form and cross-connection control survey form

Backflow Prevention Selection Considerations

An AG is the highest form of protection and should be selected wherever feasible

Where a device is installed and the potential for backpressure exists a device that protects against backpressure must be used

A CP backflow prevention device should be used when there is a valve downstream of the device or the device will be under continuous pressure for more than 12 hours out of a 24-hour period.  Valves include spray guns at the end of a hose, juice machines, coffee machines and similar equipment if the solenoid valve to operate the equipment is after or downstream of the backflow prevention device.

A backflow prevention device with an internal stainless steel construction should be used in locations where the fluid has a pH below 6.  In such cases there should be no fittings or lines of copper or copper alloys between the equipment generating the low acid fluid and the backflow prevention device.  This is especially important at soda carbonation units, juice units and beer brewing equipment.

Install devices in accordance with manufacturer’s recommendations to include the correct orientation and distance from the decks and bulkheads.

Ensure that manufacturer specified tolerances for temperature and pressure are not exceeded.

# 23.0 Swimming Pools Recreational Water Facilities (RWF) (provide information on how this new section is organized.)

Note somewhere that this includes crew pools.

# Water Source

23.1 Use Provide an independent filling system that allows for the filling of each RWF with sanitary seawater, or potable water supply passing through an air-gap or backflow preventer to fill swimming pools. For a make-up tank supplied with potable water, an overflow line located below the fill line at least twice the diameter of the fill line is an acceptable method of backflow protection provided that the overflow line discharges to the waste water system through an indirect connection.

Where make-up water is required to replace water loss due to splashing, carry out and other volume loss install an appropriately designed pre-treatment storage tank to ensure that adequate chemical balance can be maintained.

Showers and Toilet Facilities

23 Provide showers with water supplied at temperature not to exceed 110°F in close proximity to entrances of RWFs.  (Shower locations and numbers will be evaluated during plan reviews).  Provide soap dispensers at each shower.

RWF’s intended for use by children under 6 years of age should have appropriately sized shower facilities.  Provide size details (e.g., max height).

Locate toilet facilities within 30 meters of each RWF on the same deck.  It was suggested that this distance be one fire zone (40-44 meters) and there was general agreement on this.  There is a question of # of toilets/urinals per toilet facility.  Is a male and female toilet room required at each RWF?  Should this be based on bather capacity of the RWFs?

Provide diaper changing facilities within 30 meters (same fire zone distance recommendation) and on the same deck of any RWF for children in diapers or who are not toilet trained.   If these facilities are placed within toilet rooms there shall be one facility located within each toilet room (men’s, women’s and unisex).  Diaper changing facilities shall be equipped in accordance with section (child activity center?)

RWF Tub Drainage

23.2 Provide an independent pool drainage system for RWF’s from other drainage systems.   If swimming pool RWF drains are connected to another drainage system, provide an air-gap or a double-check valve RP assembly between the two.

23.2.a Install a drain at the lowest point in the pool.

23.3 Slope the bottom of the pool RWF towards the drains to achieve complete drainage.

23.4 Provide anti-entrapment type drain covers that are constructed of durable easily visible, easily cleanable material and that meet ASME/ANSI A112.19.8M voluntary standard for suction fittings (figure 9a-9c), or other drains that prevent entrapment hazards as specified in U.S. Consumer Product Safety Publication 363-009801 (figure 9-10b). Dual

If seating is provided inside an RWF ensure that drains are installed to allow for complete draining of the seating area (including but not limited to seats inside whirlpool spa and spa pools).

Make sure that all decorative and working features of an RWF are completely draining, non-porous and easily to clean.  These features shall be designed to be shock halogenated.

Safety

Anti-entrapment

Drain Covers for Lines under direct suction

23.3.a Where feasible install dual drains that are at least 1 meter (3 feet) apart and at the lowest point in the RWF.  Ensure that there are no intermediate drain isolation valves on the line between the drains.  Fig. #.  Install anti-entanglement drain covers over these drains.

23.4 b Channel drains may meet the anti-entrapment requirements if the channel is at least XXXmeters in length. Fig. 10a 10b

Where due to RWF size limitations a single drain is the only option ensure that the drain cover is desgined and certified in accordance with the anti-entrapment anti-entanglement requirements set forth in ASME/ANSI A112.19.8M.

23.5 Ensure that the fill level of the pool is at the skim gutter level

Custom built drain covers that are not stamped as certified shall be tested in accordance with the standards set forth in ASME/ANSI A112.198M.

A letter documenting the specifications of the drain cover, to include the maximum flow rate, the standard it was tested against, the RWF for which it was tested and a statement indicating that drain cover met the standard shall be provided for each custom built drain cover.

Suction Fitting Covers

Ensure that suction fitting covers are certified in accordance with anti-entrapment and anti-entanglement requirements set forth in ASME/ANSI A112.19.8M.

Custom built suction fitting covers that are not stamped as certified shall be tested in accordance with the standards set forth in ASME/ANSI A112.198M.

A letter documenting the specifications of the suction fitting cover, to include the maximum flow rate, the standard it was tested against, the RWF for which it was tested and a statement indicating that suction fitting cover met the standard shall be provided for each custom built suction fitting cover.

Depth Markers

Install depth markers for each RWF where the maximum water depth is 1 meter (3 feet) or greater.  Install depth markers so that they can be seen from the deck and the tub.  Ensure that the markers are in both meters and feet.  Additionally, depth markers shall be installed for every 1 m (3 feet) change in depth.

Safety Signs

Install appropriate safety signs at each RWF, except for aquatic spray pad facilities.  At a minimum the signs shall include:

- Do not use these facilities if you are experiencing diarrhea, vomiting, fever, or infected cuts/boils

- No running or boisterous play

- No children in diapers or who are not toilet trained

- No eating or drinking

- No glass

- No diving

- No lifeguard on duty

- Shower with soap and water before entering the facility

- Maximum bather load #

For the children’s RWF signs, include “take children on frequent bathroom breaks”.

See section (#) Whirlpool Spas and Section (#) Aquatic Spray Pad Facility for signs specific to those RWF’s.

Life Saving Equipment

Provide a shepherd’s hook (crook) and floatation device in a prominent location for each RWF where the maximum depth is 1 meter or greater.  Mount the equipment so that it is visible from all areas of the RWF and so that it is easy to remove for use.  The shepherd’s hook must be a light non-telescopic reaching pole not less than  3.7 m (12 feet) and able to reach the center bottom of the RWF.  The floatation device must have a length of rope attached that is able to span the maximum width of the RWF.  The minimum exterior diameter of the floatation device shall be  44 mm (17 inches)

The meeting ended here – below this line, only section 27.0 was reviewed during the meeting in Turku.  A couple of questions were asked regarding section 28.0 and those are noted within the text.

Recirculation and Filtration Systems

23.5 Where skim gutters are installed ensure that the filling of the RWF is to the skim gutter level.

23.6 Ensure that pool overflows are either directed by gravity to the make-up tank for recirculation through the filter system or disposed of as waste.

23.7 Install recirculation, filtration and disinfection equipment.  Alternatively, overflows may be directed to the wastewater system through an indirect connection.

23.8 Use pool equipment (e.g.,

23.6a Ensure that 100% of the water in the make-up tanks passes through the filtration and disinfection systems prior to returning to the RWF.  This includes any water directed to water features in RWF’s.

23.9 Ensure that pumps used to recirculate the RWF water are centrifugal pumps that are self-priming or that prime automatically. centrifugal pumps and filters) that has the capacity to turnover the pool water at least four times every 24 hours (i.e., once every 6 hours or less).

23.9 Use to re-circulate pool water.

23.10 Install pumps large enough to re-circulate the entire volume of the pool in 6 hours.

23.11 Install surface skimmers or gutters that are capable of handling approximately 80% of the filter flow of the recirculation system.

23.12 If skimmers are used instead of gutters, install at least one skimmer for each every 47 m² (500 ft² square feet) of pool surface area.

23.13 Provide a hair strainer between the pool RWF outlet and the suction side of the pumps to remove foreign debris such as hair, lint, pins, etc.

23.14 Ensure that the removable portion of the hair strainer is corrosion-resistant and has holes no greater than 6 mm (¼ inch) in diameter.

Filters

23.15 Use filters that are designed to remove all particles greater than 20 micrometers from the entire volume of the pool in 6 hours or less RWF within the specified turn-over rate.

23.16 Use cartridge or media-type filters (e.g., rapid-pressure sand filters, high rate sand filters, diatomaceous earth filters, or gravity sand filters). Make filter sizing consistent with American National Standards Institute (ANSI) standards for public pools RWF’s.

23.17 Use Ensure that media-type filters that are capable of being back-washed.  Provide a clear sight glass on the backwash side of all media filters.

23.18 Provide Install filter accessories, such as pressure gauges, air-relief valves, and rate-of-flow indicators meters.

23.19 Provide automatic dosing of chemicals for disinfection and pH adjustment.

Design and install filters and filter housings in a manner that allows access for inspection, cleaning and maintenance.

23.20 If desired, use a make-up tank to replace water lost by splashing and evaporation.  If the tank is supplied with potable water, ensure that the supply enters through an air-gap or backflow preventer. An overflow line at least twice the diameter of the supply line and located below the tank supply line as backflow prevention is acceptable provided it drains through a visible air-break.

Turn-over Rates

23.21 Provide easy access to the media filters so that they can be inspected at least on a weekly basis and the media can be changed periodically.

Install recirculation pumps, filtration and disinfection equipment that have the capacity to turnover the RWF water at the appropriate rates as set forth in table ### (based on ANSI/IAF-9 Standard per Aquatic Play Feature Handbook)

| RWF Type | Turnover Rate (Hours) |
| --- | --- |
| Swimming Pool | 4-6 |
| Wading Pool | 0.5-1 |
| Whirlpool Spa | 0.5-1 |
| Spa Pool | 2 |
| Aquatic Spray Pad | 1 |
| Activity Pool (continuous current, surfing pool, wave pool, etc) | 1-2 |

Primary Disinfection and pH Control

23.19 Install an independent automatic analyzer controlled halogen based disinfection and pH dosing systems for each RWF.

Provide probes and digital readouts for pH, free halogen residuals (ppm) and oxidation-reduction potential.

Similar types of RWF’s may be combined and operated under one system for halogenation, pH control and filtration provided that all operational parameters can be met.

Children’s Pools may not be combined with another type of RWF.   Aquatic Spray Pad Facilities may not be combined with another type of RWF

23.20.a Design water features such that the water cannot be taken directly from the tank but must be first routed through filtration and disinfection systems.

23.22 Provide water sample points on the system for pH and halogen level manual testing and routinely calibrating routine calibration of the analyzer.  Testing points should be located prior to chemical injection.

23.23 Provide analyzer controlled halogen-based disinfection equipment.

23.24 Ensure that pH adjustment is accomplished by using appropriate acids and bases and that a buffering agent is used to stabilize the pH. Control the injection of acids and bases by an analyzer.

Secondary Disinfection

Install a secondary disinfection system for each children’s pool and aquatic spray pad facility.  Secondary disinfection systems should be appropriately sized to disinfect 100% of the water at the appropriate turnover rate.  Secondary disinfection systems are to be installed after filtration but prior to halogen based disinfection.  Unless otherwise approved by VSP secondary disinfection shall be accomplished by a UV or ozone based disinfection system.

RWF Mechanical Room (Pump Room)

23.25 Make pool RWF mechanical rooms accessible, and well-ventilated, and provide a potable water tap with appropriate backflow protection.

Design pump rooms so that operators are not required to stoop, bend or crawl to access RWF systems.

23.26 Mark all piping with directional-flow arrows and maintain a flow diagram and operational instructions in a readily available location.

23.27 Design the pool RWF mechanical room and recirculation system for easy and safe chemical storage and re-filling of chemical feed tanks.

23.28 Install deck drains in the pool each RWF mechanical room that allow rapid allows for draining of the entire pump and, filter system; install a minimum 80 mm (3 inch) drain on the lowest point of the system.  , make-up tank and associated piping.  Slope the deck in the pump room to the deck drains.

RWF System Drainage

Install drains in the RWF system to allow for complete drainage of the entire volume of water from the pump, filter system make-up tank and all associated piping.

23.29 Provide a drain in at the bottom of each make-up tank to allow for complete draining of the tank.  the pool so that it can be seen from the deck and in the pool. Label depth markers either in feet or meters, or both. Install additional depth markers for every 1 m (3 feet) change of depth and prominently display them so that they can be seen from the deck and in the pool.

Install a tap supplied with potable water in each RWF pump room.

# Swimming Pools

# 24.0 Children’s Pools

Provide a method to prevent access to the pool when not in use.

Design the pool such that the maximum water level cannot exceed 1 meter (3 feet).

24.1 Follow all requirements in Section 23.0.

24.2 Provide an independent recirculation, filtration and halogenation system in children’s pools.

24.3 Use a water turn-over rate of is at least once every 30 minutes.

New Section: Aquatic Spray Facility

Water Source

Fill water shall be provided only to the make-up tank and not directly to the spray pad.

Spray Pad Structure and Facilities

Ensure that the decking material for the pads is durable, non-absorbent, slip-resistant, and non-toxic.

25  Design and slope the deck surface of the spray pad to ensure complete drainage and prevent pooling/ponding of water.

25  Provide adequate gravity drains throughout the spray pad to allow for complete drainage of spray pad.  Suction drains are not permitted.

25 Ensure that 100% of the gravity drains are directed to the spray pad feature make-up tank.

25  Ensure that the drains can be diverted to the waste water system through an indirect connection prior to returning to the make-up tank.

25.  The spray pad feature shall be designed and constructed to prevent run-off from the surrounding deck from entering the spray pad feature

Safety Sign

In addition to the RWF safety sign (section #), install an easy to read permanent sign, with letters at least 26 mm (1 inch) high at each entrance to the spray pad feature which at a minimum states:

- No Lifeguard on duty

- This facility is intended for use by children in diapers.

- Use of this facility may put children at increased risk for illness

- Children who have a medical condition which may put them at increased risk of illness should not use these facilities.

- Children who are experiencing symptoms such as vomiting, diarrhea, skin sores or infections are prohibited from using these facilities.

- Children in diapers or who are not completely toilet trained must wear a swim diaper.

- Children must be accompanied by an adult at all times

- Do not change diapers in the area of the spray pad facility.  A diaper changing station has been provided (exact location) for your convenience.

Recirculation and Filtration System

Install a make-up tank with an automatic level control system capable of holding an amount of water sufficient to ensure continuous operation of the filtration and disinfection systems.  Install a drain at the bottom of the tank to allow for complete draining of the tank.

Design the system such that 100% of the water for the spray pad feature passes through filtration, secondary disinfection and halogenation prior to returning to the spray pad.

Disinfection and pH Control

Provide an automatic monitoring and recording system for the free halogen residual and pH levels.  The recording system shall be capable of recording these levels 24 hours/day.

Provide a secondary UV disinfection system capable of inactivating cryptosporidium.  Ensure that these systems are installed in accordance with the manufacturer’s specifications.  Secondary UV disinfection systems shall be designed to operate in accordance with the parameters set forth in NSF International for use in spray pad facilities.

Install an automatic control that shuts off the water supply to the spray pad in the event that the free halogen residual or pH range have not been met per the requirements set forth in the most current VSP Operational Manual.  The shut-off control shall operate similarly when the UV disinfection system is not operating within acceptable parameters.

Install UV systems that allow for cleaning of the lamp jacket without dissembling the unit.

A spare ultraviolet lamp shall be provided as well as all of the necessary repair materials and operational instructions.

Spray Pad Pump Room

All recirculated water discharged to waste must be through a visible indirect connection in the pump room.

# 25.0 Whirlpool Spas and Spa Pools

For whirlpool spas, design the overflow system so that the water level is maintained.

25.1 Provide a temperature control mechanism to prevent the temperature from exceeding 40ºC (104ºF).

25.4 Design the overflow system so that water level is maintained.

25.5 If skimmers are used instead of gutters, use one skimmer for every 14 m² (150 square feet) or fraction thereof of water surface area.

25.6 Provide an independent whirlpool drainage system. If the whirlpool drainage system is connected to another drainage system, provide a double-check valve between the two.

25.7 Provide drains and ensure the bottom of the whirlpool slopes toward the drains to affect complete drainage.

25.7.a Use whirlpools seating areas that drain completely.

25.8 Provide anti-entrapment type drain covers constructed of durable easily visible, easily cleanable material and that meet ASME/ANSI A112.19.8M voluntary standard for suction fittings (figure 9a-9c), or other drains that prevent entrapment hazards as specified in U.S. Consumer Product Safety Publication 363-009801 (figures 9a-10b) dual drains meet the anti-entrapment requirements.

25.9 Design the system to permit daily shock treatment or super-halogenation in accordance with the VSP Operations Manual.

25.10 Install systems in a manner that permits routine visual inspection of the granular media filters in accordance with the VSP Operations Manual.

25.11 Ensure that the fill level of the whirlpool is at the skim gutter level.

25.12 Ensure that whirlpool overflows are either directed by gravity to the make-up tank for recirculation through the filter system or disposed of as waste.

25.13 Use self-priming, centrifugal pumps to re-circulate whirlpool water.

25.14 Provide a hair strainer between the whirlpool outlet and the suction side of the pumps to remove foreign debris such as hair, lint, pins, etc.

25.15 Ensure that the removable portion of the strainer is corrosion-resistant and has no holes greater than 6 mm (¼ inch) in diameter.

25.16 Use filters that are designed to remove all particles greater than 20 micrometers from the entire volume of the whirlpool in 30 minutes or less.

25.17 Use filters that are cartridge, or media type (e.g., rapid-pressure sand filters, high-rate sand filters, diatomaceous earth filters, or gravity sand filters). Make filter sizing consistent with ANSI standards for public pools.

25.17.1 Provide a clear sight glass on the backwash side of the filters.

25.18 Design and install filters in a manner that allows for easy access for inspection and maintenance.

25.19 Make all media-type filters capable of being back-washed.

25.20 Provide filter accessories, such as pressure gauges, air-relief valves, and rate-of-flow indicators.

25.21 A make-up tank may be used to replace water lost by splashing and evaporation. If the tank is supplied with potable water, ensure that the supply enters through an air-gap or backflow preventer. An overflow line at least twice the diameter of the supply line and located below the tank supply line may be used as backflow prevention.

25.22 Provide analyzer controlled chemical dosing for both pH and disinfection.

25.23 Accomplish disinfection by chlorination or bromination.

25.24 Provide water sample points on the system for the testing of halogen levels and routine calibration of the analyzer.

25.25 Accomplish pH adjustment by using appropriate acids and bases and that a buffering agent is used to stabilize the pH. Control acid and bases injections by an analyzer.

25.26 Make the whirlpool mechanical room accessible and well-ventilated and provide a potable water tap.

25.27 Mark all piping with directional-flow arrows and maintain a flow diagram and operational instructions in a readily available location.

25.28 Design the pool mechanical room and recirculation system for easy and safe chemical storage and re-filling of chemical feed tanks.

25.29 Install drains in the whirlpool mechanical room to allow for rapid draining of the entire pump and filter system; install them so that a minimum 80 mm (3 inch) drain is on the lowest point of the system.

25.30 Provide a drain in the make-up tanks to allow complete draining.

  - 25.31 Make sure that all decorative features of whirlpool spas are completely draining, non-porous and easy to clean.

25.2 For whirlpool spas, install an alarmed system shut-off switch at a visible, easy to access location to allow users to turn it off in an emergency.

25.3 In addition to the RWF safety sign (section#),  install a sign at each whirlpool spa and spa pool listing precautions and risks associated with the use of these facilities.

Include at a minimum the following precautions and warnings:

- Caution:  pregnant women, elderly persons, and persons suffering from heart disease, diabetes, or high or low blood pressure should not enter the spa without prior medical consultation and permission from their doctor.

- Do not use while under the influence of alcohol, tranquilizers or other drugs that cause drowsiness or that raise or lower blood pressure.

- Prolonged exposure may result in nausea, dizziness, or fainting.

- Raised body temperature can lead to heat stroke and death.

- Unsupervised use by children is prohibited

- Individuals who are  immunocompromised should consult a physician prior using these facilities

Provide a line in the drainage system to allow the whirlpool to be drained to the grey water or technical water system through an indirect connection.

# 26.0 Miscellaneous Cleaning Materials, Filters, and Drinking Fountains

# (Move this section to just after section 19 (lighting)

## 26.1 Facilities and Lockers for Cleaning Materials

26.1.1 Provide bulkhead-mounted racks on which hang wet for brooms and mops, or provide sufficient space and hanging brackets within cleaning lockers. Locate bulkhead-mounted racks outside of food storage, preparation, or service areas. These racks may be located on the soiled side of warewash areas.

26.1.2 Provide stainless steel vented lockers, with coved deck and wall junctures, for storing buckets, detergents, sanitizers, cloths, etc and other wet items.

26.1.3 The number of lockers Size and locate the location and size of lockers is determined by the according to the needs of the vessel and  make access to lockers containing cleaning materials convenient.

26.1.3.a Provide a single cleaning room for each deck of multiple level galleys, if cleaning lockers are not provided in each of the preparation areas.  Construct rooms used for cleaning materials in accordance with section 16.0 .

26.1.4 Provide accessible facilities equipped with a mop sink and adequate deck drain or a pressure washing system for cleaning mops and buckets and that are separate from food facilities.

26.1.5 Label all cleaning lockers and cleaning rooms “Cleaning Materials Only.”

## 26.2 Filters

26.2.1 If used, install only point-of-use potable water filters on ice machines, combination ovens, beverage machine, etc. A single point-of-use filter can be installed on the potable water supply line to a beverage counter.

## 26.3 Drinking Fountains

26.3.1 Ensure that the water jet orifices outlets from drinking fountains are slanted and that the orifice is protected by a sanitary guard. cover to prevent contamination. Do not allow lead in the water storage tanks and plumbing serving water fountains

26.3.2 Provide drinking fountains with stainless steel cabinets and without filling spouts in food preparation areas.

26.3.3 Provide drinking fountains that will allow the user to control of the water stream.

26.3.4 Install drinking fountains that are accessible to galley personnel.

## 26.4 Facility for Cleaning of Maintenance Equipment

26.4.1 Provide facilities (e.g., deep utility sinks) with hot and cold water or a pressure-washing system with a deck sink and drain for cleaning of maintenance equipment such as brooms and mops. Provide bulkhead-mounted racks or hooks for hanging the equipment for drying. Separate room(s) designated for this purpose from food preparation and warewashing areas.

# 27.0 Ventilation Systems

## 27.1 Air Supply Systems

27.1.1 Design fan rooms so that they are and install air handling units to be accessible for periodic inspections and air intake filter changing.

27.1.2 Design Install air condition condensation condensate collection pans to drain completely.

27.1.2.a Use air conditioner condensation Connect condensate collection pans that are designed to drain through closed piping to prevent condensate from pooling on the decks.

27.1.3 Locate air intakes for fan rooms each air handling unit so that any ventilation or processed exhaust air is not drawn back into the vessel.  (There are some supply fans that are not part of air handling units – fan rooms refers to both supply fans and air handling units)

27.1.4 Provide a sufficient make-up air supply in all food preparation, warewashing, cleaning rooms, and toilet rooms.

27.1.5 Design all cabin air vent diffusers for easy removal and cleaningto be removable.

27.1.6 Make air handling unit condensate drain collection pans easily readily accessible for inspection, cleaning and cleaning, and accessible for maintenance. Make sure that Provide access panels to all major air supply trunks have access panels to allow for periodic inspection and cleaning.

27.1.7 Provide a separate, independent air supply system for the engine room and other mechanical compartments spaces, (e.g., fuel separation, purifying, and black water treatment rooms) which are located in and around the engine room.

## 27.2 Air Exhaust Systems

27.2.1 Air handling devices units in the following areas must exhaust air through independent systems that are completely separated from systems using re-circulated air:

27.2.1.1 Engine rooms and other mechanical spaces; Aker Yards stated that negative pressure in the engine room is very difficult due to all of the supplies into that area.  It was suggested to separate engine rooms and machinery spaces into 2 separate line items.

27.2.1.2 Hospitals, infirmaries, and any rooms used for patient care or isolation;

27.2.1.3 Indoor swimming pools swimming pool: recreational water facilities, dome type swimming poolsrecreational water facilities when closed; whirlpool spa facilities, and supporting mechanical rooms.

27.2.1.4 Galleys and other food preparation areas;

27.2.1.5 Cabin and public toilet rooms; or

27.2.1.6 Waste processing areas.

27.2.2 Maintain negative air pressure, in relation to the surrounding areas, in the areas listed under Section 27.2.1.

27.2.3 Provide a sufficient exhaust system in all food preparation, warewashing, cleaning rooms, and toilet rooms to keep them free of excessive heat, humidity, steam, condensation, vapors, obnoxious odors, and smoke.

27.2.4 Provide access panels to all major air exhaust trunks with access panels to allow for periodic inspection and cleaning.

27.2.5 Provide a written ventilation system balancing report for those areas listed in Section 28 27.2.1.

# 28.0 Child Care and Child Activity Facilities Center

28.1 Include the following in child care and child activity facilities center:

28.1.1 Handwashing facilities that are accessible without barriers such as doors to each child activity and child care area. Teen areas center. Areas only for children 6 and over are exempt from the handwashing facilities requirement.

Handwashing facilities;

Provide hot and cold potable water to all handwashing sinks.

Equip handwashing sinks to provide hot water at a temperature not to exceed 430 C (1100 F).

Provide handwashing facilities that include a soap dispenser, paper towel dispenser or air dryer and a waste receptacle.

28.1.2 Toilet rooms in child care and child activity centers including shall include:  Should we have a minimum number of toilets based on the max number of children allowed in a center?

28.1.2.1 Child-sized toilets (to include the toilet seat) with a maximum height of 280 mm (11 in).*;

28.1.2.2 Handwashing facilities;

28.1.2.3 A covered waste receptacle; Provide hot and cold potable water to all handwashing sinks

28.1.2.4 A sign advising users to wash their hands after using the toilet.

Equip handwashing sinks to provide hot water at a temperature not to exceed 430 C (1100 F).

Install handwashing sinks with a maximum height of 560 mm (22 in) above the deck.*

Provide handwashing facilities that include a soap dispenser and paper towel dispenser or air dryer, and a waste receptacle.

Provide storage for gloves and wipes.

28.1.2.4 A sign stating “Wash your hands and assist the children with handwashing after helping them use the toilet.”

28.2 Provide a diaper-changing station and disposal facilities in child care facilities.  activity centers where children in diapers or children who are not toilet trained will be accepted.

Include the following in each diaper changing station:

28.2.1 A diaper changing table designed for diaper changing that is impervious, non-absorbent, non-toxic, smooth, durable, and cleanable, and designed for diaper changing;

28.2.2 An airtight, soiled-diaper receptacle;

28.2.3 An adjacent handwashing station;

A storage area for diapers, gloves, wipes, and disinfectant; and

28.2.4 A sign advising child care facility staff to wash their stating “Wash your hands after each diaper change.”

28.3 Provide separate toilet and handwashing facilities for child care providers.  (Can this be a public toilet within a certain distance of the center?)

Furnishings

Surfaces of tables, chairs and other furnishings should be constructed of an easily cleanable non-absorbent material.

# 29.0 Housekeeping

29.1 Provide handwashing stations for housekeeping staff. VSP will evaluate the number and location for these handwashing stations during the plan review process.

Ensure that at least one handwashing station is available for each cabin attendant work zone and on the same deck as the work zone.  One handwashing station may be located between two cabin attendant work zones and travel across crew passageways is permitted.

Handwashing stations for housekeeping staff include those in ice/deck pantries but do not include those located in bars, room service pantries, bellboxes, or other food service areas.

Handwashing station not located in ice/deck pantries must have a paper towel dispenser or air hand dryer, soap dispenser, and a waste receptacle; provide water at a temperature between 41°C (105°F) and 49°C (120°F) through a mixing valve; and be installed to allow for easy access by cabin attendants.  Handwash stations inside of ice/deck pantries must be installed in accordance with section 7.0.

# 30.0 Passenger and Crew Public Toilet Rooms

30.1 Provide either of the following in the public toilet rooms:

30.1.2 Hands-free exits from toilet rooms such as; doorless entry, automatic doors openers, latchless doors that open out

or

30.1.1 Paper towel dispensers with at or after handwashing stations and a waste receptacle near the last exit door(s) to allow for towel disposal after opening the exit door(s).

# 31.0 Decorative Fountains and Misting Systems

31.1 Provide potable water to all decorative fountains, misting systems and similar facilites.

31.2 Ensure that Design and install decorative fountains are designed, misting sytems and similar facilities to be maintained free of Mycobacterium, Legionella, algae and mold growth.

Install an automated treatment system (halogenation, UV or other effective disinfectant) to prevent the growth of Mycobacterium and Legionella in any decorative fountain, misting systems and similar facilities.  Ensure that these systems can also be manually disinfected.  Ensure that misting nozzles are removable for cleaning and disinfection.

Provide operational schematics for misting systems.

# 32.0 Acknowledgements

## 32.1 Individuals

This document is a result of the cooperative effort of many individuals from both the government and private industry, and the public. VSP staff thanks all of those who submitted comments and participated throughout this lengthy process.

## 32.2 Standards, Codes, and Other References Reviewed For Guidance

* Caring for Our Children:  National Health and Safety Performance Standards: Guidelines for Out-of-Home Child Care, 2nd Edition (page 238)

National Resource Center for Health and Safety in Child Care and Early Education http://nrc.uchsc.edu/CFOC/index.html

American National Standards Institute/The Association of Pool & Spa Professionals. ANSI/APSP-7 2006.  American National Standard for Suction Entrapment Avoidance in Swimming Pools, Wading Pools, Spas, Hot Tubs, and Catch Basins.  Alexandria, Virginia.  For more information, visit URL: http://www.TheAPSP.org.

32.2.1 National Sanitation Foundation (NSF) International. 2005. Certification policies for food equipment and ANSI/NSF International Standards 2–59 for food equipment, through 2005. Ann Arbor, Michigan. For information, visit the NSF International Web site at URL: http://www.nsf.org/.

32.2.2 Underwriters Laboratories (UL). 2005. Northbrook, Illinois. For information on UL standards, visit URL: http://www.ul.com/clients/.

32.2.3 American National Standards Institute/National Spa & Pool Institute. 2004. Standard for public swimming pools and standard for public spas, standard 50: circulation system components and related materials for swimming pools, spas/hot tubs. NSF/ANSI 50-2004. Ann Arbor, Michigan. For more information, visit URL: http://www.nsf.org/.

32.2.4 National Resource Center for Health and Safety in Child Care. 2002. Caring for our children: national health and safety performance standards: guidelines for out-of-home child care programs, second edition. Available through URL: http://nrc.uchsc.edu/CFOC/.

32.2.5 Food and Drug Administration. 1997, 1999, and 2001. Food Code. Rockville, Maryland: US Department of Health and Human Services. Available through URL: http://www.cfsan.fda.gov/~dms/foodcode.html.

Foundation for Cross-Connection Control and Hydraulic Research. 1993.  Manual of Cross-Connection Control, 9th Edition. University of Southern California, Los Angeles, California.  For more information visit URL: http://www.usc.edu/dept/scchr.

32.2.6 International Code Council. 2003. International Electric Code. Falls Church, Virginia. For information, visit URL: http://www.iccsafe.org/.

32.2.7 International Code Council. 2003. International Mechanical Code. Falls Church, Virginia. For information, visit URL: http://www.iccsafe.org/.

32.2.8 International Code Council. 2003. International Plumbing Code. Falls Church, Virginia. For information, visit URL: http://www.iccsafe.org/.

32.2.9 Plumbing-Heating-Cooling Contractors-National Association. 2003. National Standard Plumbing Code with illustrations. Falls Church, Virginia. Available through URL: http://www.phccweb.org/.

32.2.10 International Association of Plumbing and Mechanical Officials. 2003. Uniform Plumbing Code. Uniform Plumbing Code-IAPMO/ANSI UPC 1-2003. Ontario, California. Available through URL: http://publications.iapmo.org/.

32.2.11 Centers for Disease Control and Prevention. 2000. Vessel Sanitation Program operations manual 2000. Atlanta: US Department of Health and Human Services. Available at URL: http://

www.cdc.gov/nceh/vsp/manual/VSP%20Operations%20Manual%202000.pdf.

32.2.12 Centers for Disease Control and Prevention. 1997 March. Final recommendations to minimize transmission of Legionnaires’ disease from whirlpool spas on cruise ships. Atlanta: US Department of Health and Human Services. (Available upon request from VSP).

32.2.13 World Health Organization. 2004. Guidelines for drinking water quality, third edition. http://www.who.int/water_sanitation_health/dwq/gdwq3/en/.

32.2.14 World Health Organization. 1967. Guide to ship sanitation. The third revision of the guide was expected to be published in 2005. The draft was posted at URL:  http://www.who.int/water_sanitation_health/hygiene/ships/shipsanitation/en/.

32.2.15 US Consumer Product Safety Commission. 2005. Guidelines for entrapment hazards: making pools and spas safer 2005. Publication No. 363-009801. Available at URL: http://www.cpsc.gov/cpscpub/pubs/363.pdf.

32.2.16 International Organization for Standardization. 2002. Ships and marine technology – identification colours for the content of piping systems, ISO 14726-2. Geneva, Switzerland. For information, see URL: http://www.iso.org/iso/en/ISOOnline.frontpage.

32.2.17 International Maritime Organization. 2004. International Convention for the Safety of Life at Sea (SOLAS), 1974, as amended; consolidated edition. Summarized at URL: http://www.imo.org/home.asp.

National Swimming Pool Foundation. 2007.  Certified Pool-Spa Operator Handbook, 2007 Edition.  For more information, visit URL: http://www.nspf.org.

ASHRAE Standard 12-2000, Minimizing the Risk of Legionellosis Associated with Building Water Systems.  http://www.ashrae.org/

Food Establish Plan Review Guideline.  2000.  Food and Drug Administration.  http://www.cfsan.fda.gov/~acrobat/prev.pdf

# 33.0 Appendices

## 33.1 Sample Letter of Request for Construction Inspection

(Company or Organization Letterhead)

Chief, Vessel Sanitation Program

National Center for Environmental Health

Centers for Disease Control and Prevention (CDC)

4770 Buford Highway, NE, MS F-59 23

Atlanta, GA 30341-3717 24

Facsimile (770) 488-4127

We request the presence of USPHS representatives to conduct a construction inspection on the cruise vessel (NAME). We tentatively expect to deliver the vessel on (DATE). We would like to schedule the inspection for (DATE) in (CITY,COUNTRY). We expect the inspection to take approximately (NUMBER OF DAYS). We will pay CDC in accordance with the inspection fees published in the Federal Register.

For inspections occurring outside of the United States, we will reimburse the Vessel Sanitation Program for all expenses in connection with the on-site Vessel Sanitation inspection and will make all necessary arrangements for lodging and transportation, which includes airfare and ground transportation in (CITY, STATE, COUNTRY). We will provide in-kind lodging, airfare, and local transportation expenses. We will reimburse the CDC for en-route per diem, meals and miscellaneous expenses, and ground transportation to and from the airport nearest the representative’s work site or residence. No honorarium will be given. No U.S. federal funds will be used. Send an invoice to:

Company(note: if a U.S. company, provide your federal tax identification number)

Attention:

Street Address

City, State, Country

Zip Code

Office Telephone Number

Office Fax Number

If you have any questions concerning this request, please contact:

(Signed) note: this letter must be signed and on company/organization letterhead

Name and Title

Hotel

Address

Telephone Number

## 33.2 VSP Contact Information

33.2.1 Atlanta Office

CDC/NCEH/Vessel Sanitation Program

Centers for Disease Control and Prevention

4770 Buford Highway, NE /MS F-59

Atlanta, GA 30341-3724

Phone: (770) 488-7070

Fax: (770) 488-4127

E-mail: vsp@cdc.gov

33.2.2 Fort Lauderdale Office

CDC/NCEH/Vessel Sanitation Program

Centers for Disease Control and Prevention

1850 Eller Drive, Suite 101

Ft Lauderdale, FL 33316-4201

Phone: 1-800-323-2132 or (954) 356-6650

Fax: (954) 356-6671

33.2.3 VSP Website.  For updates to these guidelines and information about the Vessel Sanitation Program, visit http://www.cdc.gov/nceh/vsp.

## 33.3 VSP Construction Checklists and Vessel Profile Sheets

33.3.1 VSP developed checklists from these guidelines, which may be helpful to shipyard and cruise industry personnel in achieving compliance with these guidelines. You may obtain copies of these checklists from the VSP Website.

# Index

air-break

def. of	6

in drain lines	25

air-gap

between potable and non-potable water systems	45

def. of	6

for backflow prevention	47

for high-saline discharge	45

for potable water

distribution system	44

in swimming pools	49

in whirlpool spa	53

for protecting potable water	47

American National Standards Institute	See ANSI

analyzer

for potable water

bunkering and production	45

distribution	45

for swimming pools	52

for whirlpool spas	55

ANSI	5

anti-entrapment drain covers in accordance with	49, 54

filter sizing in accordance with	52, 54

sealants in accordance with	17

sneeze guards in accordance with	32

vessel design and equipment in accordance with	2

atmospheric vacuum breaker

def. of	7

for backflow prevention	47

backflow

check, or non-return valve, def. of	7

def. of	7

preventer

atmospheric vacuum breaker, def. of	7

continuous pressure backflow preventer, def. of	7

def. of	7

for potable water

in swimming pools	49

in whirlpool spas	53

hose bib connection vacuum breaker, def. of	7

reduced pressure principle backflow prevention assembly, def. of	7

prevention

air-gap for	47

atmospheric vacuum breaker for	47

for a carbonation system	33

for RP assemblies	47

pressure vacuum breaker for	47

protecting connections	47

protection, for bucket filling stations	20

back-siphonage

def. of	8

for heat exchangers that cool potable water	48

protecting connections	47

backsplash

for bulkhead	30

bar

decks for	31

food display protection in	31

lighting in	36

pantry

decks for	31

food display protection in	31

sewage drain lines in	39

beverage dispensing equipment	Also see bulk milk dispenser

general facility requirements	16

multiflow	33

black water	Also see sewage

def. of	8

drain lines for	19, 39

blast chiller

def. of	8

equipment requirements	15

bucket filling station

backflow protection for	20

below handwashing sinks	19

deck drain for	20

in food preparation and storage areas	19

in galleys	19

buffet

counter

sewage drain lines in	39

line

decks for	31

food display protection in	31

bulk milk dispenser

drip trays in	16

bulkhead

backsplash for	30

coving for	18

in walk-in refridgerators and freezers, transportation corridors, and provision rooms	28

fasteners for	17

general facility requirements	17

in bars, and bar pantries	31

in buffet lines	31

in crew toilet rooms	21

in food preparation rooms	29

in galleys	29

in pantries	29

in provision rooms	28

in transportation corridors	28

in walk-in refrigerators andfreezers	28

in watier stations	31

cart

portable

equipment requirements	15

child activity facility	58

def. of	8

child care facility	58

def. of	8

child-size toilet

def. of	8

cleaning locker

general requirements	55

labels for	56

cleaning room

air exhaust system for	58

air supply system for	57

def. of	8

in galleys	56

connection, electrical	26

continuous pressure backflow preventer, def. of	7

coved

bulkhead	18, 37

in walk-in refridgerators and freezers, transportation corridors, and provision rooms	28

corners

for equipment surfaces	17

for garbage processing sorting tables	38

on hood systems	27

deck	37

in buffet lines, waiter stations, bars and bar pantries	31

in food and garbage lifts	37

in lockers:	55

deckhead	18

in walk-in refridgerators and freezers, transportation corridors, and provision rooms	28

def. of	9

dumbwaiters	37

tray rails	32

warewashing sinks	34

crew toilet room	See toilet room

cross-connection

def. of	9

deck

coved

in buffet lines, waiter stations, bars, and bar pantries	31

in galleys, food preparation rooms, and pantries	30

drain	See drain

general facility requirements	17

in bars and bar pantries	31

in buffet lines	31

in crew toilet rooms	21

in food preparation rooms	30

in pantries	30

in provision rooms	28

in transportation corridors	28

in waiter stations	31

in walk-in refrigerators and freezers	28

made of linoleum or vinyl tile	31

material for	18

material of	30

pantry

sewage drain lines in	39

sink

material of	18

deckhead

coving

in walk-in refridgerators and freezers, transportation corridors, and provision rooms	28

coving for	18

fasteners for	17

general facility requirements	17

in bars, and bar pantries	31

in buffet lines	31

in crew toilet rooms	21

in food preparation rooms	29

in galleys	29

in pantry	29

in provision room	28

in transportation corridor	28

in walk-in freezer	28

in walk-in refrigerator	28

in watier stations	31

door

general facility requirements	16, 17

in crew toilet rooms	21

sliding

cleaning access to	30

gaps around	29

drain

deck

and equipment design	16

and garbage holding facilities	38

and garbage processing areas	38

and trolley, waste container, and cleaning equipment wash rooms	37

def. of	10

general facility requirements	18

in food service areas	18

material of	18

under bucket filling stations	20

for food and garbage lifts	37

in potable water storage tanks	42

in swimming pools	49

in whirlpool spas	53

line	25

for deck and scupper	18

for gray and black water	19, 39

for sewage	19, 39

for warewashing machine	33

in provision rooms, walk-in refridgerators, and freezers, and transportation corridors	29

material for	25

drinking fountain	56

equipment requirements	15

drip pan

in transportation corridors	29

in walk-in refridgerators, and freezers	29

drip tray

def. of	10

for beverage dispensing equipment	16

for bulk milk dispensers	16

for condiment dispensing equipment	16

in ducts of warewashing machines	27

in provision rooms	29

duct

direct duct exhaust

clean out port	26

for warewashing machine	26

over warewashing equipment

hood system for	26

electronic data loggers	46

evaporator

cold room evaporator

in provision rooms	29

in transportation corridors	29

in walk-in freezers	29

in walk-in refridgerators	29

for potable water	44

high saline discharge	44

fasteners	23

for bulkheads and deckheads	17, 29

for food contact surface	23

for non-food contact surfaces	24

filling hose	See hoses

fire shutters	29

food

display protection

in buffet lines, waiter stations, bars and bar pantries	31

food contact surface

def. of	10

fasteners for	23

general facility requirements	17

graphic	10

requirements for fasteners, securing, and sealing equipment on	23

food display area

def. of	10

food display cases

tight-fitting doors for	16

food handling area

def. of	11

handwashing sinks in	19

location of handwashing stations in	20

food lift	37

lighting for	35

food preparation

area

air exhaust system for	58

air supply in	57

bucket filling station in	19

def. of	11

drinking fountain in	56

equipment for	16

lighting in	35

location of handwashing stations in	20

storage for	16

room

bulkhead in	29

deck in	30

deckhead in	29

food service area	31

bulkhead in	31

deck drainage in	18

deckhead in	31

decks in	31

def. of	11

handwashing sinks in	19

food storage area

bucket filling station in	19

def. of	11

food transport area

def. of	11

food waste system

def. of	11

splash panels around	34

table

material of	34

wiring in	34

fountains, decorative	59

freezer, walk-in

bulkhead in	28

deckhead in	28

room

deck in	28

galley

bucket filling station in	19

bulkheads in	29

deckheads in	29

decks in	30

garbage lift	37

lighting for	35

gasket	24

material for	24

gray water

def. of	11

drain lines for	19, 39

gutterway	See scupper

halogenation	45

handles	24

in food service areas	20

in handwashing stations	20

handwashing

sign	See sign

sink	See sink

station

handles for	20

hygiene requirements	19

in child care facility	59

in garbage holding facility	38

in garbage processing area	38

in housekeeping	59

in trolley, waste container, and cleaning equipment wash rooms	37

potable water for	19

heat exchanger

for cooling potable water	48

heater coil

for freezer drip pans	29

hinges	24

hood system	26

hose

filling

for potable water	40

storage for	40

rinse

for warewashing	33

hose bib connection vacuum breaker

def. of	7

IEC	2

IMO	2

inspection

construction inspection

sample letter of request for	62

final construction inspection	1

final construction inspection	5

on-site construction inspection	4, 5

International Convention for the Prevention of Pollution from Ships	See MARPOL

International Electrical Code	See IEC

International Marine Organization	See IMO

International Plumbing Code	See IPC

International Standards Organization	See ISO

IPC	2

ISO	2

filling lines in accordance with	39

potable water piping in accordance with	43

keel laying

def. of	11

latches	24

lift

food	37

lighting for	35

garbage	37

lighting for	35

lighting

for garbage and food lifts	35

in bars	36

in garbage processing area	38

infrared	36

shatter-resistant bulbs	36

aboves bars	36

shatter-resistant fixtures for	36

shielded bulbs	36

shielded fixtures for	36

locker

cleaning

equipment requirements	15

lowerators, dishware

equipment requirements	15

MARPOL	2

mounting

equipment	21

non-portable equipment	21

potable water hoses	40

National Sanitation Foundation International	See NSF

non-food contact surface

def. of	11

equipment requirements	17

fasteners for	24

securing and sealing requirements	24

non-portable equipment

placement	21

non-potable water

def. of	11

NSF	5

sealants in accordance with	17

sneeze guards in accordance with	32

pallets, portable

equipment requirements	15

pantry

bulkheads in	29

deck in	30

deckheads in	29

piping

for potable water	43

for swimming pools	52

for whirlpool spas	55

pipeline	26

sealing area of	26

plan review

procedures for requesting	3

report	4

request a	1

potable water

and reverse osmosis plants	44

bunkering and production	45

analyzer for	45

def. of	11

disinfection of the system of	46

distribution

analyzer for	45

system for	43, 44

drains in storage tank	42

electronic data loggers for	46

evaporator for	44

filling hose storage for	40

filling hoses for	40

filters	56

for decorative fountains	59

for handwashing stations	19

halogenation of	45

heat exchangers for	48

in bunker station	39, 40

piping for	43

pressure tanks for	44

production and capacity for	40

pumps for	44

storage of	40

storage tank	41

access holes for	42

vents for	42

water level	42

system	39

tank

def. of	11

pressure tank

for potable water	44

provision room	28

and cold room evaporators	29

bulkhead in	28

deckheads in	28

decks in	28

drain lines in	29

lighting in	36

pumps

for potable water	44

ramps

general facility requirements	19

reduced pressure principle backflow prevention assembly	See RP assembly

refrigerator

walk-in	28

bulkheads and deckheads in	28

cold room evaporators, drip pans, and drain lines in	29

decks in	28

renovation, major

application of guidelines	2

rinse hose	See hose

RP assembly

between potable and non-potable water systems	45

def. of	7

for high-saline discharge	45

for potable water hoses	40

scupper

and equipment design	16

def. of	12

general facility requirements	18

material of	18

seal

electrical lines	26

piping	26

sealant

def. of	12

for bulkheads and deckheads

in galleys, food preparation rooms, and pantries	29

for bulkheads, deckheads, and decks	17

on food contact surfaces surfaces	17

use of	24

in accordance with ANSI or NSF	17

sealed def. of	12

sealed seam def. of	12

sealing equipment

requirements for	23

technical spaces

area around	26

sewage

def. of	12

in drain lines	19

system	39

drain lines for	39

shelves

equipment requirements	15

in warewashing areas	35

sign, handwashing

general requirements for	20

in child care and child activity facilities	59

in child care facilities	58

in crew toilet rooms	21

sink

deck sink

and equipment design	16

def. of	10

general facility requirements	18

food preparation culinary sink

drain line requirements for	25

equipment requirements	15

four-compartment sink

general facility requirements	16

in main pot washing area	16

handwashing sink

bucket filling station at	19

bucket filling station for	20

in food service area	19

potwashing sink	34

three-compartment sink	26

general facility requirements	16

hood system for	26

in food preparation areas	16

in main pot washing area	15

utility sink

def. of	14

general facility requirements	16

warewashing sink	34

warewashing sink, coved	34

sneeze guard

criteria for	31

SOLAS	2

garbage chutes in accordance with	37

hood or canopy system in accordance with	27

spa pool

def. of	13

splash contact surface

def. of	13

direct splash contact surface, def. of	13

general facility requirements	17

graphic	10

indirect splash contact surface, def. of	13

securing for	23

splash panel

for food waste system	34

for handwashing stations	19

storage

cabinet

equipment requirements	15

in galleys	15

in food preparation areas	16

knives

equipment requirements	15

of potable water	40

filling hose	40

rack

equipment requirements	15

shelves

equipment requirements	15

in warewashing area	35

tank

access holes	42

drains	42

potable water	41

potable water level	42

vents	42

surfaces

equipment

general facility requirements	17

exposed non-food contact surfaces	17

food contact	17

splash contact	17

swimming pool	49

analyzer for	52

indoor

air exhaust system for	57

piping for	52

table

food waste system table

material of	34

landing table

in warewashing area	33

material of	34

portable table

equipment requirements	15

technical spaces	31

for electrical connections, pipelines and other attached equipment	26

material for	30

sealing area around	26

thermometer probe	29

three-compartment sink	See sink

toilet room

air exhaust systems for	58

air supply in	57

crew

def. of	9

hygiene requirements	21

in child care or activity facility	58

lighting in	35

public	59

transportation corridor	28

bulkhead in	28

deckhead in	28

decks in	28

def. of	13

tray rail

and deck installation	31

surfaces

in food service areas	32

trolley, waste container, and cleaning equipment wash rooms

room,handwashing station in	37

utility line

location of in food service areas	30

utility sink	See sink

ventilation

air supply system for	57

exhaust in toilet room	21

exhaust system	57

in the canopy system	27

in the hood system	27

vents

in potable water storage tanks	42

waiter station

decks for	31

food display protection in	31

handwashing stations for	20

warewashing

area, shelves for	35

handwashing station location	20

landing table for	33

machine

alarm device for	34

condensate drip trays for	27

data plate for	34

drain line requirements for	25

drain lines for	33

gutters for	33

hood exhaust trunk for	26

hood system for	26

rinse hoses for	33

sink	See sink

ventilation for	35

exhaust hood design	26

warewashing machine

in food preparation areas	16

water

technical	11, 13

whirlpool spa

air-gap for potable water	53

analyzer for	55

backflow preventer in potable water	53

def. of	14

piping for	55