July 22, 1994

Contract #TW0592

SPECIAL SPECIFICATION

SECTION 10282

AIR SHOWERS

Page

PART 1 - GENERAL

1.01 Description.	2

1.02 Related Work.	2

1.03 References.	2

1.04 Submittals.	3

1.05 Delivery, Storage, and Handling.	4

PART 2 - PRODUCTS

2.01 Acceptable Manufacturers.	5

2.02 Materials.	5

2.03 Equipment.	5

2.04 Fabrication..	5

PART 3 - EXECUTION

3.01 Installation/Application/Erection.	10

3.02 Commissioning.	10

3.03 Demonstration..	10

SPECIAL SPECIFICATION

SECTION 10282

AIR SHOWERS

PART 1 - GENERAL

1.01	DESCRIPTION

A.  		This Section specifies the fabrication, installation, and start-up of air showers.

1.02	RELATED WORK

A.  	Section 01300

B.  	Section 15023

C.  	Section 15995

1.03	REFERENCES

A.  	Comply with the current editions of all the applicable codes and standards of technical societies and organizations in Section 15023 and the following:

1.  	Air Movement and Control Association (AMCA), AMCA 210  Laboratory Methods of Testing Fans for Rating Purposes

2.  	AMCA 300  Test Code for Sound Rating Air Moving Devices

3.  	AMCA 401  Fans, Standard Classifications for Spark Resistant Construction

4.  	American Society of Mechanical Engineers (ASME), ASME PTC11  Test Code for Fans

5.  	American Society for Testing and Materials (ASTM), ASTM A386  Zinc Coating (Hot-Dip) on Assembled Steel Products

6.  	ASTM A525  Steel Sheet, Zinc Coated (Galvanized) by the Hot-Dip Process

7.  	ASTM B209  Aluminum-Alloy Sheet and Plate

8.  	ASTM B221  Aluminum-Alloy Extruded Bars, Rods, Wire, Shapes, and tubes

9.  	National Electrical Manufacturer's Association (NEMA), NEMA MG1  Motors and Generators, MG-112.53b

10. 	Institute of Electrical and Electronics Engineers (IEEE), IEEE 112, Method B

11. 	Underwriter's Laboratories (UL), UL 507  Safety for Electric Fans

12. 	Occupational Safety and Health Administration

1.04	SUBMITTALS

A.  	Make all submittals according to this Section, Section 15010, and Section 01300.

B.  	Submit manufacturer's literature and certified prints to include the following:

1.  	Performance data on manufacturer's selected fans.

2.  	Fan sound power level (dB re 10-12 watts) for each octave band.

3.  	Complete description of construction materials of units and accessories, including:

a. 		Fan.

b. 		Drive.

c. 		Dampers.

d. 		Isolators.

e. 		Insulation.

f. 		Special Coatings.

g. 		Companion Angles.

h. 		Lights.

i. 		Filters.

j. 		Nozzles.

4.  	Physical and electrical characteristics of motors.

5.  	Dimensions of units and accessories, including locations and sizes of:

a. 	Electrical connections.

b. 	Support points.

c. 	Access areas required.

6.  	Shipping and operating weights of units and accessories.

C.  	Submit shop drawings and include the following on the shop drawings:

1.  	Installation details of units and all accessories.

D.  	Submit recommended spare parts list; include description, quantity and price for each part.

E.  	Submit detailed installation, operation and maintenance instructions.

1.05	DELIVERY, STORAGE, AND HANDLING

A.  	Deliver products to the project properly identified with names, model numbers, types, grades, compliance labels, and other information needed for identification.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

A.  	Liberty Industries, Inc.

B.  	Air Showers & Pass-Thrus.

C.  	Scientific Air Systems.

D.  	Comp-Aire System, Inc.

2.02	MATERIALS

A.  	Aluminum Sheet and Plate:  3003-H14 alloy, conforming to ASTM B209.

B.  	Aluminum Extrusions:  6061-T6 or 6063-T52 alloy, conforming to ASTM B221.

2.03	EQUIPMENT

A.  	Provide factory-built air shower assembly with accessories as indicated in this Section.

B.  	Meet the performance requirements indicated in this Section.  Note that design data refers to "Standard Air" (air with density of 0.075 lbs. per cubic foot at sea level, 29.92-inches (in.) mercury barometric pressure and 70 degrees Fahrenheit).

2.04	FABRICATION

A.  	Air Chamber

1.  	Use 3/4-in., flakeboard construction thick covered with white plastic laminate both inside and out.

a. 	Trim:  Anodized aluminum

b. 	Grilles:  Structural aluminum

c. 		Doors:  Anodized aluminum frame, incorporating 1/4-in. wire glass

d. 			Top over entire unit:  Same construction as air chamber

e. 		Meet NFPA and underwriter's requirements of non-combustible construction to avoid the requirement for a sprinkler system.

f. 		Floor for Floor Return Units:  Structural aluminum grating

B.  	Blower Assembly

1.  	Provide high pressure radial blade fan with electrical panel box located on mechanical section.

2.  	Provide a blower that forces air through adjustable plastic or stainless steel nozzles at 7500 feet-per-minute.  Locate the nozzles on each side and on top of each of the units.  Provide a sufficient quantity of nozzles for each unit to ensure a minimum of 700 air-changes-per-hour.

3.  	Provide motor with these features: high-efficiency, single-speed, direct-drive, open-drip-proof, permanently-lubricated, and sealed-ball-bearings.

4.  	Provide nominal efficiency per NEMA MG 1 Table 12-6C, when tested in accordance with test method IEEE 112 Method B for all high efficiency motors.

5.  	Provide vibration isolation by doing the following:

a. 		Support each fan/motor assembly on resilient isolators that deflect statically at least 0.2 in. under the load.

b. 		Ensure that the structure to which the isolators are attached deflects (at the attachment point) no more than 0.02 in. due to the weight of the fan/motor assembly.

C.  	Filtration

1.  	Provide access to each of the two filter systems.

2.  	Provide pre-filters which are 65-percent-efficient, ASHRAE filters and include magnehelic gauge to measure filter air flow resistance.

3.  	Provide filters which are 99.99-percent-efficient in the removal of 0.3 micron particles, [polystyrene latex (PSL) spheres method] and include a magnehelic gauge to measure filter air flow resistance.

D.  	Lighting

1.  	Furnish fluorescent-type lighting which provides a minimum of 100-footcandle, average illumination.  Recess the light fixtures in the ceiling of the air showers units.  Use 277-volt (V), 1-phase (ph.), 60-hertz (Hz) lighting fixtures.  Provide each light fixture with Magnetek Electronic Ballasts and 4-foot (ft.), 32W, T-8 lamps.  Provide at least one T-8 lamp in each air shower with a separate Magnetek Electronic Ballast.  Connect this separate ballast to operate only this single T-8 lamp, and provide power from a separate emergency lighting circuit as shown on the Drawings.  Provide each air shower with two low-wattage, light switches.  Do not provide the switches and wire which are to be provided by others.

2.  	Provide one single-gang box for each switch and provide a 3/4-in., electrical, metallic tubing (emt) from each box.  Provide a nylon pull string in the emt conduit for later wiring by others.  Provide each unit with a 20-ampere (A) circuit breaker in the equipment cabinet part of the air shower for use as a disconnecting means.  Provide an access path from the circuit breaker to the bottom of the unit for use by the Contractor in providing electrical power to the circuit breaker.  Provide a hole in the bottom of the unit for conduit to enter the unit from below.  Provide a hinged access door on the outside of the unit away from the room wall to provide access to the circuit breaker.  Mark this door as the access to the lighting and door circuit breaker.  Wire the emergency light circuit directly to the light fixture; do not provide provisions for disconnection within the equipment cabinet.

E.  	Power Requirements

1.  	Provide 208-V, 3-ph., 60-Hz power which can be shut-down from either the inside or outside.  Provide an alarm to indicate when the power is shut-down.  Provide each air shower with integral starters and one power connection with a 30-A shunt trip circuit breaker in the equipment cabinet part of the air shower for use as a means of disconnect.  Provide an access path from the circuit breaker to the bottom of the unit for use by the Contractor in providing electrical power to the circuit breaker.  Provide a hole in the bottom of the unit for conduit to enter the unit from below.  Provide a hinged access door on the outside of the unit away from the room wall to provide access to the circuit breaker.  Mark this door as the access to the circuit breaker.

2.  	Provide emergency push buttons on both the inside and the outside of both entrances of each unit to trip the shunt trip breaker in case of emergency.

F.  	Operating Timer:  0 - 3 minutes adjustable timer.

G.  	Provide a high static pressure and power loss alarm system with external light emitting diode.

H.  	See Drawings 104490-A8 (for Types A and B) and 104490-A10 (for Type C) for information on the three types of air showers.  Provide air return via the floor grating.  Air shower sizes are indicated below.

Type A Unit Dimensions:

Outside:		5-ft.-8-in. wide by 6-ft.-2-in. long by 9 ft. from the finished raised floor to the top of the outside envelope by 2 ft. from the finished raised floor to the concrete subfloor.

Inside: 		4-ft.-8-in. wide by 5-ft.-2-in. long

Type B Unit Dimensions:

Outside:		6-ft. wide by 8-ft. long by 9 ft. from the finished raised floor to the top of the outside envelope by 2 ft. from the finished raised floor to the concrete subfloor.

Inside: 		5-ft. wide by 7-ft. long.

Type C Unit Dimensions:

Outside:		5-ft.-10-in. wide by 7-ft.-10-in. long by 9 ft. from the finished raised floor to the top of the outside envelope by 2 ft. from the finished raised floor to the concrete subfloor.

Inside: 		4-ft.-10-in. wide by 6-ft.-10-in. long.

I.  	Design the air showers for two or three-way personnel traffic.  See Reference Drawings 104490-A8 and 104490-A10 for more information.  Provide automatic control for the air showers.  Electrically interlock both doors and start the unit after entering the air shower.  Operate the units on an adjustable timer for 0-3 minutes.  Air shower personnel traffic is indicated below.

Type A Air shower operational for personnel traffic flow to and from Deposition Area.

Type B Air shower operational for personnel traffic flow to and from Final Assembly (inner tritium).

Type C Air shower operational for personnel traffic flow to and from Particulate Contaminant Control and Final Assembly (non-tritium).

J.  	Provide the units with interior access doors to each section for fan and filter maintenance.   See architectural drawings for unit orientation and wall location.

K.  	Provide support legs and anchorage details for the unit.  Design the support legs and anchors for lateral and overturning seismic loads in accordance with section 2336 of the Uniform Building Code using Z = 0.22, I = 1.25, and Cp = 1.5.  The units are supported on an elevated concrete slab on 1-1/2-inch metal deck for a total thickness of 5 inches.  Use adhesive or undercut anchors for anchorage to concrete.  Do not use expansion anchors.

PART 3 - EXECUTION

3.01	INSTALLATION/APPLICATION/ERECTION

A.  	Install the units according to this Section, all codes and standards, and manufacturer's recommendations.  Locate the air showers at locations shown on the Drawings.

B.  	Provide a manufacturer's qualified representative to oversee the installation, start-up, and training of Sandia personnel for a minimum period of 2 working-days.

C.  	Provide Zerk fittings at all lubrication points with extended leads to the inside of the access doors for easy accessibility.

D.  	Lubricate fan and motor bearings prior to start-up.

E.  	Identify units with metal tags.

3.02	COMMISSIONING

A.  	Provide labor, material, equipment, etc., required to facilitate the commissioning process.

B.  	Perform form tests and verification procedures required by the commissioning process when requested by the Commissioning Authority and directed by the General Contractor.  See Section 15995.

3.03	DEMONSTRATION

A.  	Provide the services of a factory-authorized service representative to start-up equipment, demonstrate operation, and train personnel.

B.  	See Section 15995.

END OF SECTION