| Last updated April 2003 | Surge Protection Anthology Part 2 – Annex A – Citations Development of Standards – Reality Checks | Surges Happen! |
| --- | --- | --- |

ANDERSON, L.M. and BOWES, K.B., “The Effects of Power-line Disturbances on Consumer Electronic Equipment,” IEEE Transactions PWRD-5, No.2, April 1990.

- Experimental study of the immunity of typical electronic equipment to sags and surges.

- Surges applied were not the ANSI C62.41, but a 100 or 300 s pulse, presumably open-circuit voltage.

- Surges of 1000 V (open-circuit voltage of generator) did not cause any failure of PCs.

BACHL, H., MARTZLOFF, F.D. and NASTASI, D., “Using Incandescent Lamp Failure Levels for Assessment of the Surge Environment,” Proceedings, 12th International Zürich Symposium on Electromagnetic Compatibility, 1997.

Accessible as  Lamp failure

- Shows failure mechanisms and levels by electrical measurements and with high-speed video recording.

- 120-V lamps can fail in the range of 800 V to 1200 V, depending on waveshape and phase angle.

- Makes the point that surges are unlikely to occur frequently at levels above the failure level of lamps.

- 5 references

BARTKOWIAK, M., COMBER, M.G., and MAHAN, G.D., “Failure Modes and Energy Absorption Capability of ZnO Varistors,” IEEE Transactions PWRD-14, January 1999.

- Simulation of varistor behavior under current pulses of various magnitudes and duration.

- Comparison with experimental results.

- Demonstrates that energy-handling capability is not a constant, but depends on intensity and duration.

- 14 references, 1 discussion

FENIMORE, C. and MARTZLOFF, F.D., “Incompatibility Between the 100/1300 Surge Test and Varistor Failure Rates.” Proceedings, 9th International Zürich Symposium on Electromagnetic Compatibility, 1991

Accessible as  Incompatibility

- Numerical computations of the energy deposition associated with a proposed IEC standard indicate that massive failure of ubiquitous metal-oxide varistors should occur – but they do not.

- The proposed test was eventually removed from the menu of IEC EMC test methods.

- 10 references

FENIMORE, C. and MARTZLOFF, F.D., “Validating Surge Test Standards by Field Experience: High-Energy Tests and Varistor Performance,” IEEE Transactions IA-28 No.6, December 1992. (First publication in Conference Record, IEEE/IAS Annual Meeting, Oct. 1990).

Accessible as  Validating

- Computer modeling of the resulting current and energy deposition into typical varistors subjected to the C62.41 10/1000 (s waveform and proposed IEC 100/1300 s waveform.

- Yields a prediction of failure for the small varistors and survival for the larger varistors.

- Because small varistors do not fail in the field at the rate that is predicted by the model of the IEC waveform, the conclusion is that stresses associated with this proposed waveform make it unrealistic.

- 15 references

FISHER, F.A. and MARTZLOFF, F.D., “Transient Control Levels: A Proposal for Insulation Coordination in Low-Voltage Systems,” IEEE Transactions PAS-95, No. 1, Jan/Feb 1976.

Accessible as  TCL Proposal

- Proposes an approach parallel to that of the BIL concept for high-voltage system.

- First published version of a test circuit for 100 kHz Ring Wave.

- 12 references, 3 discussions

GOEDDE, G.L., KOJOVIC, Lj.A., and WOODWORTH, J.J., “Surge Arrester Characteristics that Provide Reliable Overvoltage Protection in Distribution and Low-Voltage Systems,” Proceedings, IEEE-PSE Summer Meeting, Seattle WA, July 2000.

- Describes field experience of arresters designed in accordance with IEEE Std C62.11-1999.

- Concludes that tests with a 10/350 s waveform are not necessary.

- 11 references

KEY, T.S., MARTZLOFF, F.D., WITT, R., MAY, J., and BLACK, S., “Developing a Consumer-Oriented Guide on Surge Protection,” Proceedings, PQA’97 North America, 1997.

Accessible as  Develop guideline

- Progress report on the development of a tutorial on surge protection.

- Presents the need for “intersystem bonding” at the entrance of power and communications utilities.

- Brief discussion of the need for surge reference equalizers.

- 6 references

MACIELA, F., “Energetic Design and EDF Distribution Network Experience of MV Metal Oxide Surge Arresters,” CIGRE SC33.95  (1995 Colloquium).

- Field experience of EDF on 700 000 arresters.

- Failure rate lower (1/4) than calculated in Rousseau, 1989 (CIRED).

MANSOOR, A., MARTZLOFF, F.D., and NASTASI, D., “Applying Reality Checks to Standards on the Surge Environment,” Proceedings, 23rd International Conference on Lightning Protection, Florence, 1996.

Accessible as  Reality Checks

- Shrinking surge recording occurrences explained by proliferation of SPDs.

- Applying equipment failure rates to assess the surge environment.

- Limits to pushing surges into branch circuits.

- 19 references

MANSOOR, A. and MARTZLOFF, F.D., “Driving High Surge Currents into Long Cables: More Begets Less,” IEEE Transactions PWRD-12, No.3, July 1997.

Accessible as  More begets Less

- Measurements and modeling, validating each other, show the physical impossibility for large surge currents to propagate very far into the branch circuits of a building, because flashover will occur at the service entrance.

- Demonstrates the importance of considering the maximum rate of rise (early in the surge) rather than an average derived from the peak value and overall rise time.

- 13 references

MANSOOR, A. and MARTZLOFF, F.D., “The Effect of Neutral Earthing Practices on Lightning Current Dispersion in a Low-Voltage Installation,” IEEE Transactions PWRD-13, July 1998.

Accessible as  Neutral earthing

- Compares the TN and TT for dispersion of lightning current in several scenarios.

- Shows the need for careful review of grounding practices in effect at service entrances.

- Questions the applicability of high amplitude, long duration requirement for service entrance SPDs.

- 20 references

MANSOOR, A. and MARTZLOFF, F.D., "The Dilemma of Surge Protection vs. Overvoltage Scenarios: Implications for Low-Voltage Surge-Protective Devices," Proceedings, 8th International Conference on Harmonics and Power Quality, Oct 14-16, 1998, Athens, Greece.

Accessible as  Dilemma

- Three examples of temporary overvoltage conditions that can produce failure of SPDs.

- The significance of available fault current and the need for more explicit standards.

- 17 references

MANSOOR, A., MARTZLOFF, F.D., and PHIPPS, K., “The Fallacy of Monitoring Surge Voltages: SPDs and PCs Galore!”  Proceedings, EPRI PQA’99 Conference, May 1999.

Accessible as  Galore

- Experimental measurements of effective mitigation by multiple SPDs.

- Numerical simulation of the effect of proliferating SPDs and PCs.

- Calls for an industry-wide reassessment of surge monitoring parameters.

- 20 references

MARTZLOFF, F.D. and FISHER, F.A., “Transient Control Level Philosophy and Implementation,” Part 1: The Reasoning Behind the Philosophy,” Proceedings, 2nd  Symposium on Electromagnetic Compatibility, Montreux, 1977.

Accessible as  TCL Philosophy

- Presents the concept of testing low-voltage equipment patterned on the high-voltage BIL concept.

- Techniques and equipment for making TCL tests.

- 10 references

MARTZLOFF, F.D., “Varistor Versus Environment: Winning the Rematch,”  IEEE Transactions  PWRD-1, No. 2, April 1986.

Accessible as  Winning Rematch

- Staged test of capacitor switching on remote MV side produces ring waves on low-voltage load.

- Coordination between 3 kV and 480 V varistor-based SPDs.

- 5 references, 1 discussion

MARTZLOFF, F.D., “Testing Varistors Against the VDE 0160 Standard,” Proceedings, Open Forum on Surge Protection Application, NISTIR-4654, August 1991.

Accessible as  MOV - VDE

- Reports tests performed with a prototype 100/1300 surge generator, resulting in failure of the ubiquitous

- 20-mm diameter varistors, hence demonstrating that the proposed standard is unrealistic.

- 9 references

MARTZLOFF,  F.D. AND MENDES,  A., “Standards: Transnational Aspects,”  Proceedings, EPRI PQA’91, Gif-sur-Yvette, France , 1991.

Accessible as  Transnational

- Describes the various types of standards: national, regional, transnational, and international.

- Tutorial review of the process of development of standards in the power quality area , presented at an international conference.

- 4 references .

MARTZLOFF, F.D. and PELLEGRINI, G.,  “Real, Realistic Ring Waves for Surge Testing,” Proceedings, 9th International Zürich Symposium on Electromagnetic Compatibility, 1991.

Accessible as  Real Waves

- Reports measurements on the propagation of oscillatory waves in typical low-voltage circuits, as opposed to the unidirectional waves initially defines for high-voltage power systems.

- Shows how impinging unidirectional surges can produce oscillatory waves responses.

- 17 references

MARTZLOFF, F. D.,  “On the Dispersion of Lightning Current after a Direct Flash to a Building,” Proceedings, 25th International Conference on Lightning Protection, Rhodes, 2000.

Accessible as  Dispersion

- Computer modeling of the current dispersion among available paths to ground.

- Comparison between proposed SPD ratings based on computer modeling and field experience.

- 9 references

MARTZLOFF, F.D., “The Trilogy update of IEEE C62.41,”  Proceedings, 25th International Conference on Lightning Protection, Rhodes, 2000.

Accessible as  Trilogy Update

- Progress report on the development of the SPD Trilogy to a European forum

- Comparison between proposed SPD ratings based on computer modeling and field experience.

- 9 references

MARTZLOFF, F.D., “New IEEE standards foster next-generation system compatibility,”  EPRI Signature Newsletter, Winter 2002.

#### Accessible as  New IEEE Stds

- Brief progress report on the development of the SPD Trilogy in an EPRI newsletter

- No references

MEISSEN, W., “Überspannungen in Niederspannungsnetzen” [Overvoltages in low-voltage networks], ETZ Bd. 104, 1983.

- The seminal paper proposing a long waveform with extremely high energy-deposition capability, leading to the development of German Standard DIN 0160.

RICHMAN, P., “New Fast-Transient Test Standards Inadvertently Permit Overstressing by as much as 600 Percent,” EMC Test and Design, Vol.2, No.5, Sept/Oct 1991.

- Points out ambiguities in the test procedures described in IEC EFT standard.

ROUSSEAU, A., “Requirements for Rating of MV Zinc Oxide Surge Arresters on EDF Distribution Networks,” CIRED 1989.

- Design of ZnO MV arresters based on statistics of lightning current magnitude and tail.

- Sharing of current between many arresters as well as the number of lightning strike per year and per km of overhead line are used in calculations.

- Design based on an energy requirement converted in lab into a 4/10 standard waveshape.

- 13 references

SMITH, S.B. and STANDLER, R.B., “The Effects of Surges on Electronic Appliances,” IEEE Transactions PWRD-7, No.3, July 1992.

- Clocks, TV receivers, and switching power supplies were subjected to surges from 0.5 kV to 6 kV.

- The switching power supplies and television receivers were damaged with surges from 4 kV to 6 kV.

- Three of five models of digital clocks were upset with surges from 1.6 kV to 6 kV.

- The conventional wisdom that electronic appliances are easily damaged by surges with a peak voltage of a few kilovolts greatly exaggerates the effect of surges on modern consumer appliances.

- 15 references

STANDLER, R.B., “Development of a Performance Standard for Surge Arresters and Suppressors,” Proceedings, IEEE 1991 International Symposium on Electromagnetic Compatibility.

- Some critical issues in the development of a performance standard for surge arresters and suppressors for use on low-voltage mains are discussed.

- Describes a series of electrical tests to determine the safety and adequacy of surge protective devices.

- 4 references

STANDLER, R.B., “Calculation of Energy in Transient Overvoltages,”  Proceedings, IEEE EMC Symposium, 1989.

- Shows that using the integral of V2/50 dt  to compute energy in a surge is invalid.

- A quantitative error analysis is presented that uses an artificial AC line network to simulate a long branch circuit and to give the impedance of the AC line as a function of frequency.

- A method for measuring energy dissipated in a varistor is advocated for use in future experiments.

- 18 references

STANDLER, R.B., “Standards for Surge-protective Devices for Connection to the Low-voltage Ac Supply Mains in the USA,”  Proceedings, Lightning Protection 92 - Buildings, Structures and Electronic Equipment Conference and Exhibition, 1992.

- Review of major standards in the USA for low-voltage AC power surge-protective devices prepared for a European-based forum.

- Since it is clear that international standards are greatly preferable for both manufacturers and users, the US position [in 1992] on the IEC SC37A drafts is also briefly reviewed.

- 9 references

VANCE, E.F., NANEVICZ, J.E., and GRAF, W., “Unification of Electromagnetic Specifications and Standards,” Defense Nuclear Agency Report DNA 5433F-1, Washington DC, 1980.

- Describes the need for dual capability of a test generator to adapt inherently to the impedance of the EUT, even during the surge event.

François Martzloff

END OF FILE “Citations Part 2”

April 2003