VA Medical Center	Medical Center Memorandum ( )

(LOCATION)	(DATE)

Waste Anesthetic Gases and Vapors Hazard Control Program

1.	Purpose.  The purpose of this policy is to briefly outline the responsibilities for the various program elements of the medical center’s Waste Anesthetic Gas and Vapors Hazard Control Program.

2.	Background.  Responding to the scientific literature indicating there may be adverse health effects associated with exposure to waste anesthetic gases and vapors, the medical center has established a program to meet the recommendations of Occupational Health Advisory Agencies (NIOSH and ASA) and to comply with JCAHO accreditation criteria.

3.	Responsibilities.

a.	Engineering Service will be responsible for preventive maintenance of affected HVAC systems, scavenging systems, and anesthesia units.

b.	Safety Specialist/Industrial Hygienist will coordinate all industrial hygiene monitoring and leak testing, review the training programs conducted by the other services, keep records on air sampling, notify exposed employees of the results of air sampling, and see that exposure records are forwarded to Employee Health to be placed in medical records.

c.	Surgical, Nursing, Dental, and Research Services will be responsible for annual training and encouraging their staff in the use of work practices designed to reduce ambient waste anesthetic gases during the administration of anesthesia.  They will keep records on the training dates, topics, and attendees.  These individual services will be responsible for seeing that their exposed employees are identified for baseline and annual medical surveillance through the Employee Health Unit (NIOSH, ASA).

4.	Exposure Limits.  Exposure limits have been recommended by the American Conference of Governmental Industrial Hygienists (ACGIH) and NIOSH.  OSHA does not currently have Permissible Exposure Limits (PEL) for anesthetic gases (other than chloroform and trichloroethylene, which are not addressed here because it is believed they are not used as anesthetics in VAMCs).  See the attachment to this memorandum for a summary of exposure limits.  See paragraph 4.g. for recommendations for VAMC exposure limits.

a.	All of the Agencies involved, ASA, NIOSH and ACGIH, admit that there are not sufficient data to establish safe occupational exposure levels for anesthetic gases, and that the recommended limits are merely based on lowering the exposure to levels that are considered achievable with current technology.  All three groups stated that in Dental Operatories it may not be possible to reduce exposure to nitrous oxide below 50 parts nitrous oxide per million parts air (ppm).

b.	NIOSH recommends an exposure limit of 25 ppm for nitrous oxide, as a Time-Weighted Average (TWA) over the period when anesthesia is being administered to the patient which should be the period of highest exposure.  This is calculated differently from an 8-hour TWA.  An 8-hour TWA takes into the calculation the exposure estimate of the entire shift, several hours of which might be spent outside of the operating room.  NIOSH’s exposure limits are expressed as TWA over the period of anesthesia administration.  This time period will vary depending on the procedure from a few minutes to several hours.

c.	The NIOSH recommendation for halogenated agents is 2 ppm as sampled during the administration period not to exceed one hour.  NIOSH notes that when administered with nitrous oxide, halogenated agents will be below 0.5 ppm when the nitrous oxide is below 25 ppm.

d.	On the surface, it would appear that these exposure limits do not cover employees working in the recovery room.  An assumption in the NIOSH limits is that there is good exposure control in every phase of the anesthesia process, not just during administration.  Given that scenario, the period of highest exposure would be during gas and vapor administration.  Therefore, it is expected that exposures during periods other than administration of the gas, such as afterward in the operating and recovery rooms, dental operatories, and research rooms, should be much lower than the limits recommended for anesthesia administration.  This will be achieved only when good equipment control, ventilation, and work practices are utilized.  A method for confirming good control is to conduct air sampling during these nonadministration periods.  As a rule of thumb, exposure levels in these circumstances should be below 25 ppm nitrous oxide.

e.	These exposure limits do not address exposure of operating room personnel during the use of unventilated cryosurgical units which have been known to leak large amounts of nitrous oxide.

f.	In 1987 ACGIH proposed a Threshold Limit Value - Time-Weighted Average (TLV-TWA) for nitrous oxide of 50 ppm.  In 1980 ACGIH proposed a TLV-TWA for enflurane of 75 ppm.  The TLV-TWA proposed in 1980 for halothane is 50 ppm.  All three proposed TLV-TWA levels are the current values adopted by ACGIH as of 1993-1994.  All TLV-TWA are calculated for an 8-hour shift.

g.	Model Exposure Limits.  Since no safe exposure level has been established, a prudent Industrial Hygiene program will utilize the lowest limits achievable; which, in this case, are recommended by NIOSH (Nitrous oxide 25 ppm, halogenated agents 2 ppm).

5.	Exposure Control Strategies.

a.	Use of scavenging systems.

b.	Routine leak detection.

1)	High pressure system - quarterly.

2)	Low pressure system - daily.

c.	Regular equipment maintenance.

d.	Efficient low leakage anesthesia administration techniques.

e.	Air monitoring - quarterly.

f.	Periodic evaluation of the ventilation system.

g.	Proper venting of the scavenging system.

6.	Exposure Control Methods.

a.	General.  Strategies for exposure control including engineering control methods and work practices have been recommended by NIOSH and ASA and are summarized below:

1)	The implementation of exposure control strategies should be included in the training conducted for exposed personnel.  Biomedical equipment repair personnel and those who operate the anesthesia equipment and Cryosurgical Units should be especially familiar with these methods.

2)	Exposure control methods that are built-in the equipment include gas scavenging devices, patient face masks or tubes that reduce leakage, and quick disconnect hoses.  Room ventilation can also contribute to exposure control.

3)	Work practices of those who operate the anesthesia equipment can be a source for reducing the exposure for themselves and others in the room.

b.	Delivery System of Medical Gases.  Medical gases such as nitrous oxide may be delivered to the anesthesia unit from a bulk storage facility.  Usually, this consists of a cylinder duplex manifold system.  VA Master Specification H-08-1, Section 15315, details specific requirements for such a system.  In addition, 29 CFR 1910.105 requires that transfer and distribution of nitrous oxide shall be designed, installed, maintained, and operated in accordance with Compressed Gas Association G-8.1-1964.  Compressed gas cylinders may also be used to deliver medical gases to the anesthesia unit.  All personnel must be provided with appropriate job training in the handling of compressed gas cylinders.

c.	How Anesthesia is Administered.

1)	Two kinds of substances are administered for general anesthesia:

a)	Nitrous Oxide is a gas at room temperature and is a nonflammable, colorless, sweet-tasting gas that is heavier than air.

b)	Halogenated anesthetic materials are liquids at room temperature.  When vaporized they are 5 to 7 times heavier than air.  Enflurance (ethrane) and halothane (fluothane) are nonflammable liquids which vaporize easily.  Halothane is colorless and has a sweet odor.  Methoxyflurane (penthrane) is a combustible colorless liquid with a fruity odor.

2)	The most commonly used method for administering anesthesia in the OR is through a high-flow, semiclosed rebreathing system with a carbon dioxide absorber.  The carbon dioxide absorber unit is equipped with a pop-off valve (expiration or pressure relief valve) which may be the chief source of gas leakage.

3)	The anesthesia unit is usually equipped with a vaporizer designed to convert a volatile liquid anesthetic agent into a vapor and to administer a controlled volume or concentration.  This vapor is mixed with other gases and then delivered to the patient but in a greater volume than the patient’s metabolic requirements.  Excess vapor is vented out of the breathing system through the pop-off valve in order to prevent overfilling.

d.	Scavenging is the collection and disposal of waste gases and vapors from the breathing systems at the site of overflow.  Scavenging assists in the prevention of anesthetic dispersion into the room air, and is a form of local exhaust ventilation.

1)	Most scavenging systems consist of two components:  a collection device (or scavenging adapter) to collect waste gases, and a disposal route to carry them out of the room.  In the absence of scavenging, the air in any given operatory may contain WAG from an adjacent suite where it is used.  WAG may also enter an operatory from adjacent rooms via window, door, and air conditioning inlets, or from the dental suction unit when the exhaust is not vented to a site outside the building.

2)	The disposal route should vent these gases away from personnel and away from the hospital ventilation intake.  The scavenging system may be part of a nonrecirculating air conditioning system, a central room suction, or separate duct system used solely for waste gas disposal.

3)	Scavenging systems themselves may be a source of leakage through failure of connections, tubing defects, or inadequate design.

e.	Ventilation.  The following are VA minimum air change rates:

1)	Operating Rooms - 15 room air changes/hour.

2)	Recovery Rooms - 8 room air changes/hour.

3)	Animal Research - 15 room air changes/hour.

f.	Maintenance and Leakage.  An ongoing preventive maintenance program is absolutely essential to assure proper functioning of the anesthesia unit and scavenging system.  The main problem with an anesthesia unit from an industrial hygiene standpoint is gas leakage.

1)	Leakage from OR equipment may originate with high pressure or low pressure systems.  The high pressure system carries the gas from the tank to the anesthesia unit, while the low pressure system carries gas from the anesthesia unit to the patient.

2)	The components of high and mid-pressure systems (located between high pressure nitrous oxide source and the flowmeters) may release gases.  Leaky wall connectors, loose high-pressure hose connections, or deformed compression fittings may provide an escape route for waste gases.

3)	The components of the low pressure systems (located between the flowmeters and the patients) are also potential leak points.  There are multiple sites at which leakage can occur:  at loose or defective gaskets and seals, at worn-out or defective bags and breathing hoses, at loose flowmeter tubes, and at inadequately sealed oxygen absorption units.  The anesthetic machine may be a leakage source.

4)	Another possible source of leakage in the OR is the diffusion of anesthetic gases through rubber and plastic material (breathing tubes, bags, scavenger lines).

5)	Recommended Leak Checks.  NIOSH and ASA recommend that high pressure systems be leak tested quarterly and low pressure systems be tested with each use.

g.	Anesthetic Techniques.  An important factor contributing to the levels of waste anesthetic gases in the OR is the work practices of the Anesthetist.  The failure to properly connect and utilize scavenging equipment, the use of poorly fitted face masks and endotracheal tubes, or leaving the gases on when the anesthesia unit is disconnected from the patient may contribute greatly to gas concentrations in the air.

h.	Dental Operatories.  Anesthesia in the dental laboratory is delivered at a much higher flow rate than in the OR.  Nonbreathing circuits are primarily used.  Gases may leak into the room through the exhalation valve, around the nasal mask, and through the patient’s mouth.  When dental operations are in progress in more than one operatory at once, nitrous oxide cross contamination can be a substantial problem.  The air conditioning system can distribute the nitrous oxide from one suite to another.

i.	Animal Research Facilities.  Nitrous oxide, halothane, and methoxyflurane are the anesthetics most frequently used in veterinary anesthesia.  Animal researchers may use closed systems, semi-closed, and rebreathing systems for anesthesia.  Significant exposures may occur to research personnel due to problems of good fit with nose and face masks, and the frequent use of the T-tube for smaller animals.  Animal operatories converted from storage space, frequently have recirculating systems as opposed to the nonrecirculating ventilation systems in hospital operating rooms.  In addition, there is frequently an absence of scavenging systems for removal of waste gases.

7.	Exposure Monitoring.

a.	Air Sampling.  Both NIOSH and ASA recommend quarterly equipment leak tests and breathing zone air sampling.  Additional air sampling may be needed when equipment or techniques are modified.  Air sampling may be performed by the facility IH/Safety staff or an Industrial Hygiene Consulting Firm.  If a Miran IR Analyzer is not available at the medical center, plans should be made to purchase one.  In the meantime, one may be borrowed from the VISN Office, provided safe transportation and prompt return can be assured.

1)	All exposure limits mentioned above are based on personal sampling; that is, air sampling conducted in the breathing zone of the exposed employees.  Typically, the results from several air measurements with the Miran in the breathing zones of the anesthesiologist, surgeon, and nurses are averaged (for each person) to estimate a TWA for each person for the anesthesia administration period.  Passive dosimeters are worn to confirm the results or to measure other agents.

2)	NIOSH identifies direct infrared analysis (the Miran) as the most desirable method and the measurement of nitrous oxide as a good indicator of the levels of halogenated agents when they are mixed with it.  Sampling studies show that when levels of nitrous oxide are below the target 25 ppm, levels of halogenated agents are around 0.5 ppm.

b.	Leak Tests are conducted, using direct reading instruments (Miran) for the purpose of detecting where gas is escaping from the anesthesia system.  As a follow-up to leak tests, immediate repair or adjustment of the equipment is essential to the exposure control program.  Equipment leak tests may be conducted when the anesthetic equipment is not in use; that is, when anesthetic procedures are not in progress.  It may be useful to have the equipment operator (anesthesiologist, dentist, research investigator, or nurse anesthetist) and the biomedical repair person in attendance.

c.	Breathing Zone Sampling.  Breathing zone air samples should be conducted during normal use of the equipment; that is, during surgical, dental or laboratory animal procedures.  When using the Miran to obtain instantaneous measurements which then need to be averaged to estimate the time-weighted average; if an automatic recorder is not used, it is important to write down the sample beginning and ending times and as many different measurements as possible for later averaging.  Passive dosimeters for organic vapor monitoring can be used to estimate time-weighted average exposures to enflurane and halothane.  They should be worn during the entire anesthesia procedure period of one day and then sent for analysis.  Passive dosimeters for nitrous oxide are available and are more precisely compared to recommended exposure limits when they are sent for analysis after a one day, rather than a one week, exposure period.

d.	Sampling Tips.  The following are suggestions to consider when initiating air sampling.  These are most appropriate for air sampling in the operating room, but many can be applied to sampling in the dental operatory or research laboratory.

1)	Brief anesthesiology and OR staff well in advance on what you are going to do.

2)	Try to schedule sampling during prolonged procedures such as hip replacements.

3)	Check with surgery early in the morning of your scheduled sampling day to confirm that you may proceed.

4)	Calibrate the Miran before you enter the OR.  Note that the clean air (charcoal) filter used to zero the Miran does not adsorb nitrous oxide.  Therefore, the instrument should be “zeroed” in air free of nitrous oxide.

5)	Allow yourself sufficient time to gown-up and transport your sampling devices to the OR.

6)	Once inside the OR keep well away from sterile fields, usually identified by blue drapes.

7)	Observe that scavenging systems are used.

8)	Sample the air around connectors and fittings on the anesthesia unit.

9)	Begin by sampling the breathing zone level at the anesthetist’s position; then, as the opportunity arises, sample for other personnel.

10)	False high measurements have been identified when air sampling with the Miran in atmospheres with significant concentrations of formalin, isopropyl alcohol, ethyl alcohol, carbon dioxide, and water vapor [NIOSH].

e.	Model Sampling Program.  The model program includes quarterly leak checks (with immediate repairs or adjustment), and quarterly breathing zone sampling during typical OR, dental, or research procedures.  The leak check and breathing zone sampling should be done with a Miran.  It is advisable to also include passive dosimetry (for enflurane and halothane, and perhaps nitrous oxide) to confirm breathing zone samples on an annual basis.

8.	Employee Training.  In 1977 NIOSH recommended initial (upon assignment) and annual training of exposed employees.  Although anesthetic gases are regulated by the Food and Drug Administration, and are thereby exempt from the requirements of the Hazard Communication Standard; an Information and Training Program similar to the Hazard Community Program is appropriate and consistent with NIOSH’s recommendation and JCAHO accreditation criteria.  The training topics should include:  health hazards of WAG; exposure control strategies (engineering and work practices); the purpose, benefits, results, and schedule for air sampling; and the purpose of medical surveillance.

9.	Product Label and Work Site Posting.  NIOSH recommends specific warning label language for anesthetic gases to appear on the product and posted where exposure is likely.  They are much less comprehensive than the label requirements of Hazard Communication Standard from which these gases and vapors are exempt.

10.	Medical Surveillance.  NIOSH recommends employers collect medical histories with emphasis on the outcome of pregnancies (for exposed women and wives of exposed men) and exposure histories for exposed male and female employees.  The following is extracted from the NIOSH Standard:  Medical surveillance, as outlined below, shall be made available to all employees subject to occupational exposure to waste anesthetic gases.

a	Comprehensive preplacement medical and occupational histories shall be obtained and maintained in the employees’ medical records with special attention given to the outcome of pregnancies of the employee or spouse; and to the hepatic, renal, and hematopoietic systems which may be affected by agents used as anesthetic gases.  This information should be updated at least yearly and at any other time considered appropriate by the responsible physician.

b	Preplacement and annual physical examinations of employees exposed to anesthetic gases are recommended and, when performed, the results shall be maintained in the employees’ permanent medical records.

c)	Employees shall be advised of the potential undesirable effects of exposure to waste anesthetic gases; such as spontaneous abortions, congenital abnormalities in their children, and effects on the liver and kidneys.

d)	Any abnormal outcome of the pregnancies of employees or of the spouses of employees exposed to anesthetic gases shall be documented as part of the employees’ medical records, and the records shall be maintained for the period of employment plus 20 years [5 CFR 293.511(b) requires 30 year retention].

11.	Recordkeeping.  Although NIOSH recommends keeping records of air sampling, leak tests and medical surveillance for at least 20 years, Federal Regulation requires them to be “maintained for the duration of employment; plus 30 years, or for as long as the Official Personnel Folder is maintained, whichever is longer."

a.	The same Federal Regulation requires relevant exposure records to be kept in the medical records of exposed employees.  Therefore, the reports of quarterly equipment leak tests and breathing zone air sampling should be copied and put in the medical records.  In addition, it may be wise to post these reports where employees are likely to see them.

b.	Training records, kept by each service, should include training topics, dates and names of attendees.

12.	References.

13.	Review/Rescission Date:

(NAME)

Medical Center Director

Attachment

Permissible Levels of Exposure

Attachment

Permissible Levels of Exposure to Anesthetic Gases

Proposed by Various Authorities

(Expressed in PPM)

| Gas/Vapor | NIOSH | ACGIH | OSHA |
| --- | --- | --- | --- |

| Nitrous Oxide | 25 TWA for the Admin. Period | 50 TWA for 8 hrs. (Proposed) | -- |
| --- | --- | --- | --- |
| Enflurance | 2 TWA for the Admin. Period but not more than 1 hour. | 75 TWA for 8 hrs. | -- |
| Halothane | 2 TWA for the Admin. Period but not 1 hour. | 50 TWA for 8 hrs. | -- |
| Methoxyflurane | 2 TWA for the Admin. Period but not more than 1 hour. | -- | -- |
| Fluoroxene | 2 TWA for the Admin. Period but not more than 1 hour. | -- | -- |