SPECIAL SPECIFICATION

SECTION 08950

EXPLOSION VENTING WALL PANEL SYSTEM

PART 1 - GENERAL

1.01	DESCRIPTION OF WORK	2

1.02	REFERENCES	2

1.03	QUALITY ASSURANCE	4

1.04	SUBMITTALS	4

1.05	STORAGE	6

PART 2 - PRODUCTS

2.01	TRANSLUCENT FACING	6

2.02	NON-COMBUSTIBLE GRID CORE	7

2.03	ADHESIVE	7

2.04	PANEL CONSTRUCTION	8

2.05	BATTENS AND PERIMETER CLOSURE SYSTEMS	8

2.06	FLEXIBLE SEALING TAPE	8

2.07	EXPLOSION VENTING SYSTEM & WIND PRESSURE REQUIREMENTS.	9

PART 3 - EXECUTION

3.01	PREPARATION	9

3.02	ERECTION	9

3.03	CLEANING	10

SPECIAL SPECIFICATION

SECTION 08950

EXPLOSION VENTING WALL PANEL SYSTEM

PART 1 - GENERAL

1.01	DESCRIPTION OF WORK

A.	All requirements of the contract documents form an integral part of the work specified herein; in particular, refer to the conditions (general or otherwise), and Division 1 of the specifications, including all subdivisions thereof.

B.	Explosion venting panels shall consist of double faced, translucent, insulated flat sandwich panels and attachment system including installation.  Panels shall be

2-3/4” thick and consist of glass fiber reinforced polymer faces bonded to a mechanically interlocked aluminum grid core.

C.	Work Included:  Supply all labor and materials required to deliver and install the insulated explosion venting panel system.  The following major items are included:

1.	Translucent panels.

2.	Explosive release fastening system.

3.	Installation system.

D.	Related work specified elsewhere:

1.	Division 5, Section “Structural Steel”.

2.	Division 5, Section “Miscellaneous Metals”.

3.	Division 7, Section “Joint Sealants”.

1.02	REFERENCES

A.	American National Standards Institute (ANSI/American Architectural Manufacturers Association (AAMA)

605.2	Voluntary Specification for High Performance Organic Coatings on

Architectural Extrusions and Panels.

B.	American Society for Testing and Materials (ASTM)

A 123		Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and 					Steel Products

B 221		Specifications for Aluminum and Aluminum-Allow Extruded Bars,

Rods, Wire, Shapes and Tubes

C-236		Test Method for Steady-State Thermal Performance of Building

Assemblies by Means of a Guarded Hot Box

C-297		Test Methods for Tensile Strengths of Flat Sandwich Construction in

Flatwise Plane

D-635		Test Method for Rate of Burning and/or Extent and Time of Burning

of Self-Supporting Plastics in a Horizontal Position

D-1002	Test Method for Apparent Shear Strength of Single-Lap-Joint

Adhesively Bonded Metal Specimens (Metal-to-Metal)

D-1037	Test Methods of Evaluation the Properties of Wood-Base Fiber and

Particle Panel Materials

D-1183	Test Method for Resistance of Adhesives to Cyclic Laboratory

Aging Conditions.

D-2244	Test Method for Calculation of Color Differences from Instrumentally

Measured Color Coordinates

E-72		Methods of Conducting Strength Tests of Panels for Building

Construction

E-84		Test Method for Surface Burning Characteristics of Building Materials

E-699		Criteria for Evaluation of Agencies Involved in Testing, Quality

Assurance, and Evaluating Building Components in Accordance

with Test Methods promulgated by ASTM Committee E-6

C.	Factory Mutual Research Corporation

1.03	QUALITY ASSURANCE

A.	Manufacturer’s and Erector’s Qualifications:

1.	Panel system manufacturer must be listed by the International Conference of 	Building Officials, which requires quality control inspections by an approved 	agency for sandwich panel construction.

2.	Quality control inspections and testing, conducted at least once each year, shall 	include manufacturing facilities, sandwich panel components and production 	sandwich panels for conformance with “Acceptance Criteria for Sandwich 	Panels” as regulated by the Uniform Building Code or equivalent.

3.	Materials and products shall be manufactured by a company continuously and 	regularly employed in the manufacture of similar materials for a period of at 	least ten (10) consecutive years; and which can show evidence of these 	materials being satisfactorily used on at least six (6) projects of similar size, 	scope and type within such a period.  At least three (3) of the projects shall have 	been in successful use for five (5) years or longer.

4.	Erection shall be by an installer which has been in the business of erecting 	similar materials for at least five (5) consecutive years; and can show evidence 	of satisfactory completion of projects of similar size, scope and type.

5.	The Explosion Venting Panel System shall be approved by Factory Mutual 	Research Corporation for use in pressure-relieving construction.

B.	Performance Requirements:  The manufacturer shall be responsible for the configuration and fabrication of the complete panel system.

1.04	SUBMITTALS

Submit the following in accordance with the Conditions of Contract and Division 1, Section, “Descriptive Submittals.”

A.	Submit shop drawings showing the total panel systems at 1/4” = 1/0” and all details of construction at full scale.

B.	Test reports to be furnished by sandwich panel system manufacturer in accordance with Division 1, Submittals.  The manufacturer shall submit certified test reports made by an independent testing organization for each type and class of panel system.  Reports shall verify that the material will meet all performance requirements of this specification.  Previously completed test reports will be acceptable if current and indicative of products used on this project.  Test reports required are:

1.	Flame Spread and Smoke Development (ASTM E-84).

2.	Burn Extent (ASTM D-635).

3.	Color Difference (ASTM D-2244).

4.	Impact Strength (SPI Method).

5.	Bond Strength (ASTM C-297 and ASTM D-1002).

6.	Accelerated Aging (ASTM D-1037).

7.	Beam Bending Strength (ASTM E-72).

8.	Insulation “U” Factor (ASTM C-236).

C.	Proof of regular, independent quality control monitoring by an approved agency shall be submitted.

D.	Submit certifications and proof of manufacturer’s and erector’s qualifications as 		itemized below:

1.	Manufacturer qualifications to substantiate the requirements above under 			paragraph 1.03, A, 3.

2.	Erector’s qualifications to substantiate the requirements above under paragraph 			1.03, A, 4.

E.	Submit Certified approval of the explosion venting panel system by the Factory Mutual Research Corporation for meeting the requirements of

for explosion relieving construction.

F.	Submit samples 12” x 24” (minimum) of the sandwich panel, a sample of the aluminum battens and closure systems, and a sample of the explosion relieving fasteners.  Provide the Sandia Delegated Representative (SDR) with 2” x 3” (minimum) custom color chips on aluminum for selection by the Sandia Delegated Representative (SDR).

G.	Submit instructions for the removal and re-installation of the panels within the perimeter framing system.  The instructions shall address a logical sequence of steps that could be followed by competent trades or maintenance personnel.  The instructions must list recommended bolt torque and tolerance required for the explosion relieving fasteners.

H.	Provide certification stating that all materials used are asbestos-free and lead paint-free.

1.05	STORAGE

A.	Store translucent panels on the long edge, several inches above the ground, blocked and under cover to prevent warping.

PART 2 - PRODUCTS

2.01	TRANSLUCENT FACING

A.	Translucent faces shall be manufactured by panel system fabricator especially for architectural use.

B.	Flammability:  The interior face sheet shall have a flame spread rating no greater than 45 and smoke developed no greater than 350 when tested in accordance with ASTM E-84.  Burn extent by ASTM D-635 shall be no greater than 1”.

C.	Weatherability:

1.	The full thickness of the exterior face shall not change color more than 3.0 Units 		(DELTA E by ASTM D-2244) after five (5) years outdoor South Florida 			weathering at 7o facing South, determined by the average of at least three (3) 			white samples without a protective film or coating to insure maximum, long 			term color stability.

2.	A white interior face sheet shall not darken more than 0.2 Units (DELTA L by 			ASTM D-2244) when exposed to 150 o F for two (2) weeks.

3.	The exterior face shall have a permanent glass erosion barrier to provide 				maximum long term resistance to surface erosion.

4.	The exterior face shall have a self-cleaning thermoset acrylic urethane surface 			molecularly bonded under factory controlled conditions, minimum 1.2 mils 			thick, fully field restorable if worn or damaged.

D.	Appearance:

1.	The faces shall be uniform in color to prevent splotchy appearance.  Faces shall 			be completely free of ridges and wrinkles which prevent proper surface contact 			in bonding to the aluminum grid core.  Clusters of air bubbles/pinholes which 			collect moisture and dirt will not be acceptable.

2.	Exterior face sheets shall be .070” thick and crystal in color.  Interior face sheets 		shall be .045” thick and white in color.  Faces shall not vary more than + 10% in 		thickness.

E.	Strength:  The exterior face sheet shall be uniform in strength and repel an impact equal to 60 ft. lbs. without fracture or tear in accordance with SPI Shatter Resistance Test.

2.02	NON-COMBUSTIBLE GRID CORE

A.	All aluminum extrusions shall meet the requirements of ASTM B221 except as modified herein.  The aluminum I-beams shall be 6061-T6 with provisions for mechanical interlocking of muntin-mullion and perimeter to prevent high and low intersections which do not allow full bonding surface to contact with face material.  Width of I-beam shall be no less than 7/16”.  Aluminum I-beam for the grid shall be machined to tolerances of not greater than + .002”.

2.03	ADHESIVE

A.	The laminate adhesive shall be heat and pressure resin-type engineered for structural sandwich panel use.  Adhesive shall pass testing requirements specified by the International Conference of Building Officials “Acceptance Criteria for Sandwich Panel Adhesive”.  Minimum strength shall be:

1.	750 PSI tensile strength by ASTM C-297 after two (2) exposures to six (6) 			cycles each of the aging conditions prescribed by ASTM D-1037.

2.	500 PSI Shear strength average of five (5) exposures by ASTM D-1002:

a.	50% relative humidity at 73 o F.

b.	Accelerated Aging by ASTM D-1183.

c.	182 o F.

d.	Full Cycle Soak.

e.	500 Hour Oxygen Bomb.

2.04	PANEL CONSTRUCTION

A.	Panels shall have a thickness of 2-3/4” with a “U” factor of 0.18; light transmission of 8% and shading coefficient of 0.07.

B.	Translucent panels shall be a true sandwich panel of flat fiberglass sheets bonded to a grid core of mechanically interlocking aluminum I-beams and shall be laminated under a controlled process of heat and pressure.  Tape bond systems are not allowed.

C.	Translucent sandwich panel deflection shall not exceed 3.5” at 35 lbs. per sq. foot loading and shall not exceed 0.10” set deflection five (5) minutes after load release per ASTM E-72 with a 12’ clearspan, tested flat.

D.	All grid patterns shall be 12” x 24” nominal shoji (long dimension vertical) and be symmetrical about the horizontal center line of each panel.

E.	The adhesive bonding line shall be straight, cover the entire width of the I-beam and have a neat, sharp edge.  In order to insure bonding strength, white spots at intersections of muntins and mullions shall not exceed four (4) for each forty (40) square feet of panel, nor shall they be more than 3/64” in width.

2.05	BATTENS AND PERIMETER CLOSURE SYSTEMS

A.	Extruded 6063-T6 and 6063-T5 aluminum screw clamp-tite closure system.  Thermal break perimeter system shall be factory prefabricated with “U” = .50 or less.

B.	All battens and perimeter closures to be supplied with 300 Series stainless steel screws (excluding final fasteners to the building).

C.	All exposed aluminum to be architectural 2-coat fluorocarbon system (high performance organic coating) equal to ANSI/AAMA 605.2.  Color and gloss to match wall panels as specified in Section “Manufactured Roof and Wall Panels”.

2.06	FLEXIBLE SEALING TAPE

A.	Sealing tape shall be manufacturer’s standard pre-applied to closure system at the factory under controlled conditions.

2.07	EXPLOSION VENTING SYSTEM & WIND PRESSURE REQUIREMENTS

A.	Translucent explosion venting panel system shall be designed so that the panels release from their perimeter frames at an internal static pressure within the building of 20 psf + 20% relative to the outside.  The panel system shall be capable of sustaining a wind pressure head-on load of 20 psf and a wind suction load of 10 psf without releasing.

B.	The explosion venting panels shall be tethered by a flexible wire capable of preventing the panels, in the event of a release, from dislodging from their installed position no further than 5 feet.

PART 3 - EXECUTION

3.01	PREPARATION

A.	The general contractor shall prepare openings including isolating dissimilar materials from aluminum system which may cause damage by electrolysis.

B.	The panel erector shall perform an inspection of the building opening to verify that the rough opening dimensions at the specified openings are of the proper dimensions on the drawings.  The panel erector shall inspect the building opening and attachment support to insure that all requirements of this specification will be met once the panels are installed.  The erector shall promptly notify the general contractor of any discrepancies or modifications required to the building and wait for their resolution prior to proceeding with erection.

3.02	ERECTION

A.	The erector shall erect the explosion venting panel system in strict accordance with approved shop drawings as supplied by manufacturer.  Fastening and sealing shall be in strict accordance with manufacturer’s shop drawings.  All aluminum shall be cleaned before sealants are applied.

B.	After other trades have completed work on adjacent material, carefully inspect explosion venting panel system installation and make adjustments necessary to insure proper installation and weather-tight conditions.

C.	All staging, lifts and hoists required for the complete panel installation, including staging, etc., necessary for field measuring, shall be provided by, set up and maintained by the erection contractor.

3.03	CLEANING

A.	Clean the completed system, inside and out, promptly after erection and installation of panels, allowing for nominal curing of liquid sealants.  The installer shall advise the Contractor of proper and adequate procedures for protection and cleaning during the remainder of the construction period so that the system will be without damage and deterioration at the time of acceptance.

B.	At the time of Substantial Completion, clean the explosion venting panel system thoroughly.  Demonstrate proper cleaning methods and materials to the Owner’s maintenance personnel.

END OF SECTION