## Explosion-Calculation
CHAPTER 15. ESTIMATING PRESSURE INCREASE AND EXPLOSIVE ENERGY
RELEASE ASSOCIATED WITH EXPLOSIONS
Version 1805.0
The following calculations estimate the pressure and energy due to an explosion in a confined space.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Fuel Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input
parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cells(s).
The chapter in the NUREG should be read before an analysis is made.
INPUT PARAMETERS
EXPLOSIVE FUEL INFORMATION
| Adiabatic Flame Temperature of the Fuel ((Tad) |  |  |  | 2338 | °F | 1281.1111 | °C
[7 empty] | 1554.1111 | K
| Heat of Combustion of the Fuel (DHc) |  |  |  | 46360 | kJ/kg
| Yield (a), i.e., the fraction of available combustion |  |  |  | 100 | % | 1
1 percent for unconfined mass release and 100
percent for confined vapor release energy
participating in blast wave generation
| Mass of Flammable Vapor Release (mF) |  |  |  | 48 | lb | 21.8182 | kg
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F | 25 | °C
[7 empty] | 298 | K
| Initial Atmospheric Pressure (Pa) |  |  |  | 14.7 | psi | 101.3529 | kPa
Calculate
THERMAL PROPERTIES FOR FUELS
FLAMMABILITY DATA FOR FUELS
| Fuel | Adiabatic Flame Temperature |  | Heat of Combustion |  | Select Fuel Type
|  | Tad (°F) |  | DHc (kJ/kg)
| Acetylene | 4779 |  | 48220 |  | Scroll to desired fuel type then
| Carbon Monoxide | 4329 |  | 10100 |  | Click on selection
| Ethane | 2244 |  | 47490
| Ethylene | 4152 |  | 47170
| Hydrogen | 4085 |  | 130800
| Methane | 2143 |  | 50030
| n-Butane | 2442 |  | 45720
| n-Heptane | 2586 |  | 44560
| n-Pentane | 2356 |  | 44980
| n-Octane | 2478 |  | 44440
| Propane | 2338 |  | 46360
| Propylene | 4050 |  | 45790
| User Specified Vlaue | Enter Value |  | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995, Page 1-86.
METHOD OF ZALOSH
Reference: SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995, Page 3-312.
Pressure Rise from an Confined Explosion
(Pmax)/Pa = (Tad/Ta)
| Where | Pmax = maximum pressure developed at completion of combustion (kPa)
Pa = initial atmospheric pressure (kPa)
Tad = adiabatic flame temperature (K)
Ta = ambient temperature (K)
Pmax = (Tad/Ta) Pa
| Pmax = | 528.5695 | kPa | 76.6626 | psi
Blast Wave Energy Calculation
E = a DHc mF
| Where | E = blast wave energy (kJ) [E is the Trinitrotoluene (TNT) equivalent energy]
a = yield (a is the fraction of available combustion energy participating in blast wave generation)
DHc = heat of combustion (kJ/kg)
mF = mass of flammable vapor release (kg)
| E = | 1011490.9091 | kJ | 957983.04 | Btu
TNT Mass Equivalent Calculation
WTNT = E/4500
| Where | WTNT = weight of TNT (kg)
E = explosive energy release (kJ)
| WTNT = | 224.7758 | kg | 495.5458 | lb
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection
Engineering, 2nd Edition, 1995.
Calculations are based on certain assumptions and have inherent limitations. The results of such
calculations may or may not have reasonable predictive capabilities for a given situation, and should
only be interpreted by an informed user.
Although each calculation in the spreadsheet has been verified with the results of hand calculation,
there is no absolute guarantee of the accuracy of these calculations.
Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheet,
please send an email to nxi@nrc.gov or mxs3@nrc.gov.
Prepared by: |  | Date |  | Organization
Checked by: |  | Date |  | Organization
Additional Information
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | January 2004
Note on F23: This default value (14.70) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.