DIVISION 1 - GENERAL REQUIREMENTS

01010	Summary of Work

01090	Sources for Reference Publications

01311	Contractor-Prepared Network Analysis System

01330	Submittal Procedures

01380	Project Photographs and Video

01400	Contractor Quality Control

01500	Construction Facilities

01560	Environmental Protection

01700	As-Built Records

01740	Health, Safety, and Emergency Response

DIVISION 2 - SITEWORK

02003	Survey Control for Excavation and Backfilling

02099	Small Access Bridge

02110	Clearing and Grubbing

02112	Erosion and Sediment Control

02225	Excavation, Backfilling, and Compacting

02420	Manhole Structures

02713	Site Piping Systems

02730	Rotary-Drilled Ground Water Monitoring Wells and Directional Drilled System Piping

02831	Fence, Chain Link

02935	Turf

DIVISION 3 - CONCRETE

03410		Precast Structural Concrete

DIVISION 4 - MASONRY

DIVISION 5 - METALS

DIVISION 6 - WOODS AND PLASTIC

DIVISION 7 - THERMAL AND MOISTURE PROTECTION

07920		Sealants

DIVISION 8 - DOORS AND WINDOWS

DIVISION 9 - FINISHES

DIVISION 10 – SPECIALISTS

DIVISION 11 – EQUIPMENT

DIVISION 12 - FURNISHINGS

DIVISION 13 - SPECIAL CONSTRUCTION

13999	Operation and Maintenance Requirements

DIVISION 14 - CONVEYING SYSTEMS

DIVISION 15 - MECHANICAL

15011	Mechanical General Requirements

15060	Valves and Piping Appurtenances

DIVISION 16 - ELECTRICAL

16010	General Requirements for Electrical Work

16011	Electrical General Requirements

16050	Basic Materials and Methods - Electrical

16301	Underground Electrical Work

16400	Service and Distribution

16901	Process Instrumentation and Controls

SECTION 01010

SUMMARY OF WORK

PART 1	GENERAL

1.1	INTRODUCTION

The project SITE encompasses sections of the Federal Aviation Administration (FAA) William J. Hughes Technical Center (facility) at the Atlantic City International Airport in New Jersey.  The SITE is known as the Recharge Bed area.  The SITE is part of the ongoing CERCLA Superfund remediation at the FAA facility.  The remediation is known as the Area B and Area 41 Remedial Action

A Recharge Bed will be constructed to receive water from a new water treatment plant located at Area D at the FAA facility.  The treatment plant will receive recovered ground water from Areas 41, B, D, and possibly E (future).

Construction at the site will consist of the excavation and construction of the Recharge Bed, conveyance piping, and controls; installation of monitoring wells; and the expansion of the existing Area B sprinkler system.  The Recharge Bed will consist of a distribution piping system within a coarse sand layer constructed approximately 15 to 20 feet below grade.  Once the Recharge Bed is constructed, the excavated areas will be completely backfilled with native materials and the site will be re-vegetated.

1.2	GENERAL REQUIREMENTS

1.2.1	Subcontractors and Personnel

The Contractor shall provide a list of the key personnel of the Contractor and subcontractors (including addresses and telephone numbers) for use in the event of an emergency.  As changes occur and additional information becomes available, correct and change the information contained in previous lists.  In addition, the Contractor shall be responsible for furnishing an identification badge or card to each employee prior to the employee’s work on the site.

1.2.2	Contractor’s Representative

The Contractor’s representative shall be someone authorized by the Contractor to make decisions and agreements on this contract for the Contractor.

1.2.3	Availability of Utility Services

Sufficient electricity to power one site trailer will be provided.  The Contractor shall pay all costs incurred in connecting, converting, and transferring the utilities to the work, including installing all transformers and wiring from the connection point to the trailer.  The Contractor shall be responsible for making connections, and for disconnections and temporary component removal.  The Contractor shall contact the FAA’s electrical engineering personnel to determine the most appropriate temporary connection point on the adjacent FAA overhead electrical power lines.

The only water available on site will be from an onsite injection well (RP-IW1) that has a capacity of up to approximately 90 gpm.  If the Contractor desires to use water from this well, the Contractor shall be responsible for providing all necessary pumps and generators to pump water from the well.  All submersible pumps, hose, and other components placed in the well shall be properly decontaminated (to the satisfaction of the FAA) prior to their installation.  The water shall be considered non-potable.

Ensure that new utility lines are complete, except for the connection, before interrupting existing service.

The utility interruption to electric service shall be considered utility cutovers.  Such interruption shall be further limited to four (4) hours.  This limit includes time for deactivation and reactivation.

1.2.4	Radio Transmitter Restrictions

Conform to restrictions and procedures for the use of radio transmitting equipment, as directed.  Do not use transmitters without prior approval from the Resident Engineer (RE).

1.2.5	Security Requirements

No employee or representative of the Contractor will be admitted to the work site without satisfactory proof of United States citizenship or specifically authorized admittance to the work site by the RE.

a.	The Contractor shall be responsible for monitoring all personnel requiring access to the work site which shall include his personnel, delivery trucks, authorized visitors to the site, etc.

b.	Proper identification will be required for anyone and everyone entering the work area.  The form of this identification shall be an identification badge and it will be the responsibility of the Contractor to comply with this requirement and the requirements spelled out at the pre-construction meeting.  The Contractor shall obtain all FAA required security badges and vehicle passes according to all current FAA security requirements.

c.	Security clearance may be required for some contractor personal as requested by the FAA.

d.	Contractor shall provide the RE with a list of Contractor’s personnel who will require access to the premises.  This list shall be kept current during project work.

e.	Work shall be arranged so that the Contractor’s personnel can be escorted when required by FAA, in certain areas classified as controlled surfaces.  Contractor’s personnel shall not violate any security regulations pertaining to the airport.  Violators may be removed from the premises with the right to reenter revoked.

f.	Current procedures at FAA facilities include the “right to search.”  If, in the judgement of the gate security guard, airport guard, or military guard, a cause to search a vehicle or the person or personnel exists, such search will be made.

g.	Failure of the Contractor to fully comply with the above instructions and/or directions from the RE shall result in an immediate shutdown of the entire project until such time as the Contractor demonstrates his compliance.

h.	Contractor vehicles requiring access to the airport must comply with the following procedure:

(1)	The Contractor must supply the following information to the RE.

a)  Company name

b)  Job supervisor’s name

c)  Number and description of vehicles

d) Description of work and location of work area.

(2)	The job supervisor will sign for airport passes at the time of issue by the FAA Technical Center Security.  Issue records are available for inspection at the Center Security Office.  All vehicles must obtain a pass prior to entering the site.

1.2.6	Weather Protection

If a warning of inclement weather conditions is issued, take precautions to minimize any danger to persons, and protect the work and any nearby Government or off-site property.  Precautions shall include, but are not limited to, closing or protecting openings in buildings or excavations; removing loose materials, tools, and equipment from exposed locations; and removing or securing other temporary work.  Additional sedimentation and erosion control measure shall be installed by the Contractor if storm events of unusual strength are anticipated.  Close openings in the work if storms of lesser intensity pose a threat to the work or any nearby Government or off-site property.

1.2.7	Coordination Meetings

Once each week, on a regularly scheduled day and hour, an authorized representative of the Contractor shall meet with the Contracting Officer (CO) and/or RE, in the Technical Support Facility (TSF) Building (or other location chosen by the FAA), to confer on contract progress, future scheduling, proposed procedures, coordination with other projects, etc.

1.3	PRE-CONSTRUCTION SUBMITTALS

The Contractor will be required to submit plans for review and receive concurrence from the RE that they meet the requirements of the Technical Specifications and regulations prior to commencement of any field activities.  Plans requiring submission include, but are not limited to, the following:

Network Analysis System (found in Section 01311)

Submittal Register (found in Section 01330)

Photography Plan (found in Section 01380)

Environmental Protection Plan (found in Section 01560)

Site Health & Safety Plan (found in Section 01740)

Soil Erosion & Sedimentation Control Plan (found in Section 02112)

1.4	SITE PREPARATION

This section discusses the preparation tasks only and does not represent a complete listing of sequential tasks. For a more complete listing refer to the Contract Drawings.

The Contractor’s SITE trailer shall be set in place and have power service installed as soon as possible.  Cellular-type phone service shall be provided to the trailer by the Contractor.  Temporary sanitary facilities for the Contractor’s use shall be in place prior to commencing site activities.  The Contractor may utilize the open field near the Main Area B Control Building as a lay-down area for the temporary storage of materials.  Outdoor storage of equipment or materials will not be allowed unless permitted by the equipment/material manufacturer.  In any case, all equipment and materials must be stored in accordance with manufacturer’s instructions.

Prior to initiating the SITE preparation activities, the Contractor shall perform any required pest control (i.e., wasp eradication) and then erect the security gates and soil erosion and sedimentation control measures.

All trees, shrubs, stumps and roots removed during clearing and grubbing shall be thoroughly dried and cleaned of all soil prior to chipping and grinding.  Wood chips shall be disposed of off-site.

Water shall be used throughout the excavation area, soil stockpile areas and work areas to control fugitive dust.  The Contractor shall provide a water tanker to transfer water to areas requiring dust control.

1.5	SITE RESTORATION

The Contractor shall be responsible for removing and/or disposing of facilities installed to construct the Recharge Bed.  Areas requiring complete removal and/or disposal off-site include the following:

Site Trailer

Temporary Utilities

Sedimentation and Erosion Controls

Lay-down Areas

The Contractor shall be responsible for leaving the SITE in a clean and neat condition.  All trash, debris, and waste material shall be completely removed from the SITE.  Lay-down areas shall be restored to pre-use conditions.

1.6	PRELIMINARY SEQUENCE OF CONSTRUCTION ACTIVITIES

The anticipated order of construction activities is given below.  The list of activities is not intended to be a critical path, nor be inclusive of all construction activities.

- Plan Development, Permitting and Approvals

- Install Erosion Sediment Controls and Fencing

- Clear & Grub

- Mobilize Office Trailer

- Construct Recharge Bed

- Install Conveyance Piping to Recharge Bed and Expanded Sprinkler System

Locations

- Construct New Control Vaults and Controls

- Install Monitoring Wells

- Integrate New Control Components into Existing System Controls

- System Checkout and Startup

- Site Restoration

END OF SECTION

SECTION 01090

SOURCES FOR REFERENCE PUBLICATIONS

PART 1	GENERAL

1.1	REFERENCES

Reference publications are cited in other sections of the specifications along with identification of their sponsoring organizations.  The addresses of the sponsoring organizations are listed below, and if the source of the publications is different from the address of the sponsoring organization, that information is also provided.  If no date for a specific reference publication is provided assume the most recent version is being referenced.

Air Conditioning and Refrigeration Institute (ARI)

4301 North Fairfax Drive, Suite 425

ATTN:  Pubs Dept.

Arlington, VA 22203

Phone:  (703) 524-8800

Fax: (703) 528-3816

Internet: www.ari.org

Email: ari@ari.org

Air Movement and Control Association (AMCA)

30 W. University Drive

Arlington Heights, IL 60004-1893

Phone:  (847) 394-0150

Fax: (847) 253-0088

Internet: www.amca.org

American Architectural Manufacturers Association (AAMA)

1827 Walden Office Square, Suite 104

Schaumburg, IL 60173-4268

Phone:  (847) 303-5664

Fax: (847) 303-5774

Internet: www.aamanet.org

American Association of State Highway and Transportation Officials (AASHTO)

444 N. Capitol Street, NW, Suite 249

Washington, DC 20001

Phone:  (202) 624-5800 or (800) 231-3475

Fax: (202) 624-5806 or (800) 525-5562

Internet: www.transportation.org

ACI International (ACI)

P.O. Box 9094

Farmington Hills, MI 48333-9094

Phone:  (248) 848-3700

Fax: (248) 848-3701

Internet: www.aci-int.org

American Conference of Governmental Industrial Hygienists (ACGIH)

1330 Kemper Meadow Drive, Suite 600

Cincinnati, OH 45240

Phone: (513) 742-2020

Fax: (513) 742-3355

Email: pubs@acgih.org

Internet: www.acgih.org

American Forest & Paper Association (AF&PA)

American Wood Council

ATTN:  Publications Dept.

1111 Nineteenth Street NW, Suite 800

Washington, DC 20036

Phone: (202) 463-2700 or (800) 294-2372

Fax: (202) 463-2471

Internet: www.afandpa.org

American Institute of Steel Construction (AISC)

One East Wacker Drive, Suite 3100

Chicago, IL 60601-2001

Phone: (312) 670-2400

Publications: (800) 644-2400

Fax: (312) 670-5403

Internet: www.aisc.org

American Iron and Steel Institute (AISI)

1101 17th St., NW Suite 1300

Washington, DC 20036

Phone (202) 452-7100

Internet: www.steel.org

American National Standards Institute (ANSI)

1819 L Street, NW, 6th Floor

Washington, DC 20036

Phone: (202) 293-8020

Fax: (202) 293-9287

Internet: www.ansi.org/

American Petroleum Institute (API)

1220 "L" Street, NW

Washington, DC 20005-4070

Phone: (202) 682-8000

Fax: (202) 682-8223

Internet: www.api.org

American Society for Testing and Materials (ASTM)

100 Barr Harbor Drive

West Conshohocken, PA 19428-2959

Phone: (610) 832-9585

Fax: (610) 832-9555

Internet: www.astm.org

American Society of Civil Engineers (ASCE)

1801 Alexander Bell Drive

Reston, VA 20191-4400

Phone: (703) 295-6300 or (800) 548-2723

Fax: (703) 295-6222

Internet: www.asce.org

Email: marketing@asce.org

American Society of Heating, Refrigerating, and Air Conditioning Engineers, Inc. (ASHRAE)

1791 Tullie Circle, NE

Atlanta, GA 30329-2305

Phone: (404) 636-8400/(800) 527-4723

Fax: (404) 321-5478

Internet: www.ashrae.org

American Society of Mechanical Engineers (ASME)

345 East 47th Street

New York, NY 10017

Phone: (212) 705-7722

Fax: (212) 705-7739

Internet: www.asme.org

American Water Works Association (AWWA)

6666 West Quincy Avenue

Denver, Co 80235

Phone: (303) 794-7711 or (800) 926-7337

Fax: (303) 794-7310

Internet: www.awa.org

American Welding Society (AWS)

550 N.W. LeJeune Road

Miami, FL 33126

Phone: (305) 443-9353/(800) 443-9353

Fax: (305) 443-7559

Internet: www.amweld.org

Builders Hardware Manufacturers Association (BHMA)

355 Lexington Avenue, 17th Floor

New York, NY 10017-6603

Phone: (212) 297-2122

Fax: (212) 370-9047

Internet: www.buildershardware.com

Building Officials & Code Administrators International (BOCA)

4051 W. Flossmoor Road

Country Club Hills, IL 60478

Phone: (708) 799-2300

Fax: (708) 799-4981

Internet: www.bocai.org

Door and Hardware Institute (DHI)

14150 Newbrook Drive, Suite 200

Chantilly, VA 20151-2223

Phone: (703) 222-2010

Fax: (703) 222-2410

Internet: www.dhi.org

Email: techdept@dhi.org

Factory Mutual Engineering and Research (FM)

500 River Ridge Drive

Norwood, MA 02062

Phone: (781) 255-6681 or (877) 364-6726

Fax: (781) 255-0181

Internet: www.fmglobal.com

Foundation for Cross-Connection Control and Hydraulic Research (FCCCHR)

University of South California

Kaprielian Hall 200

Los Angeles, CA 90089-2531

Phone:  (213) 740-2032

Fax: (213) 740-8399

Internet: www.usc.edu/dept/fccchr

Federal Specifications (FS)

General Services Administration

Federal Supply Service Bureau

470 L'Enfant Plaza, S.W.

Washington, DC 20407

Phone: 202-619-8925

Fax: 202-619-8978

Internet: http://pub.fss.gsa.gov/

Glass Association of North America (GANA)

2945 SW Wanamaker Drive, Suite A

Topeka, KS 66614-5321

Phone: 785-271-0208

Fax: 785-271-0166

Internet: www.glasswebsite.com

Hydraulic Institute (HI)

9 Sylvan Way, Suite 180

Parsippany, NJ 07054-3802

Phone: (973) 267-9700 OR (888) 786-7744

Fax: (973) 267-9055

Internet: www.pumps.org

Illuminating Engineering Society of North America (IESNA)

120 Wall Street, 17th Floor

New York, NY 10005-4001

Phone: (212) 248-5000

Fax: (212) 248-5017

Internet: www.iesna.org

Institute of Electrical and Electronics Engineers, Inc. (IEEE)

445 Hoes Lane

P.O. Box 1331

Piscataway, NJ 08855-1331

Phone: (732) 981-0060/(800) 701-4333

Fax: (732) 981-9667

Internet: www.ieee.org

Email: customer.services@ieee.org

Instrument Society of America (ISA)

67 Alexander Drive

Research Triangle Park, NC 27709

Phone: (919) 549-8411

Fax: (919) 549-8288

Internet: www.isa.org

Manufacturers Standardization Society of the Valve and Fittings Industry (MSS)

127 Park Street, NE

Vienna, VA 22180-4602

Phone: (703) 281-6613

Fax: (703) 281-6671

Internet: www.mss-hq.com

Email: info@mss-hq.com

Metal Building Manufacturers Association (MBMA)

1300 Sumner Avenue

Cleveland, OH 44115-2851

Phone: (216) 241-7333

Fax: (216) 241-0105

Internet: www.mbma.com

Email: mbma@mbma.com

Military Specification (MS)

Order Military Specifications, Standards and Related Publications From:

Department of Defense Single Stock Point (DODSSP) for

Defense Automation and Production Service (DAPS)

Building 4

700 Robbins Avenue

Philadelphia, PA 19111-5094

Phone: (215) 697-2179

Fax: (215) 697-1462

Internet: www.dodssp.daps.mil

National Association of Architectural Metal Manufacturers (NAAMM)

8 Michigan Ave., Suite 1000

Chicago, IL 60603

Phone: (312) 782-4951

Fax: (312) 332-0405

Internet: www.naam.org

Email: naamm@gss.net

National Association of Plumbing-Heating-Cooling Contractors (NAPHCC)

180 South Washington Street

P.O. Box 6808

Falls Church, VA 22046

Phone:  (800) 533-7674

Fax: (703) 237-7442

Internet: www.phccweb.org

Email: naphcc@naphcc.org

National Electrical Manufacturers Association (NEMA)

1300 N. 17th Street, Suite 1847

Rosslyn, VA 22209

Phone: (703) 841-3200

Fax: (703) 841-3300

Internet: www.nema.org

National Fire Protection Association (NFPA)

One Batterymarch Park

P.O. Box 9101

Quincy, MA 02269-9101

Phone: (617) 770-3000

Fax: (617) 770-0700

Internet: www.nfpa.org

National Institute for Occupational Safety and Health (NIOSH)

Mail Stop C-13

4676 Columbia Parkway

Cincinnati, OH 45226-1998

Phone: (800) 356-4674

Fax: (513) 533-8573

Internet: www.cdc.gov/niosh/homepage.html

New Jersey Department of Environmental Protection

401 E. State Street, CN413

Trenton, NJ 08625

Phone: (609) 984-2902

Internet: www.state.nj.us/dep/

New Jersey Department of Transportation (NJDOT)

1035 Parkway Avenue

Trenton, NJ 08625

Phone: (609) 530-2000

Internet: www.state.nj.us/transportation/

Precast/Prestressed Concrete Institute (PCI)

209 West Jackson Boulevard

Chicago, IL 60606-6938

Phone: (312) 786-0300

Fax: (312) 786-0353

Internet: www.pci.org

Email: info@pci.org

The Plastics Pipe Institute, Inc.

1825 Connecticut Ave., NW

Suite 680

Washington, DC 20009

Phone: (202) 462-9607, (888) 314-6774

Fax: (202) 462-9779

Internet: www.plasticpipe.org

Sheet Metal & Air Conditioning Contractors National Association (SMACNA)

4201 Lafayette Center Drive

Chantilly, VA 20151-1209

Phone: (703) 803-2980

Fax: (703) 803-3732

Internet: www.smacna.org

Email: info@smacna.org

Steel Deck Institute (SDI)

P.O. Box 25

Fox River Grove, IL 60021-0025

Phone: (847) 462-1930

Fax: (847) 462-1940

Internet: www.sdi.org

Email: Steve@sdi.org

Steel Door Institute (SDOI)

30200 Detroit Road

Cleveland, OH 44145-1967

Phone: (440) 899-0010

Fax: (440) 892-1404

Internet: www.steeldoor.org

The Society for Protective Coatings (SSPC)

40 24th Street, 6th Floor

Pittsburgh, PA 15222-4656

Phone: (412) 281-2331

Fax: (412) 281-9992

Internet: www.sspc.org

Steel Tank Institute (STI)

570 Oakwood Road

Lake Zurich, IL 60047

Phone: (847) 438-8265

Fax: (847) 438-8766

Internet: www.steeltank.com

Steel Window Institute (SWI)

1300 Sumner Avenue

Cleveland, OH 44115

Phone: (216) 241-7333

Fax: (216) 241-0105

Internet: www.steelwindows.com

Underwriters Laboratory, Inc. (UL)

333 Pfingsten Road

Northbrook, IL 60062-2096

Phone: (847) 272-8800

Fax: (847) 272-8129

Internet: www.ul.com/

Email: northbrook@us.ul.com

Uni-Bell PVC Pipe Association (UBPPA)

2655 Villa Creek Drive, Suite 155

Dallas, TX 75234

Phone: (214) 243-3902

Fax: (214) 243-3907

Internet: www.uni-bell.org

Email: infor@uni-bell.org

U.S. Department of Agriculture (USDA)

Order Other Publications From:

U.S. Department of Agriculture

14th Street & Independence Ave. S.W., Room 4028-S

Washington, D.C. 20250

Phone: (202) 720-2791

Fax: (202) 720-2166

Internet: www.usda.gov

U.S. Army Corps of Engineers (USACE)

U.S. Army Engineer Waterways Experiment Station

Order CRD-D Documents From.

Attn: Technical Report Distribution Section, Services Branch, TIC

3909 Halls Ferry Road

Vicksburg, MS 39180-6199

Phone: (601) 634-2664

Fax: (601) 634-2388

Internet: www.wes.army.mrl/SL/MTC/handbook/handbook.htm

U.S. Department of Defense (DOD)

Order From:

National Technical Information Service

5285 Port Royal Road

Springfield, VA 22161

Phone: (703) 605-6000

Fax: (703) 605-6900

Internet: www.ntis.gov

U.S. Department of Transportation (DOT)

400 7th Street, S.W.

Washington, DC 20590

Internet: dot.gov

U.S. Environmental Protection Agency (EPA)

Ariel Rios Building

1200 Pennsylvania Avenue, N.W.

Washington, DC 20460

Phone: 202-260-2090

Fax: 202-260-6257

Internet: www.epa.gov

U.S. Federal Aviation Administration (FAA)

Order From:

Superintendent of Documents

732 North Capitol Street, N.W.

Mail Stop: SDE

U. S. Government Printing Office

Washington, DC 20401

Phone: 202-512-1530

Fax: 202-512-1262

Internet: www.gpo.gov

U.S. General Services Administration (GSA)

Commercial Item Descriptions (CID)

Order From:

General Services Administration

Federal Supply Service Bureau

470 E L'Enfant Plaza, S.W., Suite 8100

Washington, DC 20407

Phone: (202) 619-8925

Fax:  (202) 619-8978

Internet: fss.gsa.gov/pub/fed-specs.ctm

U.S. Department of Housing and Urban Development (HUD)

Order From: HUD User

P.O. Box 6091

Rockville, MD 20849

Phone: (800) 245-2691

Fax: (301) 519-5767

Internet: www.huduser.gov

Email: Huduser@aspensys.com

U.S. National Archives and Records Administration (NARA)

Code of Federal Regulations (CFR)

700 Pennsylvania Avenue, N.W.

Washington, D.C. 20408

Phone: (800) 234-8861

Internet: www.nara.gov

PART 2	PRODUCTS

Not Used

PART 3	EXECUTION

Not Used

SECTION 01311

CONTRACTOR-PREPARED NETWORK ANALYSIS SYSTEM

PART I	GENERAL

1.1	SUMMARY

The work specified in this section consists of the preparation of a network analysis system for the contract work.

1.2	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by basic designation only.

U.S. ARMY CORPS OF ENGINEERS (USACE)

ER 1-1-11 (1995) Progress, Schedules, and Network Analysis System

1.3	SUBMITTALS

The following shall be submitted in accordance with Section 01330, “Submittal Procedures”:

SD-07, Schedules

Preliminary Network Analysis; GA

Six copies of a preliminary network analysis defining the Contractor’s planned operations during the first sixty (60) calendar days shall be submitted within ten (10) days after the notice to proceed.  The Contractor's general approach for the balance of the project shall be indicated.  Cost of activities expected to be completed or partially complete before submission and approval of the entire schedule shall be included.  Each action which may cause a potential shutdown or interruption to existing operating systems or utilities shall be identified on the preliminary network schedule.

Final Network Analysis; GA

Six copies of the complete final network analysis consisting of the detailed network mathematical analysis (on-site manpower loading schedule, equipment schedule) and network diagrams shall be submitted within forty (40) calendar days after receipt of the notice to proceed.

Revised Schedules; GA

See Paragraph 3.1.3

SD-09; Reports

Progress Reports:  GA

See Paragraph 3.1.4

PART 2	PRODUCTS

Not Applicable

PART 3	EXECUTION

3.1	NETWORK ANALYSIS SYSTEM

The progress chart to be prepared by the Contractor shall consist of a network analysis system as described below.  In preparing this system, the scheduling of construction is the responsibility of the Contractor.  The requirement for the system is included to assure adequate planning and execution of the work and to assist the Contracting Officer (CO) and Resident Engineer (RE) in appraising the reasonableness of the proposed schedule and evaluating progress of work.

3.1.1	General

The network analysis system shall be in accordance with ER 1-1-11.  The Contractor shall have the option of using a microcomputer-based network analysis system.  If the Contractor elects to use a microcomputer-based system, one of the following software programs shall be used: (1) PMS 80 Project Management System by Pinnell Engineering, Inc., 5331 S.W. Macadam Ave., Suite 270, Portland, Oregon 97201, telephone (503) 243-2246; (2) Primavera Project Planner by Primavera Systems, Inc., Suite 925, Two Bala Plaza, Bala Cynwyde, PA 19004, telephone (215) 667-8600; or (3) other software program approved by the RE.  The system to be used shall be identified at the Pre-Construction Conference.  Submittal of information by the Contractor shall be by hard copy and by electronic data transfer.

3.1.2	System Requirements

The system shall consist of diagrams and accompanying mathematical analyses.  The diagrams shall show elements of the project in detail and the entire project in summary.

3.1.2.1	Diagrams

Show the order and interdependence of activities and the sequence in which the work is to accomplished as planned.  The basic concept of a network analysis diagram will be followed to show how the start of a given activity is dependent on the completion of preceding activities and how its completion restricts or restrains the start of following activities.  The diagram shall clearly show the activities of the critical path.  In addition to construction activities, detailed network activities shall include the submittal and approval of materials, samples, delivery of O&M manuals, training to be provided, shop drawings, the procurement of critical materials and equipment, receipt of materials with estimated procurement costs of major items for which payment of materials will be requested in advance of installation, fabrication of special material and equipment, and their installation and testing.  A summary of activity for time based overhead office and management costs shall be included.  Show activities of the Government that affect progress and contract-required dates for completion of all or parts of the work.  Show activities indicating Government furnished materials and equipment utilizing delivery dates.   Show the following information on the diagrams for each activity:

a.	Activity number

b.	Description of the activity

c.	Duration in work days

d.	Responsibility code indicating the party responsible for accomplishment of the activity.  As a minimum, provide a separate responsibility code for each subcontractor.

e.	Area code indicating the area of the project in which the work will be performed.

3.1.2.2	Network Details

Detailed network activities shown on a detailed or sub-network diagram shall include, in addition to construction activities, the submittal and approval of samples of materials and shop drawings, the procurement of critical materials and equipment, fabrication of special materials and equipment and their installation and testing.  All activities of the Government that affect progress and contract required dates for completion of all or parts of the work shall be shown.  The detail of information shall be such that duration times of activities shall range from three to 30 days with not over two percent of the activities exceeding these limits.  The activities which comprise the separate project features shall be separately identifiable by coding or use of sub-networks, or both.  The selection and number of activities shall be subject to approval by the RE.  Detailed networks, when summary networks are also furnished, need not be time scaled but shall be drafted to show a continuous flow from left to right with no arrows from right to left.  The following information shall be shown on the diagrams for each activity: preceding and following event numbers; description of the activity; cost; and activity summary.

3.1.2.3	Summary Network

If the project is of such size that the entire network cannot be readily shown on a single sheet, a summary network diagram shall be provided.  The summary network diagram shall consist of a minimum of 50 activities and a maximum of 150 activities, and shall be based on and supported by detailed diagrams.  Related activities shall be grouped on the network. The critical path shall be plotted generally along the center of the sheet with channels having increasing float placed towards the top or bottom.  The summary network shall be time scaled using units of approximately one-half inch equals one week or other suitable scale approved by the RE.  Weekends and holidays shall be indicated on the network.  Where slack exists, the activities shall be shown at the time when they are scheduled to be accomplished.

3.1.2.4	Mathematical Analysis

The mathematical analysis of the network diagram shall include a tabulation of each activity shown on the detailed network diagrams.  The following information shall be furnished as a minimum for each activity:

a.	Preceding and following event numbers (numbers shall be selected and assigned so as to permit identification of the activities with bid items);

b.	Activity description;

c.	Estimated duration of activities (the best estimate available at time of computation);

d.	Earliest start date (by calendar date);

e.	Earliest finish date (by calendar date);

f.	Scheduled or actual start date (by calendar date);

g.	Scheduled or actual finish date (by calendar date);

h.	Latest start date (by calendar date);

i	Latest finish date (by calendar date);

j.	Slack or float;

k.	Monetary value of activity;

l.	Responsibility for activity (Prime Contractor, subcontractors, suppliers, Government, etc.);

m.	Manpower required;

n.	Percentage of activities completed;

o.	Contractor’s earnings based on portion of activity completed; and

p.	Bid item of which activity is a part.

3.1.2.5	Mathematical Program

The program or means used in making the mathematical computation shall be capable of compiling the total value of completed and partially completed activities and subtotals from separate or project features.

3.1.2.6	Computations

In addition to the tabulation of activities, the computation will include the following data:

a.	Identification of activities which are planned to be expedited by use of overtime or double shifts to be worked including Saturdays, Sundays, and holidays;

b.	On-site manpower loading schedule;

c.	A description of the major items of construction equipment planned for operation of the project.  (The description shall include the type, number of units, and unit capacities.)  A schedule showing proposed times that equipment will be on the work site keyed to activities on which equipment will be used shall be provided; and

d.	Where portions of the work are to be paid by unit costs, the estimated number of units in an activity which was used in developing the total activity cost.

3.1.2.7	Order of Network Activities

The analysis shall list the activities in sorts or groups as follows:

a.	By the preceding event number from lowest to highest and then in the order of the following event number:

b.	By the amount of slack, then in order by preceding event number;

c.	By responsibility in order of earliest allowable start dates; and

d.	In order of latest allowable start dates, then in order of preceding event numbers, and then in order of succeeding event numbers.

3.1.3	Revised Schedules

The Contractor shall participate in a review and evaluation of the proposed network diagrams and analysis by the RE.  Any revisions necessary as a result of this review shall be resubmitted for approval by the RE within ten calendar days after the conference.  The approved schedule shall then be the schedule to be used by the Contractor for planning, organizing, and directing the work and for reporting progress.  If the Contractor thereafter desires to make changes in the method of operating and scheduling he shall notify the RE in writing stating the reasons for the change.  If the RE considers these changes to be of a major nature, he may require the Contractor to revise and submit for approval, without additional cost to the Government, all or the affected portion of the detailed diagrams and mathematical analysis and the summary diagram to show the effect on the entire project.  A change may be considered of a major nature if the time estimated to be required or actually used for an activity or the logic of sequence of activities is varied from the original plan to a degree that there is a reasonable doubt as to the effect on the contract completion data or dates.  Changes which affect activities with adequate slack time shall be considered as minor changes, except that an accumulation of minor changes may be considered a major change when their cumulative effect might affect the contract completion date.

Any project schedule changes shall be incorporated into the submittal register, where applicable, as part of this Contract.

3.1.4	Periodic Progress Reports

The Contractor shall submit at monthly intervals and not later than the 5th of each month, four copies of a report of the actual construction progress by updating the mathematical analyses.  Revisions causing changes in the detailed network shall be noted on the summary network, or a revised issue of affected portions of the detailed network furnished.  The summary network shall be revised as necessary for the sake of clarity.  However, only the initial submission or complete revisions need be time scaled.  Subsequent minor revisions need not be time scaled.

3.1.4.1	Completion of Activities

Progress reports shall show the activities or portions of activities completed during the reporting period and their total value as basis for the Contractor’s progress payment request.  Payment will be based on the total value of such activities completed or partially completed after verification by the RE.  The report shall state the percentage of the work actually completed and scheduled as of the report date and the progress along the critical path in terms of days ahead or behind the allowable dates.  If the project is behind schedule, progress along other paths with negative slack shall also be reported.  The Contractor shall also submit a narrative report with the updated analysis which shall include, but not be limited to, a description of the problem areas, current and anticipated, delaying factors and their impact, and an explanation of corrective actions taken or proposed.

END OF SECTION

SECTION 01330

SUBMITTAL PROCEDURES

PART I	GENERAL

1.1	SUBMITTAL DESCRIPTIONS (SD)

Submittals required are identified by SD numbers as follows:

SD-01 Data

SD-04 Drawings

SD-06 Instructions

SD-07 Schedules

SD-08 Statements

SD-09 Reports

SD-13 Certificates

SD-14 Samples

SD-18 Records

SD-19 Operation and Maintenance Manuals

1.2	SUBMITTALS

Submit the following in accordance with the requirements of this section.

SD-07 Schedules

Completed Submittal Register (ENG Form 4288); Updated Submittal Register (Eng Form 4288)

Submit and receive concurrence from the Resident Engineer (RE) that the submittal register meets the requirements of the Technical Specification prior to the commencement of any field activities.

1.3	SUBMITTAL CLASSIFICATION

Submittals are classified as follows:

1.3.1	Government Approved (GA)

Governmental approval is required for extensions of design, critical materials, deviations, equipment whose compatibility with the entire system must be checked, and other items as designated by the RE.  Within the terms of the Contract they are considered to be “shop drawings.”

1.4	APPROVED SUBMITTALS

The approval of submittals by the RE shall not be construed as a complete check, but will indicate only that the general method of construction, materials, detailing, and other information are satisfactory.  Approval will not relieve the Contractor of the responsibility for any error which may exist, as the Contractor under the Contractor Quality Control (CQC) requirements of this contract, is responsible for the dimensions and design of adequate connections, details, and satisfactory construction of all work.  After submittals have been approved by the RE, no resubmittal for the purpose of substituting materials or equipment will be given consideration unless accompanied by an explanation as to why a substitution is necessary.

1.5	DISAPPROVED SUBMITTALS

The Contractor shall make all corrections required by the RE and promptly furnish a corrected submittal in the form and number of copies as specified for the initial submittal.  If the Contractor considers any correction indicated on the submittals to constitute a change to the contract, notice as required shall be given promptly to the RE and Contracting Officer (CO).

1.6	WITHHOLDING OF PAYMENT

Payment for materials incorporated in the work will not be made if required approvals have not been obtained.

PART 2	PRODUCTS

Not Applicable

PART 3	EXECUTION

3.1	GENERAL

The Contractor shall submit all items listed on the Submittal Register (ENG Form 4288) or specified in the other sections of these specifications.  The Contractor shall use the approved Government numbering system for identification of submittals, additional submittals, and resubmittals.  The Contracting Officer’s Technical Representative (COTR) or RE may request submittals in addition to those listed when deemed necessary to adequately describe the work covered in the respective sections.  Units of the weights and measures used on all submittals shall be the same used in the contract drawings.  Submittals shall be made in the respective number of copies and to the respective addresses set forth below.  Each submittal shall be complete and in sufficient detail to allow ready determination of compliance with contract requirements.  Prior to submittal, all items shall be checked and approved by the Contractor and each respective transmittal form (ENG Form 4025) shall be signed and dated certifying that the accompanying submittal complies with the contract requirements.  Proposed deviations from the contract requirements shall be clearly identified.  Submittals shall include items such as: Contractor’s, manufacturer’s, or fabricator’s drawings; descriptive literature including (but not limited to) catalog cuts, diagrams, operating charts or curves; test reports; test cylinders; samples; O&M manuals including parts list; certifications; warranties and other such required submittals.  Submittals requiring Government approval shall be scheduled and made prior to the acquisition of the material or equipment covered thereby.

3.2	SUBMITTAL REGISTER (ENG FORM 4288)

Attached at the end of this section is the Submittal Register (ENG Form 4288), listing each item of equipment and material for which submittals are required by the specifications.  Columns “d” thru “q” have been completed by the Government.  The Contractor shall complete columns “r” and “s” thru “u.”  The Contractor shall review, complete and submit, in triplicate, the completed register listing all submittals and dates, to the RE at the CQC coordination meeting.  In addition to those items listed in ENG Form 4288, the Contractor shall furnish submittals for any deviations from the plans and specifications.  The scheduled need date shall be recorded on the register for each item for control purposes.  The approved submittal register will become the scheduling document and will be used to control submittals throughout the life of the contract.  Scheduling shall be coordinated with the approved network analysis system.  The Contractor’s CQC system manager shall review the listing at least every 30 days and task appropriate action to maintain an effective system.  Copies of updated or corrected listings shall be submitted to the RE at least every 60 days, in triplicate.  Payment will not be made for any material or equipment which does not comply with contract requirements.

3.3	SCHEDULING

a.	Coordinate scheduling, sequencing, preparing, and processing of submittals with performance of work so that work will not be delayed by submittal processing.  Allow for potential requirements to resubmit.

b.	Except as specified otherwise, allow review period, beginning with receipt by approving authority, which includes at least 30 working days for submittals for RE approval.  Period of review for submittals with government approval begins when the Government receives submittal from CQC organization.  Period of review for each resubmittal is the same as for initial submittal.  No delays or damages will be allowed for time lost in late submittals.

3.4	TRANSMITTAL FORM (ENG FORM 4025)

The transmittal form (ENG Form 4025) attached to this section of the specification shall be used for submitting submittals in accordance with the instructions provided by the FAA.  This form shall be properly completed by filling out all the heading blank spaces and identifying each item submitted.  Special care shall be exercised to ensure proper listing of the specification paragraphs and/or sheet number of the contract drawings pertinent to the data submitted for each item.

3.5	SUBMITTAL PROCEDURE

Submittals referred to in the text may use the wording “submitted to the RE,” submittals will be reviewed as indicated in column “r” of the Submittal Register (ENG Form 4288).  Submittals shall be made to the addresses set forth below.  Submittals shall be made as follows:

3.5.1	Submittals for FAA (Government) Approval

The Contractor shall submit to the FAA, by the most expedient means, a total of seven copies of shop drawings and other submittals listed on the Submittals Register (ENG Form 4288) as requiring technical review by the FAA.  All copies shall be submitted to the RE.  The Contractor shall be responsible for all costs incurred in transmitting the required information for review in the submittal process.

FAA mailing address:

FAA William J. Hughes Technical Center

Attn: Mr. Greg Falzetta

Environmental and Safety Subteam, AJP-7932

Atlantic City International Airport

Atlantic City, NJ 08405

3.5.2	Submittals for Architect/Engineer Approval

As necessary, the FAA shall submit review copies to the Architect/Engineer (A/E).  If directed by the FAA, the Contractor shall submit to the Architect/Engineer (A/E), by the most expedient means, copies of shop drawings and other submittals listed on the Submittal Register (Eng Form 4288).  The Contractor shall be responsible for all costs incurred in transmitting the required information for review in the submittal process.

A/E mailing address:

TRC Environmental Corporation

Attn: Mr. Carl Stopper

21 Griffin Road North

Windsor, CT 06095

3.5.3	Deviations

For submittals which include proposed deviations requested by the Contractor, the column “variation” of ENG Form 4025 shall be checked.  The Contractor shall set forth in writing the reason for any deviations and annotate such deviations on the submittal.  The Government reserves the right to rescind inadvertent approval of submittals containing unnoted deviations.

3.5.4	Completion of Work

Upon completing the work under this contract, the Contractor shall furnish one set of prints of all shop drawings as finally approved.  These drawings shall show all changes and revisions made up to the time the items covered by the shop drawings are completed and accepted.

3.6	CONTROL OF SUBMITTALS

The Contractor shall carefully control his procurement operations to ensure that each individual submittal is made on or before the Contractor schedule submittal date shown on the approved “Submittal Register.”

3.7	GOVERNMENT APPROVED SUBMITTALS

Upon completion of review of submittals requiring Government approval, the submittals will be identified as having received approval by being so stamped and dated.  Five (5) copies of the submittal will be retained by the RE and the remaining copies of the submittal will be returned to the Contractor.

END OF SECTION

SECTION 01380

PROJECT PHOTOGRAPHS AND VIDEO

PART 1	GENERAL

1.1		SCOPE OF WORK

This section describes project photography and video taping to be performed and submitted by the Contractor in order to document construction and remediation activities.

1.2		GENERAL REQUIREMENTS

1.2.1		The documentation shall provide a complete record of events including, but not limited to, progression of work, potential and actual problems, solutions to problems, and actual conditions which may vary from contract conditions.

1.2.2		The Contractor shall furnish a digital camera and a digital video recorder to record important features of the site prior to the commencement of work, during remediation, and after the work has been completed.  Photographs shall be submitted both electronically and stored on CDs or floppy disks (for subsequent file locking by FAA) and as actual hard copy prints.

1.2.3		Each photograph shall be in color.  Photographs and videos shall be of clear professional quality.  A scale or object of known and stated dimensions, and date of photograph, shall be included within the frame of all subjects photographed.  All photos should be labeled as to location and purpose, description, problem, etc. in a manner which allows quick referencing (e.g., place label or identification number immediately adjacent to photograph.

1.2.4		Video recordings shall be DVD format, and labeled sequentially with project name and range of dates video stamped on each individual DVD.  DVD shall be narrated by the Contractor describing what is being viewed, date, potential and actual problems, solutions, etc.

1.2.5		All photographs and DVDs are U.S. Government property and shall not be released by the Contractor to the public or news media.  Photographs shall be displayed at a maximum of two to a page, with pages (minimum photograph size shall be 3” x 5”) punched to fit standard three-ring binders.  The description of the photo (label) must be visible adjacent to the photograph.  Provide binders in sufficient size and quantity to hold all photographs.  Provide at least one binder per set of prints.  Do not combine sets into the same binder.

1.2.6		Prints shall be color of standard quality, sized as described herein and of single weight photograph paper.  Each print shall show appropriate identification and other information as directed by the Resident Engineer (RE).  Identification information on each print shall include: name and location of project, item/action being photographed, General Contractor, orientation of view, date and time of exposure, and name and address of photographer.

1.3		SUBMITTALS

The following shall be submitted in accordance with Section 01330, “Submittal Procedures”.

1.3.1		SD-08 Statements

Photography Plan; GA

The Contractor shall submit for approval each month his photography plan, which shall include the following information: items to be photographed and video recorded, location and views of the photographs and video that will be taken.

1.3.2		SD-01 Data

1.3.2.1		Construction Photograph (Electronic Files and Prints); GA.

        - Initial, Semi-Final and Final Photographs.

The Contractor shall submit to the RE three sets of prints of each photograph taken prior to the commencement of work, after the completion of site work, and after completion of all work, along with the electronic files within 14 calendar days after taking the photographs, or as approved by the RE.

        - Monthly Photographs

The Contractor shall submit to the RE three prints of each monthly progress photograph, along with the electronic files, within 14 calendar days after taking the photographs, or as approved by the RE.

1.3.2.2		Videos; GA

The Contractor shall submit initial, monthly, semi-final, and final video recordings.

Three copies of each unedited video recording shall be turned over to the RE within 14 calendar days after completing the video recording, or as directed by the RE.

Three copies of edited video recording shall be turned over to the RE within 14 calendar days after completing the video footage, or as directed by the RE.

PART 2	PRODUCTS

Not applicable

PART 3	EXECUTION

3.1		INITIAL PHOTOGRAPHS AND VIDEO

The location of initial photographs will be designated by the RE.  Each video recording of initial site conditions shall include alternative views of the items photographed.  The locations of the video recorded will be designated by the RE.  The running time for initial conditions in each edited video shall be approximately 45 minutes.  The Contractor shall take a minimum of 50 photographs including views of the following:

a.	Recharge Bed Area

b.	Expanded Sprinkler System Area

- Proposed Piping Routes

3.2		MONTHLY PROGRESS PHOTOGRAPHS AND VIDEO

After construction operations have been started at the site, the Contractor shall record the remediation with photographs and video recordings.  A minimum of 60 photographs shall be taken each month.  The monthly minimum edited video running time shall be 30 minutes and unedited video running time shall be 2 hours, 80 percent of which shall be of site work.  The progress photographs and video shall include coverage of:

a.	Construction of temporary facilities (including office trailer) and utilities

b.	Construction/installation of soil erosion and sediment control measures

c.	Unanticipated events

d.	Bed construction

e.	Construction equipment

f.	Sprinkler system piping and sprinkler head installation

g.	Conveyance piping installation

h.	Control vaults and controls

i.	Bridge Installation

j.	Direction Drilling Activities

k.	Electrical and control system installation

l.	Monitoring well installation

m.	Site stabilization

3.3		SEMI-FINAL AND FINAL PHOTOGRAPHS AND VIDEO FILM

After the completion of all work, the Contractor shall take a minimum of 100 photographs and produce approximately 30-minutes of edited video film including views of the completed site.  At the completion of all work, the locations of the final photographs shall include:

- Unanticipated events

- Restored laydown areas

- Completed bed area

- Sprinkler system piping and sprinkler head installation

- Monitoring wells

- Control vaults and controls

- Electrical and control system installation

3.4		FREQUENCY

The photography and video taping efforts shall be spaced out intermittently throughout the given period as appropriate over each activity to provide views representative of the entire project.

3.5		VIEWS REQUIRED

3.5.1		Prints and video shall illustrate condition and location of work and the state of progress.

3.5.2		Consult with the RE at each period of photography for recommendations concerning views required.

END OF SECTION

SECTION 01400

CONTRACTOR QUALITY CONTROL

PART I	GENERAL

1.1	SUMMARY

The work covered by this section consists of establishing and maintaining an effective quality control system throughout the contract period.

1.2	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by basic designation only.

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM D 3740	(2001) Minimum Requirements for Agencies Engaged in the Testing and/or Inspection of Soil and Rock as Used in Engineering Design and Construction

ASTM E 329	(2000) Agencies Engaged in the Testing and/or Inspection of Materials Used in Construction.

1.3	SUBMITTALS

The following shall be submitted in accordance with Section 01330, “Submittal Procedures.”

SD-08	Statements

Final Quality Control Plan; GA

The Contractor shall furnish for review by the Government, not later than 10 days after receipt of Notice to Proceed, the Contractor Quality Control (CQC) Plan proposed to implement the requirements of the Contract. The plan shall identify personnel, procedures, instructions, tests, records, and forms to be used.

Interim Quality Control Plan; GA

The Government will consider an interim plan for this first 30 days of operation.  This plan shall be submitted at the CQC Coordination Meeting.

Notification of Proposed Changes to the Quality Control Plan; GA

Proposed changes to the CQC Plan shall be submitted for approval a minimum of seven calendar days prior to any proposed change.

SD-18	Records

Daily QC Records; GA

The original and one copy of these records in report form shall be furnished to the Government daily within 24 hours after the date covered by the report, except that reports need not be submitted for days on which no work is performed.  As a minimum, one report shall be prepared and submitted for every seven days of no work and on the last day of no work period.  All calendar days shall be accounted for throughout the life of the contract.  The first report following a day of no work shall be for that day only.  Reports shall be signed and dated by the CQC Engineer.  The report from the CQC Engineer shall include copies of test reports and copies of reports prepared by all subordinate quality control personnel.

PART 2	PRODUCTS

Not Applicable

PART 3	EXECUTION

3.1	GENERAL

The Contractor is responsible for quality control and shall establish and maintain an effective system in compliance with the Contract. The quality control system shall consist of plans, procedures, and organization necessary to produce an end product which complies with the contract requirements.  The system shall cover construction operations, both on-site and off-site, and shall be keyed to the proposed construction sequence.

3.2	QUALITY CONTROL PLAN

3.2.1	General

Construction will be permitted to begin only after acceptance of the CQC Plan or acceptance of an interim plan applicable to the particular feature of work to be started.  Work outside of the features of work included in an accepted plan will not be permitted to begin until acceptance of a CQC Plan or another interim plan containing the additional features of work to be started.

3.2.2	Content of the CQC Plan

The CQC Plan shall include, as a minimum, the following to cover all construction operations, both on-site and off-site, including work by subcontractors, fabricators, suppliers and purchasing agents:

a.	A description of the quality control organization, including a chart showing lines of authority and acknowledgment that the CQC staff shall implement the three phase control system for all aspects of the work specified.  The staff shall include a CQC Engineer who shall report to the Project Manager or someone higher in the Contractor's organization.  Project Manager in this context shall mean the individual with responsibility for the overall management of the project including quality and production.

b.	The name, qualifications (in resume format), duties, responsibilities and authorities of each person assigned a QC function.

c.	A copy of the letter to the Engineer signed by an authorized official of the firm which describes the responsibilities and delegates sufficient authorities to adequately perform the functions of the CQC Engineer including authority to stop work which is not in compliance with the contract.  The CQC Engineer shall issue letters of direction to all other various quality control representatives outlining duties, authorities and responsibilities.  Copies of these letters shall also be furnished to the Government.

d.	Procedures for scheduling, reviewing, certifying, and managing submittals, including those of subcontractors, off-site fabricators, suppliers and purchasing agents.  These procedures shall be in accordance with Section 01330, “Submittal Procedures.”

e.	Control, verification, and acceptance testing procedures for each specific test required by the Contract or Project Specification including:  the test name, Specification or Contract paragraph requiring the test, feature of work to be tested, test frequency, acceptance or passing criteria, and person responsible for each test.  (Laboratory facilities must be Corps of Engineers certified if required by the Contracting Officer’s Technical Representative (COTR)).

f.	Procedures for tracking preparatory, initial, and follow-up control phases and control, verification and acceptance tests including documentation.

g.	Procedures for tracking construction deficiencies from identification through acceptable corrective action.  These procedures will establish verification that identified deficiencies have been corrected.

h.	Reporting procedures, including proposed reporting formats.

i.	A list of the definable features of work.  A definable feature of work is a task which is separate and distinct from other tasks and has separate control requirements.  It could be identified by different trades or disciplines, or it could be work by the same trade in a different environment.  Although each section of the specifications may generally be considered as a definable feature of work, there are frequently more than one definable feature under a particular section.  This list will be agreed upon during the CQC coordination meeting.

3.2.3	Acceptance of Plan

Acceptance of the Contractor’s plan is required prior to the start of construction.  Acceptance is conditional and will be predicated on satisfactory CQC performance during the construction.  The Government reserves the right to require the Contractor to make changes in his CQC Plan and operations including removal of personnel, as necessary, to obtain the quality specified.

3.2.4	Notification of Changes

After acceptance of the QC Plan, the Contractor shall notify the RE in writing a minimum of seven calendar days prior to any proposed change.  Proposed changes are subject to acceptance by the RE.

3.3	CQC COORDINATION MEETING

After the Preconstruction Conference, before start of construction and prior to acceptance by the Government of the Quality Control Plan, the Contractor shall meet with the Contracting Officer (CO) or Authorized Representative and discuss the Contractor’s quality control system.  During the meeting, a mutual understanding of the system details shall be developed, including the forms for recording the CQC operations, control activities, testing, administration of the system for both on-site and off-site work, and the interrelationship of Contractor’s Management and control with the Government’s Quality Assurance.  Minutes of the meeting will be prepared by the Government and signed by both the Contractor and the CO or authorized representative.  The minutes shall become a part of the contract files.  There may also be occasions when subsequent conferences will be called by either party to reconfirm mutual understanding and/or address deficiencies in the CQC system or procedures which may require corrective action by the Contractor.

3.4	QUALITY CONTROL ORGANIZATION

3.4.1	CQC Engineer

The Contractor shall identify an individual, within his organization at the site of the work who shall be responsible for overall management of CQC and have the authority to act in all CQC matters for the Contractor.  This CQC Engineer shall be on the site at all times during construction and will be employed by the Contractor, except as noted in the following.  An alternate for the CQC Engineer will be identified in the plan to serve in the event of the CQC Engineer’s absence.  Period of absence may not exceed two weeks at any one time, and not more than 30 workdays during a calendar year.  The requirements for the alternate will be the same as for the designated CQC Engineer.

3.4.2	CQC Organizational Staffing

When necessary, the Contractor shall provide CQC staff with complete authority to take any action necessary to ensure compliance with the contract.  The CQC Engineer or staff member shall be at the site of the work at all times during progress.

3.4.2.1	CQC Staff

Following are the minimum requirements for the CQC staff.  These minimum requirements will not necessarily assure an adequate staff to meet the CQC requirements at all times during construction.  The actual size of the CQC staff may vary during any specific work period to cover the needs of the work period.  When necessary for a proper CQC organization, the Contractor shall add additional staff at no cost to the Government.  This listing of minimum staff in no way relieves the Contractor of meeting the basic requirements of quality construction in accordance with contract requirements.  All CQC staff members will be subject to acceptance by the RE.

3.4.2.2	CQC Engineer

Since the majority of the project QC issues shall be related to excavation, placement of soils, backfilling, compaction, and identification of different soil strata, the CQC Engineer should have experience with similar Civil Engineering Projects.

3.4.2.3	Supplemental Personnel

As required, a staff shall be maintained under the direction of the CQC Engineer such that the CQC Engineer and staff can perform all QC activities.  The staff must be of sufficient size to ensure adequate QC coverage of all work phases, work shifts, and work crews involved in the construction.  These personnel may perform other duties, but must be fully qualified by experience and technical training to perform their assigned QC responsibilities and must be allowed sufficient time to carry out these responsibilities.  The QC plan will clearly state the duties and responsibilities of each staff member.  It is assumed that the CQC Engineer shall perform the majority of the QC tasks.

3.4.3	Organization Changes

The Contractor shall obtain RE’s acceptance before replacing any member of the CQC staff.  Requests shall include the names, qualifications, duties, and responsibilities of each proposed replacement.

3.5	CONTROL

Contractor Quality Control is the means by which the Contractor assures that the construction, to include that of subcontractors and suppliers, complies with the requirements of the contract.  The controls shall be adequate to cover all construction operations, including both on-site and off-site fabrication, and shall be keyed to the proposed construction sequence.  The controls shall include at least three phases of control to be conducted by the CQC Engineer for all definable features of work, as follows:

3.5.1	Preparatory Phase

This phase shall be performed prior to beginning any work on each definable feature of work and shall include:

a.	A review of each paragraph of applicable specifications.

b.	A review of contract plans.

c.	A check to assure that all materials and/or equipment have been tested, submitted and approved.

d.	A check to assure that provisions have been made to provide required control inspection and testing.

e.	Examination of the work area to assure that all required preliminary work has been completed and is in compliance with the contract.

f.	A physical examination of materials, equipment, and sample work to assure that they are on hand, conform to approved shop drawings or submittal data, and are properly stored.

g.	A review of the appropriate activity hazard analysis to assure safety requirements are met.

h.	Discussion of procedures for constructing the work including repetitive deficiencies.  Document construction tolerances and workmanship standards for that phase of work.

i.	A check to ensure that the portion of the plan for the work to be performed has been accepted by the RE.

j.	The Government shall be notified at least 24 hours in advance of beginning any of the required action of the preparatory phase.  This phase shall include a meeting conducted by the CQC Engineer and attended by the superintendent, other CQC personnel (as applicable), and the foreman responsible for the definable feature. The results of the preparatory phase actions shall be documented by separate minutes prepared by the CQC Engineer and attached to the daily QC report.  The Contractor shall instruct applicable workers as to the acceptable level of workmanship required in order to meet contract specifications.

3.5.2	Initial Phase

This phase shall be accomplished at the beginning of a definable feature of work.  The following shall be accomplished:

a.	A check of preliminary work to ensure that it is in compliance with contract requirements.  Review minutes of the preparatory meeting.

b.	Verification of full contract compliance.  Verify required control inspection and testing.

c.	Establish level of workmanship and verify that it meets minimum acceptable workmanship standards.  Compare with sample panels is appropriate.

d.	Resolve all differences.

e.	Check safety to include compliance with and upgrading of the safety plan and hazard analysis.  Review the activity analysis with each worker.

f.	The Government shall be notified at least 24 hours in advance of beginning the initial phase.  Separate minutes of this phase shall be prepared by the CQC Engineer and attached to the daily QC report.  Exact location of initial phase shall be indicted for future reference and comparison with follow-up phases.

g.	The initial phase shall be repeated for each new crew to work on-site, or any time acceptable specified quality standard are not being met.

3.5.3	Follow-Up Phase

Daily checks shall be performed to assure continuing compliance with contract requirements, including control testing, until completion of the particular feature of work. The checks shall be made a matter of record in the CQC documentation.  Final follow-up inspections shall be conducted and all deficiencies corrected prior to the start of additional features of work which may be affected by the deficient work.  The Contractor shall not build upon or conceal nonconforming work.

3.5.4	Additional Preparatory and Initial Phase

Additional preparatory and initial phases may be conducted on the same definable features of work as determined by the Government if the quality of ongoing work is unacceptable; or if there are changes in the applicable QC staff or in the on-site production supervision or work crew; or if work on a definable feature is resumed after a substantial period of inactivity, or if other problems develop.

3.6	TESTS

3.6.1	Testing Procedure

The Contractor shall perform tests specified or required to verify that control measures are adequate to provide a product which conforms to contract requirements.  Testing includes operation and/or acceptance tests when specified.  The Contractor shall procure the services of a Corps of Engineers approved testing laboratory if required by the RE, or establish an approved testing laboratory at the project site.  If FAA does require a Corps certified laboratory, but the Contractor desires the services of a laboratory which is not Corps of Engineers approved, then he will be responsible for all costs for acquiring the required approvals.  A list of tests to be performed shall be furnished as part of the CQC Plan.  The list shall give the test name, frequency, specification paragraph containing the test requirements, the personnel and laboratory responsible for each type of test, and an estimate of the number of tests required.  The Contractor shall perform the following activities and record and provide the following data:

a.	Verify that testing procedures comply with contract requirements.

b.	Verify that facilities and testing equipment are available and comply with testing standards.

c.	Check test instrument calibration data against certified standards.

d.	Verify that recording forms and test identification control number system, including all of the test documentation requirements, have been prepared.

e.	Results of all tests taken, both passing and failing tests, shall be recorded on the Quality Control report for the date taken.  Specification paragraph reference, location where tests were taken, and the sequential control number identifying the test shall be given.  Actual test reports may be submitted later, if approved by the RE, with a reference to the test number and data taken.  An information copy of tests performed by an off-site or commercial test facility shall be provided directly to the RE.  Failure to submit timely test reports, as stated, may result in nonpayment for related work performed and disapproval of the test facility for this contract.

3.6.2	Testing Laboratories

3.6.2.1	Capability Check

The Government reserves the right to check laboratory equipment in the proposed laboratory for compliance with the standards set forth in the contract specifications and to check the laboratory technician’s testing procedures and techniques.  Laboratories utilized for testing soils, concrete, asphalt and steel shall meet criteria detailed in ASTM D 3740 and ASTM E 329.

3.6.2.2	Capability Recheck

If the selected laboratory fails the capability check, the Contractor will be assessed a charge to reimburse the Government for each succeeding recheck of the laboratory or the checking of a subsequently selected laboratory.  Such costs will be deducted from the contract amount due the Contractor.

3.6.3	On-Site Laboratory and Field Testing Equipment

The Government reserves the right to utilize the Contractor’s control testing laboratory and field equipment to make assurance tests and to check the Contractor’s testing procedures, techniques, and test results at no additional cost to the Government.

3.6.4	Split Samples

The Government reserves the right to require split samples for quality assurance tests at an independent commercial or Government laboratory.

3.6.5	Furnishing or Transportation of Samples for Testing

Costs incidental to the transportation of samples or materials shall be borne by the Contractor.  If applicable, samples of materials for test verification and acceptance by the Government shall be delivered to the RE at the following address:

For delivery by mail:   FAA William J. Hughes Technical Center

Attn: Mr. Greg Falzetta

Environmental and Safety Subteam, AJP-7932

Atlantic City International Airport

Atlantic City, NJ 08405

For other deliveries;	Same as above

The RE contact shall be provided to the Contractor prior to initiation of site activities.  Coordination for each specific test, exact delivery location and dates will be made through the RE.

3.7	COMPLETION INSPECTION

At the completion of all work or any increment thereof established by a completion time or stated elsewhere in the specifications, the CQC System Manger shall conduct an inspection of the work and develop a “punch list” of items which do not conform to the approved plans and specifications.  Such a list of deficiencies shall be included in the CQC documentation, as required by the paragraph: “Documentation” below, and shall include the estimated date by which the deficiencies will be corrected.  The CQC Engineer or staff shall make a second inspection to ascertain that all deficiencies have been corrected and so notify the Government.  The inspections and any deficiency corrections required by this paragraph shall be accomplished within the time stated for completion of the entire work or any particular increment thereof if the project is divided into increments by separate completion dates.

3.8	DOCUMENTATION

The Contractor shall maintain current records of quality control operations, activities, and tests performed including the work of subcontractors and suppliers.  These records shall be on the required form and shall include factual evidence that required quality control activities and/or tests have been performed, including but not limited to the following:

a.	Contractor/subcontractor and their area of responsibility.

b.	Operating plant/equipment with hours worked, idle, or down for repair.

c.	Work performed each day, giving location, description, and by whom.  When Network Analysis (NAS) is used, identify each phase of work performed each day by NAS activity number.

d.	Test and/or control activities performed with results and references to specifications/plans requirements.  The control phase shall be identified (e.g., preparatory, initial, follow-up).  List deficiencies noted along with corrective action.

e.	Materials received with statement as to its acceptability and storage.

f.	Identify submittals reviewed, with contract reference, by whom, and action taken.

g.	Off-site surveillance activities, including actions taken.

h.	Job safety evaluations stating what was checked, results, and instructions or corrective actions.

i.	List instructions given/received and conflicts in plans and/or specifications.

j.	Contractor's verification statement.

k.	These records shall indicate a description of trades working on the project; the number of personnel working; the weather conditions encountered; and any delays encountered.  These records shall cover both conforming and deficient features and shall include a statement that equipment and materials incorporate in the work and workmanship comply with the contract.

3.9	QUALITY CONTROL REPORT FORM

The required form for recording quality control activities shall be provided by the FAA.

3.10	NOTIFICATION OF NONCOMPLIANCE

The RE will notify the Contractor of any detected noncompliance with the foregoing requirements.  The Contractor shall, after receipt of such notice, immediately take corrective action.  Such notice when delivered to the Contractor at the site of the work shall be deemed sufficient for the purpose of notification.  If the Contractor fails or refuses to comply promptly, the RE may issue an order stopping all or part of the work until satisfactory corrective action has been taken.  No part of the time lost due to any such stop orders shall be made the subject of claim for extension of time or for excess costs or damages by the Contractor.

END OF SECTION

SECTION 01500

CONSTRUCTION FACILITIES

PART 1	GENERAL

1.1	SUBMITTALS

1.1.1	SD-01 Manufacturer’s Catalog Data

a.	Site Trailer; GA

1.2	TEMPORARY UTILITIES

Reasonable amounts of the following utilities will be made available to the Contractor without charge.

Water and Electricity

The Contractor shall pay all costs incurred in connecting, converting, and disconnecting utilities.  The Contractor shall make all connections and provide disconnects, fuse protection, overhead and buried power feed wires, transformers, and shall make disconnections and remove temporary components and feed wires upon project completion.  Sufficient electrical service will be made available to power one site trailer.  The Contractor shall ensure that new utility lines are complete, except for the connection, before interrupting existing service.  The utility interruption to electric service shall be considered utility cutovers.  Such interruption shall be further limited to four (4) hours.  This limit includes time for deactivation and reactivation.  The Contractor shall contact the FAA’s electrical engineering personnel to determine the most appropriate temporary connection point on the adjacent FAA overhead electrical power lines.

The only water available on site will be from an onsite injection well (RP-IW1) that has a capacity of up to approximately 90 gpm.  If the Contractor desires to use water from this well, the Contractor shall be responsible for providing all necessary pumps and generators to pump water from the well.  All submersible pumps, hose, and other components placed in the well shall be properly decontaminated (to the satisfaction of the FAA) prior to their installation.  The water shall be considered non-potable.

Ensure that new utility lines are complete, except for the connection, before interrupting existing service.

1.3	TEMPORARY SANITARY FACILITIES

Provide adequate sanitary conveniences (portable chemical toilet with hand washes or sanitizers) of a type approved for the use of persons employed on the worksite, properly secluded from public observation, and maintained in such a manner as required or approved by the Resident Engineer (RE).  Sanitary conveniences shall be provided at the site trailer. The facilities shall be secluded from public observation with stockade type fence or chain link fence with privacy slats.  Maintain these conveniences at all times without nuisance.  Upon completion of the work, remove the conveniences from the premises, leaving the premises clean and free from nuisance.

1.4	ODOR AND PEST CONTROL

Include provisions for pest control and elimination of odors.

1.5	PROJECT SIGN

Within 15 days after the commencement of work, provide one project identification sign at the Recharge Bed site.  Construct the sign using 4-foot by 8-foot by 2-inch thick exterior grade plywood, preservative-treated lumber, and galvanized hardware.  Paint the plywood portion of the sign using one coat of lead-free alkyd oil primer paint and two coats of exterior enamel, but do not paint the preservative-treated lumber portion of the sign. Lettering and details of construction shall be as indicated.  Maintain throughout the life of the project.  Upon completion of the project, remove the sign from the SITE.

On the project sign, list two points of contact by name and telephone number

1.6	SITE TRAILER

The Contractor is responsible for providing one site trailer.  The trailer shall be suitably painted and kept in a good state of repair.  Failure of the Contractor to maintain the trailer in good condition will be considered sufficient reason to require its removal.  A sign not smaller than 24 inches by 24 inches shall be conspicuously placed on the trailer depicting the company name, business phone number, and emergency phone number.  The trailer shall be anchored to resist high winds and must meet applicable state or local standards for anchoring mobile trailers. The trailer shall be furnished with necessary steps and anchors.

The site trailer shall be approximately 10 feet x 40 feet and shall be located as shown on the Contract Drawings.  Provide a weather-tight structure with adequate heating and cooling, lighting, ventilation, a 4-foot by 8-foot plan table, a standard size office desk and chair, and working cellular communications facilities.  Provide either a 1,500-watt radiant heater and a window-mounted air conditioner rated at 9,000 BTUs minimum or a window-mounted heat pump of the same minimum heating and cooling ratings.  Provide a door with a cylinder lock and windows with locking hardware. Furnish all necessary utilities.  File Contractor quality control records for ongoing work in the field office trailer and make available at all times to the Government.  After completion of the work, remove the entire structure from the SITE.

1.7	IDENTIFICATION OF CONTRACTOR VEHICLES

Each Contractor-provided vehicle and towed trailer shall show the Contractor’s name so that it is clearly visible on both front doors of the vehicle and both sides of a towed trailer and shall at all times display a valid state license plate and safety inspection sticker.  Contractor vehicles operated on Government property shall be maintained in good state of repair.

PART 2	PRODUCTS

Not Used

PART 3	EXECUTION

3.1		TRAILER INSTALLATION AND REMOVAL

The Contractor is responsible for providing, installing, connecting to the utilities, and maintaining the Site trailer.  The Contractor shall remove the trailer upon completion of the project.

  - UTILITY LOCATION

Utility markouts are required prior to any excavation work.  The Contractor is responsible for contacting the NJ One Call Utility Hotline.  Additionally, the contractor shall notify the RE of any excavation work so that the Center Operations and Maintenance Services (COMS) contractor can mark out the “private” utility lines.  The Contractor shall notify the RE at least seven days prior to beginning any excavation activities.

END OF SECTION

## SECTION 01560

ENVIRONMENTAL PROTECTION

PART 1	GENERAL

# 1.1	SUMMARY

This section covers the furnishing of all labor, material, and equipment and performing all work required for the protection of the environment during construction operations except for those measures set forth in other sections of these Specifications.

For the purpose of this Specification, environmental protection is defined as the retention of the environment in its natural state to the greatest extent possible during project construction and to enhance the natural appearance in its final condition.  Environmental protection requires consideration of air, water, and land resources and involves noise, solid waste management and management of other pollutants.  In order to prevent, and to provide for abatement and control of any environmental pollution arising from the construction activities in performance of this contract, the Contractor and his subcontractors shall comply with all applicable federal, state, and local laws and regulations and shall obtain all necessary permits required by same.

# 1.2	REFERENCES

APPLICABLE PUBLICATIONS:  The publications listed below are integral to this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

U.S. DEPARTMENT OF LABOR, OCCUPATIONAL SAFETY AND HEALTH ADMINISTRATION (OSHA)

29 CFR 1910.12	Subpart B - Adoption and Extension of Established Federal Standards, Construction Work

29 CFR 1910.94	Subpart G - Occupational Health and Environmental Control, Ventilation

29 CFR 1910.95	Subpart G - Occupational Health and Environmental Control, Occupational Noise Exposure

29 CFR 1910.106	Subpart H - Hazardous Materials, Flammable and Combustible Liquids

29 CFR 1910.109	Subpart H - Hazardous Material, Explosives and Blasting Agents

29 CFR 1910.146	Permit-required Confined Spaces

29 CFR 1910.120	Hazardous Waste Operations and Emergency Response

29 CFR 1910.134 	Subpart I - Personal Protective Equipment, Respiratory Protection

29 CFR 1910.178	             Subpart N - Materials Handling and Storage,

Powered Industrial Truck

29 CFR 1910.1000	Subpart Z- Toxic and Hazardous Substances, Air Contaminants

29 CFR 1910.1200	Subpart Z - Toxic and Hazardous Substances Hazard Communication

29 CFR 1926.21	Subpart C - Safety Training and Education

29 CFR 1926.350	Subpart J - Welding and Cutting

ENVIRONMENTAL PROTECTION AGENCY (EPA) REGULATIONS

40 CFR 51	Federal Conformity Determination for Federal Actions

40 CFR 173	Shippers – General Requirements for Shipments and Packaging

40 CFR 761	Polychlorinated Biphenyls (PCBs) Manufacturing, Processing, Distribution in Commerce, and Use Prohibitions

40 CFR 261	Identification and Listing of Hazardous Waste

40 CFR 262	Standards Applicable to Generators of Hazardous Waste

40 CFR 263	Standards Applicable to Transporters of Hazardous Waste

40 CFR 264	Standards for Owners and Operators of Hazardous Waste Treatment, Storage, and Disposal Facilities

40 CFR 300	National Contingency Plan

49 CFR 178	Specifications for Packaging

NEW JERSEY ADMINISTRATIVE CODE (NJAC)

NJAC 2:90	State Soil Conservation Committee

NJAC 7:1E	Discharges of Petroleum and Other Hazardous Substances

NJAC 7:9	Water Pollution Control

NJAC 7:10	Safe Drinking Water Act

NJAC 7:14A	The New Jersey Pollutant Discharge Elimination System

NJAC 7:14B	Underground Storage Tanks

NJAC 7:18	                         Regulations Governing the Certification of

Laboratories and Environmental Measurements

NJAC 7:19	Water Supply Allocation Permits

NJAC 7:26	Solid Waste

NJAC 7:26G	Hazardous  Waste

NJAC 7:27	Bureau of Air Pollution Control Regulations

NJAC 7:30	Pesticide Control Code

NJAC 7:50	Pinelands Comprehensive Management Plan

#### FEDERAL AVIATION ADMINISTRATION (FAA) ORDERS

1050.1D	Policies and Procedures for Considering Environmental Impacts

1050.10B	                          Prevention, Control, and Abatement of

Environmental Pollution at FAA Facilities

1050.17	Airway Facilities Environmental and Safety Compliance Program

3900.13B	Personal Protective Equipment and Clothing

3900.24A	Accident and Fire Reporting

3900.25	Respiratory Protection Program

FAA WJH TECHNICAL CENTER ORDERS

3900.55	Occupational Safety and Health

ARMY CORPS OF ENGINEERS (COE)

COE EM-385-1-1	Corps of Engineers Safety and Health Requirements Manual

1.3	DEFINITIONS

Debris

Combustible and noncombustible wastes such as ashes; waste materials resulting from construction, demolition, maintenance, or repair work; leaves; and tree trimmings.

Discharge

Any intentional or unintentional action or omission resulting in the releasing, spilling, leaking, pumping, pouring, emitting, emptying or dumping of hazardous substances, hazardous wastes, hazardous materials, or pollutants into surface or ground waters or onto lands from which it might flow or drain into said waters or volatilize into the air.

Drip Line

The outer most horizontal perimeter of the foliage or limbs of trees and shrubs.

Environmental Assessment (EA)

A concise public document for which a federal agency is responsible, that serves to: (a) briefly provide sufficient evidence and analysis for determining whether to prepare an environmental impact statement or a finding of no significant impact;(b) aid an agency’s compliance with the National Environmental Policy Act (NEPA) when no environmental impact statement is necessary; and, (c) facilitate preparation of an environmental impact statement when one is necessary.

Environmental Impact Statement (EIS)

A document required by the NEPA for major projects or legislative proposals significantly affecting the environment.  A tool for decision making, it describes the positive and negative effects of the undertaking and lists alternative actions.

Hazardous Substance

Such elements and compounds, including petroleum, petroleum products, pesticides, solvents and other substances as set forth NJAC 7:1E.

Hazardous Waste

Hazardous substances as defined in 40 CFR 261 or as defined by applicable state and local regulations.

Oily Waste

Petroleum products and bituminous materials.

Pollutant

Any dredged spoil, solid waste, sewage, garbage, refuse, oil, grease, sewage sludge, munitions, chemical wastes, biological materials, thermal waste, wrecked or discarded equipment, rock, sand, construction waste or runoff, or other residue discharged to the land, ground waters or surface waters.

Rubbish

Combustible and noncombustible wastes such as paper, boxes, glass, crockery, metal, lumber, cans, and bones.

Sewage

Wastes characterized as domestic sanitary sewage.

Garbage

Refuse and scraps resulting from preparation, cooking, dispensing, and consumption of food.

Sediment

Soil and other debris that has eroded and have been transported by runoff water or wind.

Solid Waste

Non-hazardous rubbish, debris, garbage, and other discarded solid materials resulting from industrial, commercial, and agricultural operations and from community activities.

Volatile Organic Substance

Any organic substances, mixture of organic and inorganic substances including, but not limited to, petroleum crudes, petroleum fractions, petrochemicals, solvents, diluents, and thinners which have vapor pressures or sums of partial pressures of substances of 0.02 pounds per square inch (one millimeter of mercury) absolute or greater measured at standard conditions of atmospheric pressure and a temperature of 60 degrees Fahrenheit; in the case of surface coating formulations, includes coalescing or other agent, regardless of vapor pressure, which evaporates from the coating during the drying phase; but does not include methane, CFC-11, CFC-12, CFC-22, FC-23, CFC-113, CFC-114 and CFC-115.

Wetlands

Those areas that are inundated or saturated by surface or ground water at a frequency and duration sufficient to support, and that under normal circumstances do support, a prevalence of vegetation typically adapted for life in saturated soil conditions.  Wetlands generally include swamps, marshes, bogs and similar areas.  National Wetland Inventory Maps, promulgated by the U.S. Fish and Wildlife Service, shall be used to identify wetlands to  be protected.  Maps are available from the Fish and Wildlife Service and the New Jersey Department of Environmental Protection.

1.4	SUBMITTALS

The following shall be submitted in accordance with Section 01330, “Submittal Procedures.”

1.4.1	SD-04 Drawings

a.	Location of Laydown and Trailer Areas, GA

Plans showing construction facilities shall be submitted for approval of the RE.

1.4.2	SD-08 Statements

a.	Environmental Permit Applications; GA

Submit four (4) copies of applicable construction permit applications(s) in accordance with Part 3 of this section.

b.	Administrative or Closeout Submittals; GA

i.	Solid Waste Disposal Permit (if required)

Submit one copy of a state and local permit or license showing such agencies’ approval of the disposal plan.

1.4.3	SD-09, Reports

a.	Environmental Protection Plan; GA

Prior to commencement of the work, the Contractor shall submit to the RE for approval four (4) copies of his proposed Environmental Protection Plan.  The Contractor shall also prepare and submit to the Cape-Atlantic Soil Conservation District for certification, a Soil Erosion and Sediment Control Plan, in accordance with Section 02112.  A copy of the approved Soil Erosion and Sediment Control Plan shall be submitted to the Resident Engineer (RE) prior to the commencement of work.

b.	Monthly Recycling Report; GA

See Paragraph 3.4.4

c.	Dirt and Dust Control Plan; GA

Prior to commencement of the work, submit truck and material haul routes along with a plan for controlling dirt, debris, and dust on base roadways.  As a minimum, identify in the plan the subcontractor and equipment for cleaning along the haul route and measures to reduce dirt, dust, and debris from roadways.

1.5	ENVIRONMENTAL PROTECTION REQUIREMENTS

Provide and maintain all environmental protection measures established, during the life of the contract.  Plan for and provide environmental protective measures to control pollution that develops during normal construction practice.  Plan for and provide environmental protective measures required to correct conditions that develop during the construction of permanent or temporary environmental features associated with the project.  Comply with all applicable federal, state, Pinelands Commission and local regulations pertaining to the environment, including but not limited to water, air, soil, sediment, wetlands, floodplains, and noise pollution.

1.5.1	Environmental Protection Plan

Five (5) days after Notice to Proceed, the Contractor shall meet with the RE to discuss the proposed environmental protection plan and to develop mutual understanding relative to the details of environmental protection, including measures for protecting natural resources, required reports, and other measures to be taken.  Approval of the Contractor’s plan for environmental protection does not relieve the Contractor of his responsibility for adequate and continuing control of pollutants.

1.5.1.1	Environmental Planning

The Contractor shall comply with all specified mitigative measures and/or environmental concerns in preparation of the Environmental Protection Plan by addressing the Environmental Assessment (EA), Environmental Impact Statement (EIS) and the preconstruction and postconstruction phases of the project.  The Contractor shall be financially and legally liable for any deviations and/or non-conformance with the applicable EA or EIS.

Fourteen (14) days after the environmental protection plan meeting, submit to the RE the proposed environmental plan for further discussion, review, and approval.

1.5.1.2	Commencement of the Work

As directed by the RE, following approval.

1.5.2	Preconstruction Survey

Prior to field mobilization perform a preconstruction survey of the project site with the RE, and take photographs showing existing environmental conditions in and adjacent to the site.  Land, streams, wetlands, and fish and wildlife resources to be protected shall be specifically noted. Photographs shall be submitted in accordance with Specification Section 01380, “Project Photographs and Video.”

1.5.3	Postconstruction Survey

Within five (5) days after completion of construction, perform a postconstruction survey of the project site with the RE, and take photographs showing existing environmental conditions in and adjacent to the site.  Land, streams, wetlands, and fish and wildlife resources that were identified in the preconstruction survey shall be specifically noted.  Photographs shall be submitted in accordance with Specification Section 01380, “Project Photographs and Video”.

1.5.4	EA and EIS Compliance

The Contractor shall comply with all specific mitigation measures and/or environmental concerns in preparation of the Environmental Protection Plan, during and after construction.  The Contractor shall be financially and legally liable and responsible for any deviations or nonconformance with the EA or EIS.  It is the contractor’s responsibility to clearly understand the requirements of this paragraph.

1.5.5	Environmental Permit Compliance

The Contractor shall construct all work in conformance with requirements or conditions of all federal, state, Pinelands Commission and local environmental permits.  It is the Contractor’s responsibility to fully understand the environmental permit requirements.  With many permits issued contingent to design specifications and drawings, no deviations from these Specifications and Drawings shall occur without written approval of the RE.  The Contractor shall be financially and legally liable for any deviations, nonconforming or in violation of applicable environmental permits.

1.6	NOTIFICATION OF NON-COMPLIANCE

The RE or RE’s representative will notify the Contractor in writing of any non-compliance with the aforementioned federal, state or local laws or regulations.  Such notice, when delivered to the Contractor or his authorized representative at the site of the work, shall be deemed sufficient for the purpose.  The Contractor shall, after receipt of such notice, immediately inform the RE of proposed corrective action and take such action as may be approved.  If the Contractor fails or refuses to comply promptly, the RE may issue an order stopping all or part of the work until satisfactory corrective action has been taken.  No part of the time lost due to any such stop orders shall be made subject of a claim for extension of time or for excess costs or damages by the Contractor.

1.7	SUBCONTRACTORS

Compliance with the provisions of this section by subcontractors will be the responsibility of the Contractor.

1.8	CLASS I ODS PROHIBITION

Class I Ozone Depleting Substances (ODS), as defined in Section 602(a) of the Clean Air Act, shall not be used in the performance of this contract, nor be provided as part of the equipment.

1.9	UNFORSEEN HAZARDOUS REGULATED MATERIAL

If material that is not indicated in the contract documents is encountered that may be dangerous to human health upon disturbance during construction operations, stop that portion of work and notify the RE immediately.  Intent is to identify hazardous substances or wastes. Within 14 calendar days the RE will determine if the material is hazardous.  If the material is not hazardous or poses no danger, the RE will direct the Contractor to proceed without change.  If the material is hazardous and handling of the material is necessary to accomplish the work, the RE will issue a modification and additional direction regarding material handling, management and disposal.

PART 2	PRODUCTS

Not used.

PART 3	EXECUTION

3.1	PROTECTION OF NATURAL RESOURCES

The natural resources within the project boundaries and outside the limits of permanent work performed under this contract shall be preserved in their present condition or be restored to a condition after completion of construction that will appear to be natural and not detract from the appearance of the project.  The Contractor shall confine his construction activities to areas defined by the Plans and Specifications.  The following additional requirements are intended to supplement the requirements of the Contract Clauses.

3.1.1	Land Resources

Except in areas indicated on the plans or specified to be cleared, the Contractor shall not deface, injure, or destroy trees or shrubs, nor remove or cut them without the authority of the RE.  Ropes, cables, or guys shall not be fastened to or attached to any existing nearby trees for anchorages unless specifically authorized.  Where such special emergency use is permitted, it shall be performed in such a manner as to avoid damage to the trees.  The Contractor shall in any event be responsible for any damage resulting from such use.

3.1.1.1	Protection

Where the possibility exists that trees may be defaced, bruised, injured, or otherwise damaged by the Contractor’s equipment or operations, the Contractor shall adequately protect such trees.  Stone, earth or other material that is displaced into uncleared areas shall be removed.  By approved excavation, remove trees with 30 percent or more of their root system destroyed.  The use of heavy equipment within the drip line of trees shall be avoided to prevent root system damage.  Boards shall not be nailed to trees that will be saved during construction.  Damaged trunks or exposed roots shall be painted immediately with a good grade of tree paint.  Tree limb removal, where necessary, will be done flush to trunk or main branch and that area painted with a good grade of tree paint.  Monuments and markers shall be protected before construction operations commence.

3.1.1.2	Replacement

Remove trees and other landscape features scarred or damaged by equipment operations, and replace with equivalent, undamaged trees and landscape features.  Tree species shall conform to Pineland Commission requirements, NJAC 7:50-6.23 et seq. Obtain RE’s approval before replacement.  Restoration of scarred and damaged trees shall be performed in an approved manner by experienced workmen.  Trees damaged beyond restoration shall be removed and disposed of under requirements for excavation.  Trees that are to be removed because of damage shall be replaced at the Contractor’s expense by nursery-grown trees of the same species or a species approved by the RE.  The size and quality of nursery-grown trees shall also be approved by the RE.  Any disturbed turfed (grassed) areas shall be seeded and mulched as directed by the RE.

3.1.1.3	Temporary Construction

Remove traces of temporary construction facilities such as haul roads, work areas, structures, foundations of temporary structures, stockpiles of excess or waste materials, and other signs of construction.  Grade temporary roads, parking areas, and similar temporarily used areas to conform with surrounding contours.  Temporary construction facilities shall not be located in or encroach wetlands, streams or wildlife management areas unless prior approval has been received from the RE.

3.1.1.4	Replanting

Contractor shall be responsible to replant trees and/or shrubs until 100% survival is attained for one complete year after construction is completed.

3.1.1.5	Location of Storage Facilities

A Contractor laydown area shall be designated by the RE.  Grade temporary roads, parking areas, and similar temporarily used areas to conform with surrounding contours.  Temporary construction facilities shall not be located in or encroach upon wetlands, streams or wildlife management areas, unless prior approval has been received from the RE.

The Contractor will not be permitted to store materials in other existing buildings on portions of the FAA property.  Storage and other construction facilities shall be confined to the approved Contractor operations and laydown areas.

3.1.2	Water Resources

The Contractor shall not pollute any streams, rivers or waterways with fuels, oils, bitumens, calcium chloride, acids, insecticides, herbicides or other hazardous or harmful materials or pollutants.  The Contractor shall investigate and comply with all applicable federal, state, county and municipal laws concerning pollution of rivers and streams.

3.1.2.1	Stream Crossings

The RE’s approval is required before any equipment will be permitted to ford live streams. In areas where frequent crossings are required, install temporary culverts or bridges.  Remove temporary culverts or bridges upon completion of work, and repair the area to its original condition or as specified.

3.1.2.2	Oily Wastes

Prevent oily or other hazardous substances from entering the ground, drainage areas, or local bodies of water.  Any tank utilized for storage shall be double walled and designed to contain the type of liquids required for the project as well as providing secondary containment. Surround all temporary fuel oil or petroleum storage tanks with a temporary earth berm of sufficient size and strength to contain 110% (by volume) of the contents of the tanks in the event of leakage or spillage.  The berm shall be covered by poly sheeting to protect the soil from contamination that might occur from the filling, draining, or failure of the tank.  All spills and discharges of oily or other hazardous substances shall be immediately reported to the RE or authorized representative in accordance with NJAC 7:1E-2.14, Standard Operating Procedures.

3.1.2.3	Wetlands Protection

Except in conformance with an issued federal, state, or Pinelands Commission permits, do not disturb, alter, fill, affect, drain, encroach upon or destroy any wetlands.  Except in conformance with an issued federal, state, or Pinelands Commission permit, do not disturb, alter, fill, affect, encroach upon, or destroy upland buffers within 300 feet of a wetlands or alter surface or ground water flows into or from wetlands.  Do not allow the discharge of petroleum products, pesticides, hazardous substances, chemicals, solid wastes, or silt into wetlands.  Do not stage construction materials, supplies, or equipment in wetlands or floodplains.

3.1.3	Fish and Wildlife Resources

Do not disturb fish and wildlife.  Do not alter water flows or otherwise significantly disturb the native habitat adjacent to the project and critical to the survival of fish and wildlife, except as indicated or specified.  Protect and do not alter, modify or affect endangered or threatened species habitat.  Protect other noted critical fish and wildlife habitats.

3.1.3.1	Wildlife Hazard Abatement

Comply with the requirements and recommendations as approved by the RE.

3.2	HISTORICAL AND ARCHAEOLOGICAL RESOURCES

Carefully protect in-place and report immediately to the RE items having possible historical and archaeological interest or human skeletal remains discovered in the course of work.  Stop work in the immediate area of the discovery until directed by the RE to resume work.  Protect monuments, markers, and works of art.  Do not disturb archaeological finds.

3.3	EROSION AND SEDIMENT CONTROL MEASURES

Soil erosion measures shall comply with the Standards for Soil Erosion and Sediment Control in New Jersey, in accordance with NJAC 2:90 et. seq., Section 02112, “Erosion and Sediment Controls,” and any other requirement specified herein.

3.3.1	Burnoff

Burnoff of the ground cover is not permitted.

3.3.2	Borrow Pit Areas

Manage and control borrow pit areas to prevent sediment from entering nearby streams or lakes.  Restore areas, including those outside the borrow pit, disturbed by borrow and haul operations.  Restoration includes grading, replacement of topsoil, and establishment of a permanent vegetative cover.  Uniformly grade side slopes of borrow pit to not more than a slope of 1 part vertical to 2 parts horizontal.  Uniformly grade the bottom of the borrow pits to provide a flat bottom, and drain by outfall ditches or other suitable means.  Stockpile topsoil removed during the borrow pit operation, and use as part of restoring the borrow pit area.

3.3.3	Protection of Erodible Soils

Immediately finish the earthwork brought to a final grade, as indicated or specified.  Immediately protect the side slopes and back slopes upon completion of rough grading.  Plan and conduct earthwork to minimize the duration of exposure of unprotected soils.

3.3.4	Temporary Protection of Erodible Soils

Use the following methods to prevent erosion and control sedimentation:

3.3.4.1	Mechanical Retardation and Control of Runoff

Mechanically retard and control the rate of runoff from the construction site.  This includes construction of silt fences, straw bale barriers, diversion ditches, benches, and berms to retard and divert runoff to protected drainage courses.

3.3.4.2	Vegetation and Mulch

Provide temporary protection on sides and back slopes as soon as rough grading is completed or sufficient soil is exposed to require erosion protection.  Protect slopes by accelerated growth of permanent vegetation, temporary vegetation, mulching, or netting.  Stabilize slopes by hydroseeding, anchoring mulch in place, covering with anchored netting, sodding, or such combination of these and other methods necessary for effective erosion control.

Seeding:  Provide new seeding where ground is disturbed.  Seed type shall be consistent with NJAC 7:50 requirements.  Include topsoil or nutriment during the seeding operation necessary to establish a suitable stand of grass.

3.3.4.3	Borrow

Borrow is permitted only in areas where suitable environmental controls are possible.

3.3.5	Seeding

Provide new seeding where ground is disturbed.  Include topsoil during the seeding operation necessary to establish a suitable stand of cover.  The seeding operation shall be as specified in Specification Section 02935, “Turf.”

3.4	CONTROL AND DISPOSAL OF SOLID AND SANITARY WASTES

Pick up solid wastes (at least daily), and place in containers which are regularly emptied (no less than once every two weeks unless approved by the RE).  Do not prepare, cook, or dispose of food on the project site.  Prevent contamination of the site of other areas when handling and disposing of wastes.  On completion, leave the areas clean.  Control and dispose of waste.

3.4.1	Disposal of Rubbish and Debris

Dispose of rubbish and debris in accordance with the requirements specified.

Remove and dispose rubbish and debris from Government property at a properly licensed facility.

3.4.2	Garbage Disposal

Place garbage in approved containers, and move to a pickup point or disposal area, where directed.

3.4.3	Sewage, Odor, and Pest Control

Provide chemical toilets or comparably effective units in accordance with Section 01500, “Construction Facilities,” and periodically empty wastes into municipal, district, or station sanitary sewage systems.  Include provisions for pest control and elimination of odors in accordance with NJAC 7:30.  Sewage discharges onto the land or into surface or ground water from leaks, spills or broken pipes must immediately be reported to the RE and Security Operations Center.  All work shall be in accordance with the General Paragraphs titled, “SANITATION.”

3.4.4	Recycling

The Contractor shall comply with Center Order 1050.2.

On a monthly basis the Contractor shall provide a written report of the volume or weight of the following recycled materials:

Office – Paper, aluminum cans, glass containers of all colors, triangle 1 and 2 plastics, and cardboard.

Construction – Concrete, asphalt, iron, steel, carbon, bulk aluminum, copper, bulk plastics, batteries, oil, and fuel.

3.5	CONTROL AND DISPOSAL OF HAZARDOUS WASTE

3.5.1	Hazardous Storage Containers (if required)

Choose approved containers utilizing the Hazardous Materials Table (HMT) in 49 CFR 172.101.  Refer to 49 CFR 173 to ensure manufacturing is in compliance with 49 CFR 178.  Store hazardous waste in approved containers properly labeled to identify the type of waste and the date the container was filled.  Remove the containers from the project site, and handle, transport and dispose of hazardous waste within 90 days in accordance with 40 CFR 263, 40 CFR 264 and NJAC 7:26-7.1 through 12.1 et. seq. and paragraph 3.8 of this section.  For oil and hazardous material spills, notify the RE immediately.

3.5.2	Petroleum Products

Conduct the fueling and lubricating of equipment and motor vehicles to protect against spills and evaporation.  Dispose of lubricants to be discarded and all excess oil as hazardous waste in accordance with NJAC 7:26G-7.1 to 9.1 et. seq.

3.5.3	Lead-Acid Battery Electrolyte

Dispose of electrolyte solution from lead-acid batteries.  Do not dump electrolyte onto the ground or into storm drains or sanitary sewers.  Comply with 29 CFR 1910.178(g), when installing or charging storage batteries.  Use one of the following alternatives for disposal of waste electrolyte:

a.	An industrial waste treatment plant, if available and approved by the RE for neutralizing and disposing of battery acid electrolyte.

b.	Transport the electrolyte to a state-approved hazardous waste disposal site.  The method of transportation and equipment shall comply with applicable Federal and state regulations.

3.5.4	Discharges

Prevent discharges of hazardous wastes, hazardous substances, hazardous materials or pollutants from entering the environment.  If an accidental leak occurs, take immediate steps to contain free flowing liquid, e.g. construct temporary containment dikes using soil.  All spills and discharges of hazardous materials shall be immediately reported to the Security Operations Center and the RE in accordance with NJAC 1:E-2.14, Standard Operating Procedures.

3.5.5	Disposal

Disposal of any debris resulting from the contract work and any wastes, effluents, trash, garbage, oil, grease chemicals, etc., in or adjacent to the work area will not be permitted.  If any waste material is dumped in unauthorized areas the Contractor shall remove the material and restore the area to its original condition at no cost to the FAA.  If necessary, contaminated ground shall be excavated, disposed of as directed by the RE, replaced with suitable fill material, compacted and finished with topsoil, and planted as required to reestablish vegetation, all at the Contractor’s expense.

3.6	DUST CONTROL

Keep dust down at all times, including during non-working periods.  Sprinkle or treat, using water-only, the soil at the site, haul roads, and other areas disturbed by operations.  Dry power brooming will not be permitted.  Instead, use vacuuming, wet mopping, wet sweeping, or wet power brooming.  Air blowing will be permitted only for cleaning nonparticulate debris such as steel reinforcing bars.  Only wet cutting will be permitted for cutting concrete blocks, concrete, and bituminous concrete.  Do not unnecessarily shake bags of cement, concrete mortar, or plaster.

3.7	NOISE

Make the maximum use of low-noise emission products, as certified by the EPA.  Blasting or use of explosives will not be permitted without written permission from the RE, and then only during the designated times.

3.8	AIR

3.8.1	Open Burning

Open burning for salvage operations and of rubbish is strictly prohibited.

3.8.2	Volatile Organic Substances (VOS)

All architectural coatings shall comply with NJAC 7:27-23.3 requirements regarding the maximum allowable VOS content per volume of the specific coating.

3.9	PERMIT APPLICATION REQUIREMENTS

The Contractor shall obtain and accurately prepare all other required environmental construction permit applications and registration forms, together with all supporting documents and drawings, in accordance with paragraph “Submittals”.  Submit completed applications(s) to RE for review and approval.  Submit approved application(s) and applicable fees to appropriate regulatory agencies within 5 working days of the RE’s approval.

3.10	WELL DRILLING PERMIT(S)

Prepare and submit permit application form(s) for the drilling of well(s) and boring holes into ground water in accordance with NJAC 7:10-12.1 et. seq.  The Contractor shall be responsible for all fees assessed per well permit.  All wells and borings into ground water must be drilled by a New Jersey licensed well driller.  A copy of all permit applications shall be provided to the RE.  Adhere to the drilling requirements contained in Section 02730 and shown on the Contract Drawings.

3.11	COMPLIANCE WITH PERMITS

The Contractor shall comply with all permits issued and with all terms and conditions contained therein.  Copies of all permits issued shall be made available to the Contractor and RE.

3.12	SUPERFUND AREAS OF CONCERN (AOC)

The entire Center was placed on the National Priorities List (Superfund) on October 1, 1990. There are currently 25 separate parcels of land called AOCs located throughout the Center on which the disposal of hazardous wastes did occur or is suspected of having occurred.  Every reasonable effort has been made to delineate and avoid contaminated areas.  However, if during the course of performing any subsurface work, debris (paper, wood, concrete, asphalt, brick, vehicle/airplane parts, eating utensils, dishware, scrap metal, drums, military ordnance, etc); unusual odors; or staining is encountered subsurface work at that particular location will stop and the RE shall be notified immediately.

3.13	ENVIRONMENTAL HEALTH AND SAFETY

Health, Safety, and Emergency Response is addressed in Specification 01740, “Health, Safety, and Emergency Response.”

END OF SECTION

# SECTION 01700

AS-BUILT RECORDS

PART 1	GENERAL

1.1	AS-BUILT RECORD DRAWINGS

During the progress of the work, the Contractor shall keep a careful record at the job site of all changes and corrections from the layouts and details shown on the drawings.  The Contractor shall enter such changes and corrections on the contract drawings promptly, but in no case later than on a weekly basis.  The Contractor shall maintain at the job site two sets of full-size marked prints; marked sets shall be available for review by the Contracting Officer’s Technical Representative (COTR) or Resident Engineer (RE) at all times.

1.2	AS-BUILT RECORD OF MATERIALS

A record of the materials used shall be furnished prior to completion of the contract.  Submission of this data is a condition of final payment under the contract.  Where several manufacturer’s brands, types, or classes of the item listed have been used in the project, the specific areas where each item was used shall be designed.  Designations shall be keyed to the areas and spaces depicted on the contract drawings.  The record of materials used shall be furnished in the following format:

Materials Used

Materials                                                       (Manufacturer’s      Where

Designation   Specification   Manufacturer   Designation)           Used

1.3	SUBMITTALS

The following shall be submitted in accordance with Section 01330, “Submittal Procedures.”

1.3.1	SD-04 Drawings

As-Built Record Drawings; GA

At the time of completion of the installation of each major structure involved under the contract, the Contractor shall submit to the RE as-built record drawings showing the aforementioned changes, corrections and data.  If the Contractor fails to maintain the record drawings as required herein, the Contracting Officer (CO) will consider that satisfactory progress has not been achieved for the period, thereby requiring the retainage of 10% of any progress payments to be made until such drawings are made current.  In addition, the estimated cost of maintaining the record drawings will be deducted from any such progress payment.  Requests for final payment will not be approved until the marked prints are delivered to the RE.

1.3.2	SD-18 Records

As-Built Record of Materials; GA

PART 2	PRODUCTS

Not Used

PART 3	EXECUTION

Not Used

END OF SECTION

SECTION 01740

HEALTH, SAFETY, AND EMERGENCY RESPONSE

PART 1	GENERAL

1.1	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI)

ANSI A10.14	Construction and Demolition Operations - Requirements for Safety Belts, Harnesses, Lanyards and Lifelines for Construction and Demolition Use

ANSI Z359.1           Safety Requirements for Personal Fall Arrest Systems

U.S. ARMY CORPS OF ENGINEERS (USACE)

EM-385-1-1	U.S. Army Corps of Engineers Safety and Health Requirements Manual

U.S. NATIONAL ARCHIVES AND RECORDS ADMINISTRATION (NARA)

29 CFR 1910	Occupational Safety and Health Standards

29 CFR 1910.120	Hazardous Waste Operations and Emergency Response

29 CFR 1910.146	Permit-Required Confined Spaces

29 CFR 1910.147	The Control of Hazardous Energy (Lockout/Tagout)

29 CFR 1926	Safety and Health Regulations for Construction

29 CFR 1926.65	Hazardous Waste Operations and Emergency Response

FEDERAL AVIATION ADMINISTRATION (FAA) ORDERS

The publications listed below are available upon request to assist the Contractor in

preparing his bid.  Submit all certifications, permit applications, and issued

permits as required by these FAA Orders to complete the work.

CT 3900.55	Occupational Safety and Health Order

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

NFPA 70	National Electrical Code

NFPA 241	Safeguarding Construction, Alteration, and Demolition Operations

1.2	SCOPE OF WORK

This section describes the minimum health, safety, and emergency response requirements for performing specified activities at the Department of Transportation, Federal Aviation Administration (FAA), FAA William J. Hughes Technical Center (Center), Atlantic City, New Jersey site.  The responsibility for development, implementation, and enforcement of the Site Safety and Health Plan (SSHP) lies with the Contractor and his health and safety personnel.  The SSHP developed by the Contractor shall include programs for accident prevention, personnel protection, emergency responses/contingency planning, and air monitoring.  Controls and procedures specified herein and by the SSHP may be terminated only when a Certified Industrial Hygienist (CIH) determines that hazards have been eliminated.  Such termination shall be effective if approved in writing by the Resident Engineer (RE).

This section provides additional requirements for implementing the accident prevention provisions of Contract Clause: EM 385-1-1, and specifies a Site Safety and Health Plan (SSHP) which shall satisfy the requirements for submission of a separate Accident Prevention Plan (APP) as required by EM 385-1-1.  The requirements shall apply to all work.

1.3	REGULATORY REQUIREMENTS

Work performed under this contract shall comply with EM 385-1-1, applicable federal, state, and local safety and occupational health laws and regulations.  This includes, but is not limited to, Occupational Safety and Health Administration (OSHA) standards, 29 CFR 1910, especially Section .120 “Hazardous Waste Site Operator Standards” and 29 CFR 1926, especially Section .65 “Hazardous Waste Site Operations and Emergency Response.” This also includes the FAA Technical Center’s Occupational Safety and Health Order, CT Order 3900.55.  Matters of interpretation of standards shall be submitted to the appropriate administrative agency for resolution before starting work.  Where the requirements of this specification, applicable laws, criteria, ordinances, regulations, and referenced documents vary, the most stringent requirements shall apply.

1.4	SUBMITTALS

The following shall be submitted in accordance with Section 01330, “Submittal Procedures”.

1.4.1	SD-01 Data

a.	Site Safety and Health Plan (SSHP); GA

The Contractor shall submit four copies of an SSHP to the RE within 15 days of the Notice of Award.  Approval of the SSHP shall be the responsibility of the RE.  Contents of the SSHP shall include, but not be limited to, items described herein (Articles 3.1 through 3.9).

b.	Material Safety Data Sheets (MSDS); GA

The Contractor shall submit Material Safety Data Sheets for all hazardous or other applicable materials, both furnished for the work or used in the course of the work.

PART 2	PRODUCTS

Not Used

PART 3	EXECUTION

3.1	ORGANIZATIONAL RESPONSIBILITIES

a.	Key Personnel and Organization Chart: The Contractor shall provide, at a minimum, an organizational chart and resumes of key personnel involved in all phases of construction.  This chart must include Senior-Level Management, Project Manager, Site Safety and Health Officer (SSHO), Field Supervisors/Foreman Personnel that are key personnel.

b.	SSHO: The Contractor must employ or contract a qualified individual (e.g., an industrial hygienist, safety engineer, etc.) to function as the SSHO for the project.  That individual must be responsible to the Contractor and have the authority and knowledge necessary to implement the SSHP and verify compliance with applicable safety and health requirements.

c.	At a minimum, the SSHO shall have the following responsibilities and authority to perform the following functions:

1.	Visit the site as needed to insure that the SSHP is being implemented, ensure that daily tailgate safety meetings are being conducted by the Field Supervisor/Site Forman, and provide any necessary training to on-site personnel.

2.	Have the authority to enforce the SSHP and stop operations if safety and health of personnel may be jeopardized.

3.	Effect evacuation of the site if necessary.

4.	Evaluate monitoring data to make field decisions regarding safety and health.

5.	Respond and visit the site within 24 hours of notification from the RE regarding health and safety violations and concerns.

3.2	HAZARD ASSESSMENT

The Contractor shall perform and provide a hazard assessment for each location and operation to be performed.  The hazard assessment shall be based on the best information available regarding contaminants and conditions present at the site as well as the practice and tools to be applied in the operation and shall include but not be limited to the following:

a.	A preliminary evaluation of the site’s characteristics

b.	An evaluation of the known (including the use of MSDS) or suspected hazards.

c.	An evaluation of known or potential safety hazards associated with each task.

d.	An overview of the site including descriptions of the operations and tasks to be performed.  Include the following:

1.	Size and location of the site.

2.	Description of the operation and tasks to be performed.

3.	Approximate duration of the operation and each task.

4.	Site topography and special features (e.g., structures, tanks, etc.).

5.	Known or suspected pathways of hazards pertinent to the operation and tasks performed.

6.	Site accessibility.

7.	Safety and health hazards expected on the site.

3.3	EMPLOYEE TRAINING

The Contractor shall provide site specific training and perform daily safety briefings (tailgate safety meetings) that will provide an awareness of planned operations, the site specific SSHP, the form and warning properties of potential hazards, work zones, locations of emergency/safety equipment, local emergency response procedures, site characteristics, levels of protection, communications, decontamination procedures, emergency facilities and signals, and evacuation procedures.

3.4	PERSONNEL PROTECTION

The Contractor shall apply engineering and/or work practice controls as a means of protecting personnel in performance of site-specific tasks.  Engineering controls shall be implemented to reduce and maintain employee exposure to at or below safety levels for those tasks demonstrating known or suspected hazards.  Work practice controls shall be applied when engineering controls are impractical and shall be incorporated as site-specific standard operating procedures (SOPs) for personnel precautions and routine operations.

The Contractor shall use personal protective equipment (PPE) beyond Level D only when engineering and/or work practice controls have been deemed impractical or insufficient to protect employees during site operations.  Personnel shall be properly trained in the use of PPE.  When necessary, personnel shall be medically cleared to use the required PPE.  If the use of PPE beyond Level D (hard had, steel toe shoes, and reflective safety vest) is required, contact the RE.  Use of PPE in emergency situations is allowed as necessary.

If PPE beyond Level D is required, the SSHO shall update the SSHP to include all necessary training and medical surveillance.  The SSHP shall also be revised as follows:

a.	The Contractor shall include in the SSHP a list of components for each protective ensemble, the level of protection (LOP) selected for each task, the rationale for each task-specific selection, and any contaminant action levels to be followed in LOP decision making.

b.	The Contractor shall include in the SSHP a description of their respiratory protection program and the method of respirator fit testing employed.

c.	The Contractor shall only make use of NIOSH approved respiratory protective equipment.

d.	The Contractor shall establish and include in the SSHP a PPE program addressing the following elements:

1.	Site hazards

2.	PPE selection

3.	PPE use

4.	Duration of site operations

5.	PPE maintenance and storage

6.	PPE decontamination

7.	PPE training and proper fit

8.	Donning and doffing procedures

9.	PPE inspection

10.	PPE in-use monitoring

11.	Evaluation of program effectiveness

12.	Heat stress and temperature limitations

3.5	EMPLOYEE HEAT AND COLD STRESS MONITORING

As dictated by seasonal conditions, the Contractor shall implement an employee heat or cold stress monitoring program during site operations and shall incorporate the program into the site SSHP.

a.	The program shall include employee awareness of the signs and symptoms of heat or cold stress, preventive measures, and employee parameters to be monitored.

b.	The Contractor shall maintain a daily heat or cold stress log on all employees on-site engaging in field activities and shall describe the log in the SSHP.

3.6	SITE CONTROL

The Contractor shall be responsible for conducting operations at the site in a manner as to reduce the possibility of contact with any contaminants present to prevent the removal of contaminants by personnel or equipment leaving the site, and to prevent the migration of contaminants.

The Contractor shall keep a daily log of site activities, including: personnel visiting the site, affiliation, date, arrival time, departure time, and purpose of the visit.

The Contractor shall provide the RE with a list of all Contractor and subcontractor personnel authorized to enter the site prior to start of operations, updating the list as necessary.

3.7	SITE STANDARD OPERATING PROCEDURES

The Contractor shall be responsible for the development and implementation of all necessary SOPs (e.g., air monitoring) for site operations.  The SOPs shall be incorporated into the SSHP.

3.8	CONTINGENCY PLANNING

The Contractor shall develop and implement an Emergency Response Plan (ERP) to handle anticipated on-site emergencies prior to start of site operations.  The ERP shall be incorporated into the SSHP as a separate section of that document and shall be periodically reviewed and amended to keep it current with new or changing site conditions or information.

3.9	CONFINED SPACE ENTRY (if required)

Entry into and work in a confined space will not be allowed when oxygen readings are less than 19.5% or greater than 23.5% or if the Lower Flammable Limit (LFL) reading is greater than 10%, unless these conditions are adequately addressed in the confined space entry program.  In addition, action levels for toxic atmospheres shall be determined.

In accordance with CT 3900.55, Chapter 20, Contractors must present a copy of their confined space program and proof of training prior to being allowed to enter any confined space on the Center. CT Form 3900-40 must be properly filled in and signed prior to a confined space entry and a copy of the form must be provided to the FAA Technical Center Safety Office, ACX-42.

In addition, all confined space entries must be arranged with the Technical Center Safety Office.  An entry permit identifying all conditions that must be satisfied prior to confined space entry shall be prepared in accordance with EM-385-1-1, 29 CFR 1910.146, and 29 CFR 1910.147.  The SSHP shall describe the standard operating safety procedures, engineering controls and safe work practices to be implemented for compliance with these permit requirements.

In addition to the requirements set forth in EM-385-1-1, 29 CFR 1910.146, and 29 CFR 1910.147, the Contractor shall also satisfy the following:

1.	The Contractor shall supply all sampling and testing equipment and personnel.

2.	The Contractor shall have an OSHA approved mechanical extraction system that utilizes a full torso harness.

END OF SECTION

SECTION 02003

SURVEY CONTROL FOR EXCAVATION AND BACKFILLING

PART 1	GENERAL

1.1	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

STATE OF NEW JERSEY BOARD OF PROFESSIONAL ENGINEERS & LAND SURVEYORS

Title 45:8	New Jersey State Statues, Chapter Professional Engineers and Land Surveyors

Chapter 40	State Board of Professional Engineers and Surveyors Administrative Rules and Regulations

CODE OF FEDERAL REGULATIONS

29 CFR 1910	Occupational Safety and Health Standards; General Industry

1.2	DESCRIPTION

This section includes requirements for field survey control, measurement and marking for work associated with the excavation and backfilling of the Recharge Bed.  The requirements are also applicable to surveys performed in work areas sampled to demonstrate that soil has not become contaminated during the project, if required by the RE.

1.3	SURVEY REQUIREMENTS

All surveys shall be performed in accordance with an accuracy of class A-2 as defined in the Code of Survey Standards dated 1976 and shall be performed by a surveyor licensed in the State of New Jersey.  All survey control work shall be conducted with standards set forth by the Federal Geodetic Control Committee for third order Class I traverse and triangulation and third order leveling.

1.4	SUBMITTALS

1.4.1	SD-02; Data

a.	Survey Field Notes; GA

Two (2) copies of all survey field notes and calculations shall be provided to the Resident Engineer (RE).

1.4.2	SD-04 Drawings

a.	Topographic As-Built Maps; GA

Provide copies of Topographic As-Build Maps.  Provide copies of all survey data in tabular form.

PART 2	PRODUCTS

2.1	STAKES AND FLAGGING

Tall stakes shall be 1” by 1” by 36” high oak or other material approved by the Resident Engineer (RE) with point for driving.  Flagging to be tied to stakes shall be wide bright colored plastic flagging.

PART 3	EXECUTION

3.1	EXCAVATION LAYOUT

The Contractor shall locate and mark the location of the Recharge Bed excavation with tall stakes and flagging of all excavations.  Locations shall be located to an accuracy of 0.1 feet and the surface elevation to an accuracy of 0.01 feet.

3.2	EXCAVATION SURVEY

As soil is being excavated from the Recharge Bed area, the survey crew shall check the depth of excavation and provide depth correction and grade stakes for the excavation equipment operators.  Where computer controlled construction equipment is used, provided survey data as needed.  As the excavation is completed for the construction of the Recharge Bed, a survey of location and depth shall be completed.  The coordinate location and elevation of the surface at each survey location shall be measured to an accuracy of 0.1 and 0.01 feet, respectively.  The Surveyor shall provide a complete topographic survey of the bottom of the recharge bed excavation prior to backfilling.  No backfilling will be allowed until the RE approves the survey data.

3.3	POST-EXCAVATION SURVEY

Following completion of all excavation activities, the Contractor shall survey the recharge bed area.  The Contractor shall prepare a topographic as-built map of the Recharge Bed area with a minimum of one-foot contour intervals.

END OF SECTION

SECTION 02099

SMALL ACCESS BRIDGE

PART 1	GENERAL

1.1	DESCRIPTION

a.	This work consists of the design, fabrication and erection of a simple span, wood and steel model bridge with a timber deck in accordance with the specifications and Project Plans.

b.	The bridge shall have a span length of 20 feet and clear width of 7 feet.  The clear width shall be defined as the total width of the timber deck.  The bridge style shall be curb-only.

1.2	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by basic designation only.  Unless otherwise directed, use the most recent version of the applicable publication.

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM A 36		(2005) Carbon Structural Steel

ASTM A 307	(2007) Carbon Steel Bolts and Studs, 60 000 PSI Tensile Strength

ASTM A588 	(2005) Standard Specification for High-Strength Low-Alloy Structural Steel

ASTM A572 	(2007) Standard Specification for High-Strength Low-Alloy Columbium-Vanadium Structural Steel

1.3	MANUFACTURER

The bridge shall be a product of a manufacturer regularly engaged in the manufacture of similar bridges and shall essentially duplicate items that have been in satisfactory use for at least 2 years prior to bid opening.

The recommended bridge supplier:

Moosman Enterprises

P.O. Box 803

Valentine, NE 69201

Phone: (402) 376–2544

Fax:  (402) 376–1737

or an approve equal.

The acceptable Bridge configuration is the Moosman “Tioga” model or

approved equal.

1.4	SUBMITTALS

The following shall be submitted in accordance with Section 01330 "Submittal Procedures”.

1.4.1	SD-01 Data; GA

- Timber; GA

- Structural Steel; GA

- Structural Fasteners; GA

Provide data showing all materials conform to the requirements of the specifications.

1.4.2	SD-01 Data; GA

- Loading Calculations; GA

Provide loading calculations demonstrating conformance with the specifications.  All calculations shall be signed and sealed by a New Jersey licensed PE.

1.4.3	SD-04 Drawings; GA

Bridge Drawings; GA

Drawings of the bridge shall include a complete list of materials, bridge dimensions, and installation instructions.  All drawings shall be signed and sealed by a New Jersey licensed Professional Engineer (PE).

1.4.3	SD-13 Certifications

Warranty; GA

Provide a copy of the bridge manufacturer’s standard warranty on materials and workmanship.  The warranty shall be a minimum of 10 years.

Qualifications of Bridge Manufacturer; GA

Qualifications of the Bridge Manufacturer demonstrating compliance with Article 1.3.

PART 2	PRODUCTS

2.1	MATERIALS

2.1.1	Structural Steel

a.	All structural steel shall be new (unused) material.  The Contractor shall provide the Owner with copies of all certified mill test reports for all structural steel and bolts upon request.

b.	All structural wide flange beams shall conform to the requirements of ASTM A588 or ASTM A572, Corten Structural Steel.

c.	All structural plates shall conform to the requirements of ASTM A588 Structural Steel.

2.1.2	Timber

a.	All timber shall be pentachlorophenol treated material.

b.	All timber except deck material shall be Douglas Fir–Larch, “Select Structural” or better quality, graded in accordance with West Coast Lumber Inspection Bureau (WCLIB) rules.

c.	Douglas Fir–Larch, “No. 1 or better” or better quality shall be used for the timber decking only.

2.1.3	Structural Fasteners

a.	All bolts shall conform to the requirements of ASTM A307 or ASTM A36.  All bolts exposed in wood structure shall be plain, uncoated steel.

b.	All anchor bolts and nuts shall conform to the requirements of ASTM A307, Grade A, Carbon Steel Bolts and Studs.  Each anchor bolt shall be provided with two nuts for jamming.

2.2	DESIGN

The superstructure of the bridge shall consist of two Douglas Fir timbers.  Floor beams shall be fabricated from structural steel wide flange sections.  The structure shall conform to the clear span and clear width requirements as specified.

2.2.1	Design Loads

Each bridge shall be designed for the following loads and loading conditions:

a.	Pedestrian live load shall be as defined by the AASHTO Guide Specifications for load group I of the AASHTO Standard Specifications, Section 3.  A minimum pedestrian live load of 85 psf, or a reduced pedestrian live load as defined in the AASHTO Guide Specifications shall be used for design.  Distribution to the stringer and floor beams shall be in accordance with Section 3 of the AASHTO Standard Specifications.  Deflection and vibration limits shall be met per the AASHTO Guide Specifications.

b.	Vehicle live load shall be as defined by the AASHTO Guide Specifications, and used in load group IB of the AASHTO Standard Specifications, Section 3 or as noted following.  The vehicle axle loads shall be 4,000 lbs for rear axles and 2,000 lbs for the front axle.  The total vehicle live load shall be 10,000 lbs.

c.	Minimum thickness of a structural steel shall be ¼ of an inch for tubular steel and 3/8 of an inch for steel plate material.

d.	Timber decking shall have a minimum nominal thickness of 3 inches.  Decking shall be securely fastened to each floor beam and at each end to prevent warping.  Decking shall be fastened from the bottom up.

e.	Final design and construction of the bridge support (abutment, pier, or footing) will be the responsibility of the Contractor and shall be based on bridge support reactions and anchor bolt location and placement which shall be furnished by the bridge manufacturer.

PART 3	EXECUTION

3.1	DELIVERY AND ERECTION

a.	Bridge materials shall be delivered to the site using normal over–the–road tractor/trailer equipment.  The Contractor shall unload the bridge sections/materials and store them in accordance with the manufacturers’ instructions.  The Contractor shall supply all lifting equipment needed to unload the bridge sections/materials.

b.	The bridge manufacturer or its representative will instruct the Contractor or his representatives in the proper lifting procedure for the unloading of the bridge.  Care shall be taken to prevent damage to the finish of the bridge.

- The unloading, splicing (if required), and placement of the bridge shall be the responsibility of the Contractor.  The procedure for bolting field splices shall be given to the Contractor by the bridge manufacturer.

- No wetlands shall be disturbed during the construction and placement of the bridge.

END OF SECTION

SECTION 02110

CLEARING AND GRUBBING

PART 1	GENERAL

1.1		APPLICABLE PUBLICATIONS

The publications listed form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

AMERICAN ASSOCIATION OF STATE HIGHWAY AND TRANSPORTATION OFFICIALS (AASHTO)

M182-60(1974)		Burlap Cloth Made From Jute or Kenaf

1.2		SCOPE OF WORK

The work described herein and as shown on the Contract Drawings shall consist of furnishing all labor, material and equipment and performing all operations required for performing clearing and grubbing during construction as specified herein and as shown on the Contract Drawings.  The work shall conform to the Soil Erosion and Sediment Control Plan and Permit as approved by the Pinelands Commission and Soil Conservation District. Site soil erosion and sediment controls must be in place and pest control must also be conducted before proceeding with any site construction activity (i.e., clearing and grubbing).

1.3		DELIVERY AND STORAGE

Deliver materials to and store at the SITE in a manner which will maintain the materials in their original manufactured or fabricated condition until ready for use.

1.4		PROTECTION

1.4.1		Roads

Keep roads free of dirt and debris at all times.

1.4.2		Trees, Shrubs, and Existing Facilities

Provide barricades for trees, shrubs, and existing facilities designated to remain in areas to be cleared and grubbed.  In addition to fencing, protect shrubs from wind damage with burlap enclosures as indicated.  Currently, no trees or shrubs will be preserved in the area to be cleared and grubbed.

1.4.3		Barricades

Erect barricades for items in paragraph “Trees, Shrubs, and Existing Facilities,” above, before commencing clearing and grubbing operations.  Barricades shall be of a 4- to 6-foot high wire or wood fencing supported by posts on 10- to 12-foot centers.  Erect barricades at or outside the tree and shrub drip line.  Place barricades for existing facilities as directed by the Resident Engineer (RE).  No traffic or storage shall be permitted within the barricaded areas.  Upon completion of all work all barricades shall become the property of the Contractor and shall be removed from the SITE.

1.4.4		Utility Lines

Protect from damage all existing utility lines that are indicated to remain.  Notify the RE immediately of any damage to or encounter with an unknown existing utility line.  The Contractor shall be responsible for the repair of any damage to existing utility lines that are indicated or made known to the Contractor prior to start of clearing and grubbing operations.

1.4.5		Blasting

The use of explosives will not be permitted.

1.4.6		Personal Protective Equipment

All work within the contaminant zone shall require that personal protective equipment be worn to protect the health and safety of workers.  The personal protective equipment shall be in accordance with the Contractor’s approved health and safety plan.

PART 2	PRODUCTS

2.1		MATERIALS

2.1.1		Burlap

AASHTO M182

2.1.2		Tree Wound Paint

Tree wound paint shall be bituminous based paint of standard manufacture specially formulated for the intended use.

PART 3	EXECUTION

3.1		CLEARING

Clearing shall consist of the felling, trimming, and cutting of trees into sections and the satisfactory disposal of the trees and other vegetation designated for removal, including downed timber, snags, brush, and rubbish occurring within the areas to be cleared.  Cut off flush with the original ground surface trees, stumps, roots, brush, and other vegetation in areas to be cleared, except for trees and vegetation indicated or directed to be left standing.  Trim trees designated to be left standing within the cleared areas of dead branches 1-1/2 inches or more in diameter; and trim all branches to heights and in a manner as indicated.  Neatly cut limbs and branches to be trimmed close to the bole of the tree or main branches.  Paint cuts more than 1-1/4 inches in diameter with an approved tree-wound paint.

3.2		GRUBBING

Grubbing shall consist of the removal and disposal of roots larger than 3 inches in diameter, matted roots, and stumps from the indicated grubbing areas.  Excavate this material together with logs, organic and metallic debris, brush and refuse.  Excavate materials completely in areas where construction of the recharge bed is to occur.  Where required, fill depressions made by grubbing with backfill material and compact in accordance with the requirements specified to make the new surface conform with the existing adjacent surface of the ground.

3.3		PEST CONTROL

Remove and eradicate all pests from the work area during the clearing and grubbing project and during the course of the project.  This shall include the removal of wasp and bees nests in the work area and equipment to be scrapped or staged.

3.4		DISPOSAL OF CLEARED AND GRUBBED MATERIALS

All trees, shrubs, stumps and roots removed during clearing and grubbing shall be thoroughly dried and cleaned of all soil prior to chipping and grinding.  All cleared and grubbed materials shall be chipped and disposed of off-site.

Timber may be disposed of off-site prior to chipping if approved by the RE.  Burning will not be permitted.

END OF SECTION

SECTION 02112

EROSION AND SEDIMENT CONTROL

PART 1	GENERAL

1.1	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM D 4439	(2000) Geosynthetics

ASTM D 4491	(1999a) Water Permeability of Geotextiles by Permittivity

ASTM D 4533	(1991; R 1996) Trapezoid Tearing Strength of Geotextiles

ASTM D 4632	(1991; R 1997) Grab Breaking Load and Elongation of Geotextiles

ASTM D 4751	(1999a) Determining Apparent Opening Size of Geotextile

STATE OF NEW JERSEY, DEPARTMENT OF ENVIRONMENTAL PROTECTION STORMWATER MANAGEMENT REGULATIONS

NJDEP New Jersey Soil Erosion and Sediment Control Manual, revised July

1999.

NEW JERSEY DEPARTMENT OF TRANSPORTATION (NJDOT)

NJDOT-SS 1989 New Jersey Department of Transportation Standard

Specification for Road and Bridge Construction

1.2	SCOPE OF WORK

The work described herein and as shown on the Contract Drawings shall consist of furnishing all labor, material and equipment and performing all operations required for furnishing and installing the erosion and sediment controls during construction as specified herein and as shown on the Contract Drawings, and maintaining the erosion and sediment controls through the construction period until the SITE has been stabilized, as determined by the Resident Engineer (RE).

The work shall conform to the Soil Erosion and Sediment Control Plan and Permit as approved by the Pinelands Commission and Cape-Atlantic Soil Conservation District.  Site soil erosion and sediment controls must be in place before proceeding with any site construction activity (i.e., clearing and grubbing).

1.3	SUBMITTALS

Submit to the RE the following:

1.3.1	SD-08, Statements

a.	Soil Erosion and Sediment Control Plan; GA

Describe materials and methods to be used.  Provide plans, sketches, details and sequence.

PART 2	PRODUCTS

2.1	STRUCTURAL PRACTICES

2.1.1	Silt Fence Fabric

The geotextile shall comply with the requirements of ASTM D 4439, and shall consist of polymeric filaments which are formed into a stable network such that filaments retain their relative positions.  The filament shall consist of a long-chain synthetic polymer composed of at least 85 percent by weight of ester, propylene, or amide, and shall contain stabilizers and/or inhibitors added to the base plastic to make the filaments resistance to deterioration due to ultraviolet and heat exposure.  Synthetic filter fabric shall contain ultraviolet ray inhibitors and stabilizers to provide a minimum of six months of expected usable construction life at a temperature range of –18 to 49 degrees C (0 to 120 degrees F).  The filter fabric shall meet the following requirements:

FILTER FABRIC FOR SILT SCREEN FENCE

# Physical Property		Test Procedure		Strength Requirement

Grab Tensile 		ASTM D 4632		100 lbs. min.

Elongation (%)						30% max.

Trapezoid Tear		ASTM D 4533		55 lbs. min.

Permittivity		ASTM D 4491		0.2 sec-1

AOS (U.S. Std Sieve)		ASTM D 4751		20-100

2.1.2	Run-On/Barrier Fabric

Fabric used to wrap the soil pile in run-on barrier construction shall be non-rotting, ultraviolet light resistant, non-woven polyester geotextile with sufficient strength for the purpose intended.

2.1.3	Strawbales

Bales used in sedimentation control system shall be made of straw with forty pounds minimum weight and one hundred and twenty pounds maximum.

2.1.4	Wood Stakes

Wood stakes used in sedimentation control system shall be a minimum 2-inch by 2-inch nominal size by a minimum 3 feet long.

2.1.5	Run-on Barrier Soil

Run-on Barrier soil shall be Backfill Material as specified in Section 02225, “Excavation, Backfilling, and Compacting”.

2.1.6	Silt Fence Wire Mesh (if used)

The wire mesh used shall be steel wire mesh of significant strength to support the filter fabric loaded with sediment to 1/3 of its overall height.  Minimum 20 gauge with 1-inch square openings wire shall be used.

2.1.7	Stone

Stone used for the stabilized construction entrance shall be 1-inch to 2-inch crushed stone conforming to the requirement of Size #3 in Table 901-1 of the NJDOT-55.

2.1.8	Sand Bags

Sand bag fabric shall be woven polypropylene, polyethylene or polyamide with a minimum unit weight of four ounces per square yard.  The fabric shall have a mullen burst strength of at least 300 psi, conforming to the requirements in ASTM D 3786, and an ultraviolet (UV) stability exceeding 70 percent.  Sand bags shall have a length of 24 to 32 inches, width of 16 to 18 inches, thickness of 6 to 8 inches, and mass of 88 to 121 pounds.

Sand bag fill material shall be non-cohesive, coarse sand or gravel, free from deleterious material.

2.1.9	Dewatering Filtration Bag

Dewatering filtration bags shall be manufactured of durable nonwoven needle punched poly propylene geotextile, Geo-Synthetics Inc Dirtbag® or approved equal.  Hose opening shall be 4”.    Flow through filtration bag shall have minimal impact on pump efficiencies.

PART 3	EXECUTION

3.1	CONSTRUCTION METHODS

Construction of erosion and sediment control practices shall be sequenced to coordinate with the construction schedule.  Perimeter erosion and sediment controls shall be in place and be completely functional prior to start of any land disturbing activities.  Perimeter controls, topsoil stockpiles and other disturbed areas on the SITE shall be stabilized within 14 calendar days following soil disturbance.  All erosion and sediment controls shall be constructed and installed in accordance with the Contract Drawings and Soil Erosion and Sediment Control Plan approved by the Cape-Atlantic Soil Conservation District.

Install controls where shown on plans and as necessary to protect areas disturbed by the Contractor which may not be shown on the plans.

3.1.1	Silt Fence

Furnish and install silt fence as detailed and at the locations as shown on the Contract Drawings.  The silt fence shall remain in place during the duration of the project and shall not be removed without the approval of the RE.

3.1.2	Run-On Barrier

Run-on barriers shall be constructed as detailed and at the locations shown on the Contract Drawings.  Filter fabric shall be placed on the natural ground surface and backfill material placed to form the berm shown on the Contract Drawings.  Filter fabric shall completely encircle the soil berm and the two ends of fabric shall be buried in a 4 inches deep continuous trench on the upstream side.  The run-on barrier shall remain in place during the duration of the project and shall be removed with the approval of the RE.

3.2	MAINTENANCE

The erosion and sediment control measures shall remain in place for the duration of the construction period, unless otherwise noted on the contract drawings.  The Contractor shall inspect all erosion and sediment control measures after each rainfall event and replace or repair as necessary for measures to remain functional and as directed by the RE.

END OF SECTION

SECTION 02225

EXCAVATION, BACKFILLING, AND COMPACTING

PART 1	GENERAL

1.1		APPLICABLE PUBLICATIONS

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM C 136	Sieve Analysis of Fine and Coarse Aggregates

ASTM C 913	Precast Concrete Water and Wastewater Structures

ASTM D 422	Particle-Size Analysis of Soils

ASTM D 698	Moisture-Density Relations of Soils and Soil-Aggregate Mixtures, Using 5.5 lb (2.49-kg) Rammer and 12-in. (304.8-mm) Drop

ASTM D 1140	Amount of Material in Soils Finer than the No. 200 (75-micrometer) Sieve

ASTM D 1556	Density of Soil in Place by the Sand Cone-Method

ASTM D 1557	Moisture-Density Relations of Soils and Soil-Aggregate Mixtures Using 10-lb (4.54-kg) Rammer and 18-in. (457-mm) Drop

ASTM D 2434	Permeability of Granular Soil (Constant Head)

ASTM D 2487	Classification of Soils for Engineering Purposes

ASTM D 2922	Density of Soil and Soil-Aggregate in Place by Nuclear Methods (Shallow Depth)

ASTM D 3017	Moisture Content of Soil and Soil-Aggregate in Place by Nuclear Methods (Shallow Depth)

ASTM D 4318	Liquid Limit, Plastic Limit, and Plasticity Index of Soils

ARMY CORPS OF ENGINEERS (COE)

EM-385-1-1	Safety and Health Requirements Manual

STATE OF NEW JERSEY, DEPARTMENT OF TRANSPORTATION (DOT)

STANDARD SPECIFICATION

NJDOT 			Specifications for Road and Bridge Construction

STATE OF NEW JERSEY, DEPARTMENT OF ENVIRONMENTAL PROTECTION, DIVISION OF WATER RESOURCES

NJDEP	Underground Storage Tank Regulations - NJAC 7:14B

NJDEP	Guidance Document for the Remediation of Contaminated Soils

NJDEP	Technical Requirements for Site Remediation NJAC 7:26E

1.2	DESCRIPTION

This section includes requirements for excavating, preparation of soil surface, bedding, backfilling and compaction for all work, including but not limited to the Recharge Bed, structures, and trenching.

1.2.1	Requirements

Referenced Standard Specifications:  Materials and workmanship specified herein with reference to the State of New Jersey Department of Transportation (NJDOT) Standard State Specifications shall be in accordance with the referenced articles, sections, and paragraphs of the NJDOT Standard Specifications except that contractual and payment provisions do not apply.

1.3	DEFINITIONS

1.3.1	Backfill

Material used in refilling a trench or other excavation.

1.3.2	Cohesive Materials

Soils classified by ASTM D 2487 as GC, SC, ML, CL, MH, and CH.  Materials classified as GM and SM will be identified as cohesive only when fines have a plasticity index greater than four.

1.3.3	Cohesionless Materials

Soils classified by ASTM D 2487 as GW, GP, SW, and SP.  Materials classified as GM and SM will be identified as cohesionless only when the fines have a plasticity index of less than or equal to four.

1.3.4	Compaction

Any method of mechanically stabilizing a material by increasing its density at a controlled moisture condition.  “Degree of Compaction” is expressed as a percentage of the maximum density obtained by the test procedure described in ASTM D 698 or ASTM D 1557 for general soil types or abbreviated in this specification as “95 percent ASTM D 1557 (or ASTM D 698) maximum density.”

1.3.5	Controlled Fill

A fill consisting of a specified soil mix or gradation of materials constructed to attain maximum bearing strength and minimize consolidation or differential settlement under a load.  Controlled fill is sometimes called “structural fill.”

1.3.6	Embankment

A “fill” having a top that is higher than adjoining ground.

1.3.7	Excavation

The removal of soil, rock, or hard material to obtain a specified depth or elevation.

1.3.8	Fill

Specified material placed at a specified degree of compaction to obtain an indicated grade or elevation.

1.3.9	Granular Pipe Bedding

A dense, well-graded aggregate mixture of sand, gravel, or crushed stone (mixed individually, in combination with each other, or with suitable binder soil) placed on a subgrade to provide a suitable foundation for pipe.  Granular bedding material may also consist of poorly graded sands or gravels where fast draining soil characteristics are desired.

1.3.10	Hard Material

Weathered rock, dense consolidated deposits, or conglomerate materials which are not included in the definition of “rock” but which usually require the use of heavy excavation equipment, ripper teeth, or jack hammers for removal.

1.3.11	In-Situ Soil

Existing in place soil.

1.3.12	Lift

A layer or course of soil placed on top of unprepared subgrade or a previously prepared or placed soil in a fill or backfill.

1.3.13	Refill

Material placed in excavation to correct overcut in depth.

1.3.14	Rock

Solid homogeneous interlocking crystalline material with firmly cemented, laminated, or foliated masses or conglomerate deposits, neither of which can be removed without systematic drilling and blasting, drilling and the use of expansion jacks or feather wedges, or the use of backhoe-mounted pneumatic hole punchers or rock breakers; also large boulders, buried masonry, or concrete other than pavement, pits and vaults exceeding one cubic yard in volume.  Removal of “hard material” will not be considered rock excavation because of intermittent drilling and blasting that is performed merely to increase production.

1.3.15	Soil

The loose surface material of the earth’s crust resulting from the chemical and mechanical weathering of rock and organic material.

1.3.16	Subgrade

The bottom layer of material (sometimes in-situ soil or rock) graded or otherwise prepared for supporting the addition of fill material, pavement courses, or a building slab.

1.3.17	Suitable Backfill Material

Backfill material that meets all of the requirements for its intended use as specified in this, and other, sections.

1.3.18	Unyielding Material

Rock or soil with cobbles in the trench bottom requiring a covering of finer grain material or special bedding to avoid bridging in the pipe or conduit.

1.3.19	Unsatisfactory Material

In-situ Soil or other material identified as having insufficient strength or stability to carry intended loads on trench backfills without excessive consolidation or loss of stability.  Also backfill material which contains refuse, frozen material, large rocks, debris, and other material which could damage the pipe or cause the backfill not to compact.  Materials containing contaminants above regulatory concern are unsatisfactory.  Materials classified as MH, CH, PT, OH, or OL by ASTM D 2487 are unsatisfactory.  Additionally, unsatisfactory material may refer to material within the footprint that does not have sufficient permeability to allow the basin to perform adequately.

1.3.20	Unstable Material

Material in the trench bottom which lacks firmness to maintain alignment and prevent joints from separating in the pipe, conduit, or appurtenant structure during backfilling.  This may be material otherwise identified as satisfactory which has been disturbed or saturated.

1.4	SUBMITTALS

Submit the following in accordance with Section 01330, “Submittal Procedures.”

1.4.1 	SD-09 Reports; GA

Provide certified test reports stating the materials below meet the requirements of Articles 2.1.1 through 2.1.3 of this section of the specifications.

a.	Pipe Bedding Material

b.	Backfill Material Tests

c.	Sand

d.	Gravel and Crushed Stone

1.4.1.1	SD-09 Soil Laboratory Analytical Test Reports; GA

Submit copies of all analytical reports from the testing service.

1.4.2	SD-13 Certificates; GA

a.	Manufacturers Certificates of Compliance - Warning and identification tape

b.	Certifications of each welder’s qualifications prior to on-site welding.

1.4.3	SD-08 Statements and SD-04 Drawings; GA

Provide Contractor Furnished Plans and Shop Drawings, and necessary permits for the following:

a.	Shoring and Sheeting Plan: Describe materials of shoring system to be used.  Components shall not remain after filling or backfilling.  Provide plans, sketches, or details along with calculations by a professional engineer registered in any jurisdiction.  Indicate sequence and method of installation and removal.

b.	Hot Work Permit from the FAA Technical Center Fire Inspector.

c.	Confined Space Entry Permit per applicable OSHA and FAA requirements.

1.4.4	SD-09 Reports; GA

Provide field test reports, as described below:

- Laboratory Density and Moisture Tests:  Submit within 14 days of test date.

- Results of Field Density and Moisture Tests: Results shall be made available in the field immediately after testing.  Submit results within 2 days of test date.

Submit all test data not listed above sufficiently in advance of construction so as not to delay work.

1.4.5	SD-02 Data; GA

- Provide a list of all excavation equipment to be used at the site including the track or tire loading.

- Scrim/String Reinforced LDPE Liner

- Non-woven Filter Fabric

- Tri-planar Drainage Grid

1.5	REGULATORY REQUIREMENTS

Materials and workmanship specified herein with reference to DOT State Standard shall be in accordance with the referenced articles, sections and paragraphs of the standard except that contractual and payment provisions do not apply.  Where the term “Engineer” is used, it shall mean the Resident Engineer (RE).  Where term “state” is used, it shall mean “Federal Government.”

1.6	DELIVERY AND STORAGE

Deliver and store materials in a manner to prevent contamination, segregation, freezing, and other damage.  Store synthetic fiber filter fabric to prevent exposure to direct sunlight.

1.7	PROTECTION

1.7.1	Utility Location

Contact the RE 10 calendar days prior to construction to request FAA location of underground utilities.  The Contractor shall verify the location of all utilities shown on the Contract Drawings or identified during utility mark-outs.

Movement of construction machinery and equipment over pipes and utilities during construction shall be at the Contractor’s risk.  Perform all work adjacent to non-government utilities as indicated in accordance with procedures outlined by the utility company.  For work immediately adjacent to or for excavations exposing a utility or other buried obstruction, use hand or light equipment excavation.  Start hand or light equipment excavation on each side of the indicated obstruction and continue until the obstruction is uncovered or until clearance for the new grade is assured.  Support uncovered lines or other existing work affected by the contract excavation until approval for backfill is granted by the RE.  Report damage to utility lines or subsurface construction immediately to the RE.  The Contractor shall be responsible for the repair of all damaged utilities that were previously shown on Contract Drawings identified during utility mark-outs at no cost to the FAA.

1.7.2	Structures and Surfaces

Protect newly backfilled areas and adjacent structures, slopes, or grades from traffic, erosion settlement, or any other damage.  Repair and reestablish damaged or eroded grades and slopes and restore surface construction prior to acceptance.  All work shall be conducted in accordance with the requirements specified in Section 01560, “Environmental Protection,” and Section 02112, “Erosion and Sediment Control.”

1.7.3	Use suitable surplus excavated material as backfill for excavated areas as shown on the Contract Drawings.

PART 2	PRODUCTS

2.1	SOIL MATERIALS

Provide soil materials as described below free of debris, roots, wood, scrap material, vegetable matter, refuse, soft unsound particles, ice, or other deleterious and objectionable materials.  Unless otherwise noted, maximum particle size permitted is 3 inches.  Use excavated material from the SITE for the work indicated when material falls within the requirements specified herein.

No soft, spongy, highly plastic, or otherwise unstable material is permitted.  Material shall be unclassified but shall contain sufficient fines to ensure proper compaction.  Material shall be classified as GP, GM, GC, SP or SM, by ASTM D 2487.  If more material is required than is available from on-site excavation, then provide that material from approved sources.

All soil materials brought to the site from offsite sources (including but not limited to sand, recharge bed materials, gravel, stone, borrow, and pipe bedding materials) shall be tested in accordance with Article 3.9 with all data being reported to the RE.

2.1.2	Sand (other than that used in the Recharge Bed)

Clean, coarse-grained sand, all of which passes a 3/8-inch sieve and not more than 10 percent passes a #200 sieve.

2.1.3	Recharge Bed Sand Layer

Clean, washed, coarse-grained 6 x 12 (1.7 – 3.4 mm) rounded sand /gravel, not crushed.

2.1.4	Gravel and Crushed Stone

Clean, coarsely graded natural gravel, crushed stone or a combination thereof meeting the following requirements:

Percent Passing by Weight

Sieve Size		             Nominal Size

½"  	   3/4"   	    2"

2-1/2"			100

2"			90 - 100

1-1/2"			35 - 70

1"		100	0 - 15

3/4"	100	90 - 100

½"	90 - 100	20 - 15	0 - 5

3/8"	40 - 70	0 - 15

No. 4	0 - 15	0 - 5

No. 8	0 - 5	-

2.1.5	Borrow

Borrow material shall meet requirements for the backfill for which it is intended to be used.  Obtain borrow materials in excess of those furnished from excavations described herein from tested sources within FAA property, if available.  If untested sources are proposed, the Contractor shall be responsible for all testing requirements.

2.1.6	Pipe Bedding

Provide material for specific types of pipe bedding as described in the following Table 2.1.6-1 for pipe material listed.

Table 2.1.6-1

Pipe Material	Spec. Article	Bedding material

a.	PVC	2.1.2 or 2.1.4	Sand or ½" Gravel

b.	Copper or Steel	2.1.2 or 2.1.4	Sand or ½" Gravel

c.	Electrical Conduit	2.1.2	Sand

d.	Polyethylene	2.1.2	Sand

e.	RCP	2.1.2	Sand

2.2	BURIED WARNING AND IDENTIFICATION TAPE

Polyethylene plastic and metallic core or metallic-faced, acid- and alkali-resistant, polyethylene plastic warning tape manufactured specifically for warning and identification of buried utility lines.  Provide tape on rolls, 3-inch-minimum width, color coded as stated below for the intended utility with warning and identification imprinted in bold black letters continuously over the entire tape length.  Warning and identification to read, “CAUTION, BURIED (intended service) LINE BELOW” or similar wording.  Color and printing is to be permanent, unaffected by moisture or soil.

Warning Tape Color Codes

Red:	Electric

Orange:	Telephone and Other Communications

Blue:	Water Systems

2.2.1	Warning Tape for Metallic Piping:  Acid and alkali-resistant polyethylene plastic tape conforming to the width, color, and printing requirements indicated above.  Minimum thickness of the tape shall be 0.003 inch.  Tape shall have a minimum strength of 1500 psi lengthwise and 1250 psi crosswise with a maximum 350 percent elongation.

2.2.2	Detectable Warning Tape for Non-Metallic Piping:  Polyethylene plastic tape conforming to the width, color, and printing requirements indicated above.  Minimum thickness of the tape shall be 0.004 inch.  Tape shall have a minimum strength of 1500 psi lengthwise and 1250 psi crosswise.  The tape shall be manufactured with integral wires, foil backing, or other means of enabling detection by a metal detector when the tape is buried up to 3 feet deep.  Encase the metallic element of the tape in a protective jacket or provide with other means of corrosion protection.

2.3	RECHARGE BED MATERIALS (OTHER THAN BED SAND)

2.3.1	Scrim/String Reinforced LDPE Liner

The Scrim/String Reinforced LDPE Liner to be place above the Recharge Bed is a 6 mil (.006” thick) LDPE material with a cross-patterned polyester tie cord between layers to provide strength and tear resistance.  Liner shall meet ASTM D751-95.  Liner shall be as distributed by McMaster-Carr Part No. 85505K16 or approved equal.

2.3.2	Non-woven Filter Fabric

Nonwoven needle punched geotextile made of 100% polypropylene staple filaments.  The density shall be 7.0 oz/sy.  The product shall conform to the following test methods and values.

Property	Test Method	Value

Tensile Strength	ASTM D 4632	180 lbs

Elongation Break	ASTM D 4632	50 %

Mullen Burst	ASTM D 3786	350 psi

U.V. Resistance	ASTM 4335	70 %

Trapezoidal Tear 	ASTM D 4533	75 lbs

Puncture Strength	ASTM D 4833	105 lbs

AOS		ASTM D 4751	70 U.S. Std Sieve

Permittivity	ASTM D 4491	1.5 Sec-1

Flow Rate	ASTM D 4491	100 gal/min/sf

2.3.3	Tri-planar Drainage Grid

The drainage geocomposite shall be comprised of a tri-axial geonet structure consisting of thick supporting ribs with diagonally placed top and bottom ribs with thermally bonded nonwoven geotextiles on both sides.   The product shall conform to the following test methods and values.

Property	Test Method	Value

Density	ASTM D 1505	0.94 g/cm3

Melt Flow Index	ASTM D 1238	1.0 g/10 min

Tensile Strength - MD	ASTM D 4595	1,200 lb/ft

Thickness	ASTM D 5199	300 mil

Carbon Black	ASTM 4218	2 – 3 %

U.V. Resistance	ASTM G 154 or D 4335	70 %

Grab Tensile	ASTM D 4632	157 lbs

Tear Strength	ASTM D 4533	56 lbs

Puncture Resistance	ASTM D 4833	56 lbs

AOS		ASTM D 4751	70 U.S. Std Sieve

Permittivity	ASTM D 4491 (falling head)	0.5 Sec-1

Peel Adhesion	ASTM D7005	1.0 lb/in

The tri-planar drainage grid shall be Tenax Corporation’s Tendrain 770-2 or approved equal.

PART 3	EXECUTION

3.1	SITE PREPARATION

Refer to Section 01010, “Summary of Work” and procedural notes on the Contract Drawings for a description of the sequencing and site preparation activities.

3.1.1	Sedimentation, Erosion and Run-on Controls

Install in accordance with Section 02112, “Erosion and Sediment Control” and the Contract Drawings.

3.2	SURFACE PREPARATION

3.2.1	Clearing and Grubbing

Perform as specified in Section 02110, “Clearing and Grubbing.”

3.2.2	Stockpiling Topsoil

Strip suitable soil from the SITE where excavation or grading is indicated and stockpile separately from other excavated material.  Material unsuitable for use as topsoil shall be stockpiled and used for backfilling.  Locate topsoil so that the material can be used readily for the finished grading.  Where sufficient existing topsoil conforming to the material requirements is not available on site, provide borrow materials suitable for use as topsoil.  Protect topsoil and keep in segregated piles until needed.

  - GENERAL EXCAVATION

3.3.1	Excavation of Material from the Recharge Bed Area

Keep excavations free from water while construction is in progress.  Construct sediment berms at the bottoms of the basin as shown on the Project Drawings.  Notify the RE immediately in writing if it becomes necessary to remove hard, unstable, or otherwise unsatisfactory material or excavate to a depth greater than indicated.  Slope trench sides as necessary to meet OSHA requirements (where depth and stability of soils prohibits vertical side walls).  When excavating and/or transporting material from the Recharge Bed area, minimize the amount of compaction of the remaining soils to the maximum extent practicable.  This is especially true when traveling across the soils near the elevation of the bottom of the Recharge Bed (see Project Drawings for restrictions on construction vehicle compaction).  After the excavation reaches the elevation of the bottom of the Recharge Bed (uncovers the underlying higher permeability materials), and prior to beginning installation of Recharge Bed sand materials, the underlying materials shall be scarified to a depth of at least two feet using a dozer/grader mounted ripper, farm equipment, or other suitable means.

Material that is removed from the bed footprint and will be utilized for backfilling the Recharge Bed excavation.  Segregate the materials of mixed permeability from the low permeability materials to the extent practical.  Stockpile the differing permeablity materials separately.

If suspected contaminated soil (stained, odorous, or other) is encountered at the site, immediately stop all site activities and contact the RE.

3.3.2	Excavation for Pipe Installation

When piping is being installed in a trench, sides of trenches shall not be sloped from the bottom of the trench up to the elevation of the top of the pipe.  Keep the remainder of the trench walls as nearly vertical as possible.  Excavate ledge rock, boulders, and other unyielding material to an over depth at least 6 inches below the bottom of the pipe and appurtenances unless otherwise indicated or specified.  Blasting will not be permitted.  Over excavate soft, weak, or wet excavations as indicated.  Use gravel or sand placed in 6-inch-maximum layers to refill over depths to the proper grade.  At the option of the Contractor, the excavations may be cut to an over depth of not less than 4 inches and refilled to required grade as specified.  Grade bottom of trenches accurately to provide uniform bearing and support for each section of pipe conduit and structure on undisturbed soil, or bedding material as indicated or specified at every point along its entire length except for portions where it is necessary to excavate for bell holes and for making proper joints.  Dig bell holes and depressions for joints after trench has been graded.  Dimension of bell holes shall be as required for properly making the particular type of joint to ensure that the bell does not bear on the bottom of the excavation.  Trench dimensions shall be as indicated on the Contract Drawings.

3.3.3	Shoring and Sheeting

Sheeting, shoring and bracing are not shown on the Drawings.  Provide shoring, bracing and sheeting where required.  In addition to Section 25 of COE EM-385-1, and other requirements of this Contract meet the following requirements:

a.	Prevent undermining of pavements, foundations and slabs.

b.	Slope banks where space permits.

c.	Remove all shoring and sheeting materials when work has been completed.

3.3.4	Dewatering

Dewatering may be required.  Any dewatering water encountered north of the proposed new small access bridge location shall be temporarily containerized and transported to the water treatment plant for treatment.  Any dewatering water encountered south of the proposed new small access bridge location may be discharged to the ground surface through a discharge structure as shown on the Project Plans.  The water shall be discharged outside of any wetlands.

If minor amounts of water are observed during trenching for piping, ½-inch gravel may be used to fill the trench to the level of the water.  In no case shall gravel be installed when water is present in the trench at the required piping depth.

Remove and dispose of surface runoff water which may accumulate in open excavations, unfinished fills, or stump holes prior to soil removal and backfilling operations, as described above.

3.3.5	Protection and Restoration of Surfaces

Protect newly graded areas from traffic, erosion, and settlements.  Repair and reestablish damaged or eroded slopes, elevations or grades and restore surface construction prior to acceptance.  Protect existing streams, ditches and storm drain inlets from water-borne soil by means of filter fabric fences.  Conduct work in accordance with requirements specified in Section 01560, “Environmental Protection.”

3.3.6	Disposal of Excavated Material

It is anticipated that all materials excavated from the Recharge Bed area will be reused for backfilling.  Removal of excess excavated material shall be approved by the RE.

Any excess excavated material to be removed from the site shall be stockpiled in an area at the FAA Facility designated by the RE.  Stockpile excavated material in such a manner that it will not obstruct the flow of runoff, streams, endanger a partly finished structure, impair the efficiency or appearance of facilities, or be detrimental to site work or operations.

3.3.7	Excavations for Structures

Excavate to depth indicated on the Contract Drawings.  If excavation is deeper than indicated, then fill with compacted granular subbase material prior to placement of structures.

3.4	GENERAL BACKFILLING AND COMPACTION

Remove all wood, metal paper, organic debris, or other deleterious and objectionable materials prior to backfill placement.  Prior to placement of fill materials, ensure that areas to be filled are free from standing water, frost, frozen materials, trash, and debris.

Backfilling and compaction shall be segregated into three distinct operations:  backfilling the sand for the Recharge Bed, backfilling the excavation area above the Recharge Bed, and backfilling and compacting the conveyance piping and conduit trenches.

    - Backfilling and Compacting the Sand for the Recharge Bed

Place the one-foot of coarse/gravel sand in the Recharge Bed location as shown on the Contract Drawings.  Spread the sand bed material using construction equipment that minimizes the compaction of the materials (see Project Plans).  .

    - Backfilling the Excavation Above the Recharge Bed

Material that has been removed from the Recharge Bed footprint shall be utilized to backfill the excavation.  The previously segregated material shall be placed as shown on the Contract Drawings.

The materials of mixed permeability shall be placed at the bottom of the excavation (above the bed) and be used as the backfilling proceeds toward the proposed surface grade.  The material shall be placed in lifts with a maximum depth of two feet.  While no specific compaction values are required, the material shall be compacted by passing construction equipment, used to spread the backfill, across the surface of the backfill to mitigate the formation of voids.  Use only low ground pressure (5 psi) equipment within the first three feet of the top of the recharge bed.  At least two passes shall be required.

The lower permeability materials shall be used to form a cap-like layer near the surface of the previously excavated area.  The lower permeability material shall be spread such that the entire cap-like layer is approximately the same thickness across the entire previously excavated area.  As with the materials of varying permeability, no specific compaction values are required.  The lower permeability materials shall, however, also be compacted by passing construction equipment, used to spread the backfill, across the surface of the backfill.  At least two passes shall be required.

The surface of the previously excavated area shall be re-graded per the Contract Drawings.

    - Backfilling and Compacting Utility Trenches

Excavate utility trenches in accordance with Article 3.3.2.  Backfill using material described in Articles 1.3.9 and 2.1.6 and previously excavated native trench material meeting the backfill requirements.    Place bedding and backfill material as shown on the Contract Drawings.  Compact backfill material in accordance with Article 3.5.2.

3.4.4	Filling and Backfilling Beside Structures

Place backfill adjacent to structures and compact to prevent wedging action or eccentric loading upon or against the structures.  Step or serrate slopes bounding or within areas to be backfilled to prevent sliding of the fill.  Do not use equipment for backfilling operations or for the formation of embankments against structures that will overload the structure.  Construct backfill for storm drains, manholes, utility lines, and other utility appurtenances using the material and compaction requirements specified herein for the adjacent or overlying work.  Backfilling against concrete shall be done only after approval has been obtained from the RE.

3.4.5	Final Backfill for Utilities

Construct backfill (final backfill) for manholes, utility lines, and other utility appurtenances using the material and compaction requirements specified herein for the adjacent or overlying work.  Backfilling against concrete shall be done only after the concrete has attained its 28-day compressive strength or that it is demonstrated that sufficient strength has been obtained to fully protect the utility.

3.4.6	Weather Limitations

Fill and backfill shall not be constructed when weather conditions detrimentally affect the quality of the finished course.  Place fill and backfill only if the atmospheric temperature is above freezing in the shade and is rising.  Do not construct fill and backfill in the rain or on saturated subgrades.  If weather conditions are windy, hot or arid, with high rate of evaporation, schedule the placement in cooler portions of the day and furnish equipment to add moisture to the fill or backfill during and after placement.

3.5	GENERAL COMPACTION

Use hand-operated, plate-type, vibratory, or other suitable hand tampers in areas not accessible to larger rollers or compactors.  Avoid damaging pipes and protective pipe coatings.  Compact material in accordance with the following Table 3.5-1 unless otherwise specified.  If necessary, alter, change, or modify selected equipment or compaction methods to meet specified compaction requirements.

Table 3.5-1

Percent ASTM D-1557 Maximum Density

Fill, Embankment, Backfill		Cohesive	Cohesionless

and Crushed Stone		Material	Material

Under footings, building slabs,		  95	  95

steps, septic tank and secondary

pavements

Under grassed areas		  85	  85

Adjacent to structures		  90	  95

Refill undercut materials		 N/A	100

3.5.1	Compaction of Material for Subcuts or Overexcavations

In soft, weak, or wet soils, tamp material to consolidate to density of adjacent material in trench wall.  In stable soils, compact to 90 percent of ASTM D 1557 maximum density.

3.5.2	Compaction of Pipe and Conduit Bedding

Compact to 90 percent of ASTM D 1557 maximum density except where higher values are specified adjacent to, or under, structures or for refilling undercuts.

3.5.3	Compaction of Backfill

Compact initial backfill overlying pipes, cables, conduits, or ducts, to 85 percent of ASTM D 1557 maximum density except where bedding and backfill are the same material.  Where bedding and backfill are the same material, compact initial backfill to the density of the bedding.  For utilities under driveways, building slabs or other areas to be paved compact succeeding layers of final backfill as specified under paragraph entitled “Special Earthwork Installation Requirements.”

3.6	SPECIAL EARTHWORK INSTALLATION REQUIREMENTS

3.6.1	Roads, Streets, and Gravel Surfaces

Place final backfill in 6-inch-maximum loose lifts.  If a vibratory roller is used for compaction of final backfill, the lift thickness can be increased to 9 inches.  Compact all backfill and bedding surrounding pipes, ducts, conduits, and other structures to 90 percent of ASTM D 1557 maximum density except compact the top 12 inches of subgrade to 95 percent of ASTM D 1557 maximum density.  Backfill to permit the rolling and compacting of the completed excavation with the adjoining material, providing the specified density necessary to enable paving of the area immediately after backfilling has been completed.

3.6.2	Manholes and Other Appurtenances

Provide at least 12 inches clear from outer surfaces to the embankment or shoring.  Remove rock as specified herein.  Remove unstable soil that is incapable of supporting the structure to an over depth of two feet and refill with ¾-inch gravel or sand to the proper elevation.  Refill over depths with gravel and sand to the required grade and as shown in Table 3.5-1 herein.

3.7	FINISH OPERATIONS

3.7.1	Grading

All areas covered by the project, including excavated and filled sections and adjacent transition areas, shall be uniformly smooth-graded.  The finished surface shall be reasonably smooth, compacted, and free from irregular surface changes.  The degree of finish shall be that ordinarily obtainable from blade-grader operations, except as otherwise specified. The surface of areas to be turfed shall be finished to a smoothness suitable for the application of turfing materials.

Finish to grades indicated within one-tenth of a foot.  Provide topsoil in areas to be seeded as indicated and in accordance with requirements specified in Section 02935, “Turf”.  Grade areas to drain water away from structures and to provide suitable surfaces for mowing machines.  Grade existing grades that are to remain but have been disturbed by the Contractor’s operations.

3.7.2	Finishing Subgrades Under Structures and Pavements

Finish the surface of the top lift of the fill or top of the subgrade to the elevation and cross section indicated.  The finished surface shall be smooth and of uniform texture.  Lightly scarify or blade the finished surface to bring the finished surface to within 0.2 foot of the indicated grade and to eliminate imprints made by compaction and shaping equipment.

3.7.4	Protection of Surfaces

Protect newly graded areas from traffic, erosion, and settlements that may occur and as required in Section 01560, “Environmental Protection,” and Section 02112, “Erosion and Sediment Control.”  Repair or reestablish damaged grades, elevations, or slopes.

3.8	FIELD SAMPLING AND TESTING

3.8.1	Pipe Bedding and Backfill

Test sand, gravel, bedding material and backfill for conformance to specified requirements.  Test sand and gravel gradation in accordance with ASTM C136.  Test bedding and backfill for moisture-density relations in accordance with ASTM D 1557 as specified herein.  Perform at least one of each of the required tests for each material used sufficiently in advance of construction so as not to delay work.  Provide additional tests as specified above for each change of source.

Perform density and moisture tests in randomly selected locations and in accordance with ASTM D 2992 and ASTM D 3017 as follows:

a.	Bedding and Backfill in Trenches:  One test per 100 linear feet in each lift.

- Appurtenant Structures:  One test per 400 square feet or fraction thereof in each lift.

  - OFF SITE SOURCE MATERIAL TESTING

Material brought to the site from offsite sources shall be tested in accordance with the following laboratory analytical methods: Gradation - ASTM D 422, Priority Pollutant Semivolatile Organic Compounds (SVOCs) - EPA Method 8270, Priority Pollutant Volatile Organic Compounds (VOCs) -  EPA Method 8260, Priority Pollutant Metals - EPA Method 6010 (HG Method), Pesticides -  EPA Method 8081, PCBs -  EPA Method 8082, Herbicides -  EPA Method 8151, and Soil pH - EPA Method 9045D.

The services of a qualified testing laboratory shall be engaged by the Contractor to make tests and determine acceptability of the material as listed below.  The laboratory shall be New Jersey certified for the applicable tests.

Tests for Topsoil material from off-site shall be performed at a frequency of 1 per 3,000 cubic yards or 3 per source, whichever is more stringent.

Material shall be acceptable if environmental test results show that all contaminant levels are below the lowest (most restrictive) soil cleanup criteria established by the NJDEP.

3.10	PERMITTING

The Contractor is responsible for obtaining any permits necessary to perform the excavation work.  The Contractor shall obtain the necessary permits/permission to remove the section of curbing along Tilton Road necessary to install the construction entrance as shown on the Project Plans.

END OF SECTION

SECTION 02420

MANHOLE STRUCTURES

PART 1	GENERAL

1.1	APPLICABLE PUBLICATIONS

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

FEDERAL SPECIFICATIONS (FED. SPEC.)

RR-F-621C	Frames, Covers, Gratings, Steps, Sump and Catch Basin, Manhole

TT-C-490B	Cleaning Methods and Pretreatment of Ferrous Surfaces for Organic Coatings

TT-E-489G	Enamel, Alkyd, Gloss (for Exterior and Interior Surfaces)

TT-P-645A	Primer, Paint, Zinc Chromate, Alkyd Type

AMERICAN CONCRETE INSTITUTE

ACI 315	1980 (Rev. 1986) Details and Detailing of Concrete Reinforcement

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM C 478	1993 Precast Reinforced Concrete Manhole Sections

ASTM C 834	1991 Latex Sealing Compounds

ASTM C 920	1987 Elastomeric Joint Sealants

ASTM A 615	1990 Deformed and Plain Billet Steel Bars for Concrete Reinforcement

ASTM D 4101	1992 (Rev. A) Propylene Plastic Injection and Extrusion Materials

1.2	SUMMARY

This section applies to manholes associated with the control vaults as shown on the Contract Drawings.

1.3	SUBMITTALS

1.3.1	Shop Drawings; GA

Submit shop drawings for the following:

a.	Precast concrete structures; GA

b.	Structure frames and covers; GA

c.	Concrete reinforcement in accordance with ACI 315; GA

1.3.2	Manufacturer’s Data; GA

Submit manufacturer's standard drawings or catalog cuts of the following items:

a.	Fittings; GA

b.	Joints and couplings; GA

c.	Gaskets; GA

d.	Wall penetration sleeves; GA

e.	Manhole steps; GA

1.3.3	Manufacturers’ Certificates of Conformance; GA

Submit manufacturer’s certificates of conformance or compliance for each of the following materials which are specified to conform to publications referenced under paragraph, “MATERIALS,” in this section:

a.	Precast concrete manhole sections; GA

All tests required by each applicable referenced publication shall have been performed, whether specified in that publication to be mandatory or otherwise.  For tests which are not specified in the referenced publications to be performed at definite intervals during manufacture, the tests shall have been performed within 3 years of the date of submittal of certificates on the same type, class, grade, and size of material as is being provided for the project.

1.4	DELIVERY, STORAGE, AND HANDLING OF MATERIALS

1.4.1	Cement and Lime (if applicable)

Store cement and lime immediately upon receipt at site of work.  Cement in ripped bags at time of delivery shall be rejected.  Store bagged cement and lime in a suitable waterproof structure which has been made as air-tight as practicable, and which has floors elevated above ground a sufficient distance to prevent absorption of moisture.  Stack bags close together to reduce circulation of air, but do not stack against outside walls; arrange storage to permit easy access for inspection and identification of each shipment.  Transfer bulk cement and lime to elevated weatherproof and air-tight bins.  Use cement in the chronological order in which it is delivered to the job site.  At the time of use, cement and lime shall be free-flowing and free of lumps.  Cement or lime that has been in storage longer than 6 months will be tested by standard mortar tests or other tests as deemed necessary to determine its suitability for use, and such cement or lime shall not be used without approval.

1.4.2	Precast Concrete Manholes

Handle precast manhole sections with care to avoid chipping and breakage; store as directed.  Protect precast concrete from contact with the earth and exposure to weather; keep dry until used.  Use of precast concrete containing frost will not be permitted.

1.4.3	Metal Items (Except Concrete Reinforcement)

Check upon arrival; identify and segregate as to types, functions, and sizes.  Store in a manner affording easy accessibility and not causing excessive rusting or coating with grease or other objectionable materials.

1.4.4	Aggregates

Store aggregates on areas covered with tightly laid wood planks, sheet-metal, or other hard and clean material.  Store aggregates of different sizes in separate piles.  Store masonry mortar aggregates separately from concrete aggregates.  Build  stockpiles of coarse aggregate in horizontal layers not exceeding 4 feet in depth to minimize segregation.  Should coarse aggregate become segregated, remix to conform to the applicable grading requirements.

PART 2	PRODUCTS

2.1	MANHOLES

The system shall include watertight precast concrete manholes, frames and covers and appurtenances.

2.1.1	Manholes

2.1.1.1	Watertight Manholes

All manhole structures, frames and covers shall be watertight.  Provide watertight manholes at the locations indicated, constructed as indicated on the Drawings.

2.2	MATERIALS

2.2.1	Manholes

Manholes to be constructed as shown on the Contract Drawings and consisting of precast concrete units with ASTM A615 reinforcing steel capable of supporting H20 traffic loading.

2.2.2	Manhole Covers

Covers (frames and hatches) for the manhole structures shall be as shown on the Contract Drawings and capable of supporting H20 traffic loading.  Covers (hatches) shall be as manufactured by Pennsylvania Insert Corporation or approved equal.

2.2.3	Sealant and Caulking

Sealant and caulking shall conform to ASTM C 834 or ASTM C 920.  For joints in vertical surfaces, provide ASTM C920, Type S or M, Grade NS, Class 25, Use NT.  For joints in horizontal surface, provide ASTM C 920, Type S or M, Grade P, Class 25, Use T.  Provide a sealant compatible with the material(s) to which it is applied.  Do not use a sealant that has exceeded shelf life or has jelled and cannot be discharged in a continuous flow from the gun.  Apply sealant in accordance with the manufacturer instructions with a gun having a nozzle that fits the joint width.  Force sealant into joints to fill the joints solidly without air pockets.

2.2.4	Steps

Install into base, riser, and top sections sidewall at 12- to 16-inch intervals.

2.2.3.1	Plastic

Co-polymer polypropylene plastic in accordance with ASTM D 4101; as shown on the Project Plans.

2.2.3.2	Steel Bar

As shown on the Project Plans.

PART 3	EXECUTION

3.1	MANHOLE CONSTRUCTION

Seal all joints and opening with sealant with the limits of 40 and 100 degrees F.

Use precast concrete units meeting ASTM C478.  Construct all manhole structures with precast concrete sections.  For precast concrete construction, make joints between sections with rubber gaskets and watertight.  Give a smooth finish to inside joints of precast concrete manholes.  Parging will not be required for precast concrete manholes.

Steel sleeves for passing pipes shall be cast into the manhole.  The annular space between the steel pipe sleeve and passing pipe shall be made water tight through the use of a Link-Seal® type (or approved equal) mechanical seal.  All mechanical seal hardware (nuts, bolts, etc.) shall be stainless steel.  The annular space shall be 2-inches from the exterior of the passing pipe to the inside of the steel pipe sleeve, or as required by the mechanical seal manufacturer to produce a watertight seal.

All buried exterior manhole surfaces shall be completely coated with two (2) layers of bitumastic waterproofing sealant.

3.2	METAL WORK

3.2.1	Workmanship and Finish

Manhole frames, covers and gratings shall be of watertight type.  Seal watertight all joints and openings.  For surfaces contaminated with rust, dirt, oil, grease, or other contaminants, wash with solvents until thoroughly clean.  Immediately after cleaning, coat surfaces with a coat of pretreatment coating, Mil. Spec. MIL-C-15328, applied to a dry film thickness of 0.3 to 0.5 mil; or apply a crystalline phosphate coating, Fed. Spec. TT-C-490, Method I, Type II.  As soon as practicable after the pretreatment coating has dried, prime treated surfaces with a coat of zinc chromate primer, Fed. Spec. TT-P-645, applied to a minimum dry film thickness of 1.0 mil.  If primed surfaces are damaged before removal from the shop, retouch with primer.

3.3	FIELD TESTS AND INSPECTIONS, GENERAL

The Resident Engineer (RE) will conduct field inspections and witness all field tests specified in this section.  The Contractor shall perform all field tests and provide all labor, equipment, and incidentals required for testing.  The Contractor shall be able to produce evidence, when required, that any item of work has been constructed properly in accordance with the drawings and specifications.

END OF SECTION

SECTION 02713

SITE PIPING SYSTEMS

PART 1	GENERAL

1.1	SUMMARY

1.2	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

AMERICAN ASSOCIATION OF STATE HIGHWAY AND TRANSPORTATION OFFICIALS (AASHTO)

AASHTO M 294 	Corrugated Polyethylene Pipe, 300- to 1200-mm Diameter

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM A53	Specification for Threaded Seamless Galvanized Steel Pipe

ASTM D1248	Specification for Polyethylene Plastics Molding and Extrusion Materials

ASTM D2241	Poly (Vinyl Chloride) (PVC) Plastic Pipe (SDR-PR)

ASTM D 2321	Standard Practice for Underground Installation of Thermoplastic Pipe for Sewers and Other Gravity-Flow Applications.

ASTM D 3212	Standard Specification for Joints and Sewer Plastic Piping Using Elastomeric Seals

ASTM D3139	Joints for Plastic Pressure Pipes Using Flexible Elastomeric Seals

ASTM D3350	Polyethylene Plastic Pipe and Fittings Materials

ASTM F477	Elastomeric Seals (Gaskets) for Joining Plastic Pipe

AMERICAN SOCIETY OF MECHANICAL ENGINEERS (ASME)

ASME B16.3	Malleble Iron Threaded Fittings

AMERICAN WATER WORKS ASSOCIATION (AWWA)

AWWA C111	Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings

AWWA C605	Underground Installation of PVC Pressure Pipe and Fittings for Water.

AWWA C800	Underground Service Line Valves and Fittings

MANUFACTURES STANDARDIZATION SOCIETY OF THE VALVE AND FITTINGS INDUSTRY (MSS)

MSS SP-58	Pipe Hangers and Supports - Materials, Design and Manufacture

MSS SP-70	Cast Iron Gate Valves, Flanged and Threaded Ends

MSS SP-80	Bronze Gate, Globe, Angle and Check Valves

MSS SP-71	Cast Iron Swing Check Valves, Flanged and Threaded Ends

THE PLASTIC PIPE INSTITUTE (PPI)

TR-31	Underground Installation of Polyolefin Piping

UNI-BELL PLASTIC PIPE ASSOCIATION (UNI)

UNI B3	Installation of Polyvinyl Chloride (PVC) Pressure Pipe Complying with AWWA Standard C-900.

1.3	DESCRIPTION OF WORK

The work includes providing new piping systems and related work.  Provide each system complete and ready for operation.  Piping systems including piping, fittings, valves, flow meters, pressure sensors, materials, installation, and workmanship shall be as specified herein.

1.4	SUBMITTALS

Submit the following in accordance with Section 01330, “Submitted Procedures.”

1.4.1	SD-01 Data; GA

Manufacturer's Data:

- Pipe, fittings, joints, couplings, and gaskets (separate submittal for each type of piping, fitting, joint, coupling, gasket, etc.)

- Flexible Coupling

- Repair Coupling

- Wall Penetration Seals

- Pipe Supports

- Others as required by the Resident Engineer (RE)

1.4.2	SD-13 Certificates; GA

Manufacturer’s Certificate of Conformance:

a.	Pipe and fittings, including shop-applied linings and coatings

b.	Pipe joint materials

c.	Flexible Coupling

d.	Repair Coupling

e.	Others as required by the RE

Resin Certification; GA

Certified copies of test reports demonstrating conformance to applicable pipe specifications, before pipe is installed. Certification on the ability of frame and cover or gratings to carry the imposed live load.

1.5	QUALITY ASSURANCE, DELIVERY AND STORAGE, AND HANDLING OF MATERIALS

1.5.1	Quality Assurance

All materials supplied and the installation shall conform to the applicable standards referenced.  All materials provided shall be new.

Provide materials and equipment that are standard products of manufacturers regularly engaged in the manufacture of such products, which are of similar material design and workmanship.  Standard products shall have been in satisfactory commercial or industrial use for 2 years prior to bid opening.  The 2 year use shall include applications of equipment and materials under similar circumstances and of similar size.

1.5.2	Delivery and Storage

Inspect materials delivered to site for damage.  Unload and store with minimum handling.  Store materials in enclosures or under protective covering.  Store rubber gaskets and plastic piping not to be installed immediately under cover, out of direct sunlight.  Do not store materials directly on the ground.  Keep interior of pipes and fittings free of dirt and debris.

1.5.3	Handling

Handle pipe, fittings, valves and other accessories in such manner as to ensure delivery to the trench in sound, undamaged condition.  Avoid injury to coatings and linings on pipe and fittings; make satisfactory repairs if coatings or linings are damaged.  Carry pipe to the trench; do no drag it.

1.6	EXCAVATION, TRENCHING, AND BACKFILLING

Provide in accordance with Section 02225, “Excavation, Backfilling, and Compacting” except as specified herein.

PART 2	PRODUCTS

2.1	MATERIALS FOR PIPING

Piping systems shall installed as shown in the project drawings.

2.1.1	Polyvinyl Chloride (PVC) Pipe and Fittings (if required)

All PVC pipe and fittings shall be Schedule 40, unless otherwise specified, as shown on the project drawings.  Pipe shall be Type I, Grade 1 conforming to the requirements of ASTM-D-1784 and ASTM-D-1785.  Pipe shall be rigid, homogeneous throughout, and free from visible cracks, holes, foreign inclusions, and other defects.  All PVC pipe and fittings shall be installed with socket-type joints conforming to the requirements of ASTM D-2466 or D-2467 (Sch. 80) using PVC solvent cement, conforming to ASTM D-2564, or with flanged or screwed joints conforming to ASTM D-2464, where necessary to connect to valves, equipment or existing piping.  Gaskets for flanged connections shall be full faced elastomeric Viton, durometer A scale 55 to 80, 1/8-inch thick.

2.1.2	Polyethylene Pipe

Polyethylene piping material and fittings shall be Type III C5 P34 as tabulated in ASTM D-1248, and have recommended designation values of 3-3-5-4-3-3-C or better as referenced in ASTM D 3350.

The polyethylene pipe shall have a minimum rating of 100 psi and minimum thickness equivalent to SDR-11 or as shown on the Contract Drawings.

The pipe shall be homogeneous throughout and free from visible cracks, holes, foreign materials, blisters, wrinkles and dents.

The pipe shall be marked with an easily legible and permanent surface mark specifically identifying the manufacturers by name or trademark and the size, schedule, and type of pipe.

All polyethylene piping and fittings shall be joined by the heat fusion process producing homogeneous sealed, leak-tight joints in accordance with manufacturer’s recommendations and procedures.

2.1.3	Perforated Corrugated HDPE Pipe with Integral Wall Liner (Recharge Bed Distribution Piping)

AASHTO M 294, Type S, for pipes 12 to 36 inches.  Type S piping shall be produced from PE certified by the resin producer as meeting the requirements of ASTM D 3350, minimum cell class 324420C, except that the carbon black content shall not exceed 5%.  Pipe walls shall have the following properties:

Minimum Moment

Nominal 			Minimum 			of Inertia of

Size			Wall Area 			Wall Section

(in.) 			(square in/ft) 			(in to the 4th/in)

12 				1.50 				0.024

Piping shall have integrally formed smooth interior waterway.

All perforations shall conform to AASHTO M294.  The pipes shall be perforated with 0.375" holes every 60( around the pipe circumference with a minimum inlet open area of no less than 4.14 in2/ft for 12" diameter pipe.  The perforations shall be located in the outside valleys of each of the corrugations.

All HDPE distribution piping for this project, shall include water tight joints.

Water tight joints shall be made using a PVC or PE coupling and rubber gaskets as recommended by the pipe manufacturer. Rubber gaskets shall conform to ASTM F 477 and shall be constructed to meet a laboratory pressure test of 10.8 psi per ASTM D 3212.

Gaskets and jointing materials shall be as recommended by the particular manufacturer in regard to use of lubricants, cements, adhesives, and other special installation requirements. Surfaces to receive lubricants, cements, or adhesives shall be clean and dry. Gaskets and jointing materials shall be affixed to the pipe not more than 24 hours prior to the installation of the pipe, and shall be protected from the sun, blowing dust, and other deleterious agents at all times. Gaskets and jointing materials shall be inspected before installing the pipe; any loose or improperly affixed gaskets and jointing materials shall be removed and replaced. The pipe shall be aligned with the previously installed pipe, and the joint pushed home. If, while the joint is being made the gasket becomes visibly dislocated the pipe shall be removed and the joint remade.

Piping shall be capable of supporting H-25 live loads with 12” minimum cover.

All necessary watertight fittings needed to transition from the HDPE piping downcomers and risers shall be provided where necessary.

Piping shall be ADS N-12® or approved equal.  Joints shall be watertight and equal to ADS N-12 Pro Link WT®.

2.1.4	Insulating Joints (if required)

Joints between pipe of dissimilar metals shall have a rubber gasket or other approved type of insulating joint or dielectric coupling which will effectively prevent metal-to-metal contact between adjacent sections of piping.

2.1.5	Polyethylene Pipe Compression Gasket Fittings

Compression gaskets shall be manufactured and tested in accordance with AWWA C800.  The compression gasket shall be constructed of corrosion resistant cast bronze for underground use and shall be installed with a stainless steel liner as recommended by the manufacturer for use with plastic pipe.

2.1.6	Accessories

Provide flanges, connecting pieces, transition glands, transition sleeves, and other adapters as required.

2.2	PIPE SUPPORTS AND HANGERS

All piping shall be supported in a substantial manner to prevent sagging, vibration and noise due to vibration.  Structural members necessary or required to support, brace, or otherwise secure piping shall be furnished by Contractor unless specifically noted otherwise.  The installation shall comply with MSS SP-58 and MSS SP-69, and the latest edition of the ANSI code for Pressure Piping, B31.3 or B31.9.  Piping near floors shall be supported with adjustable saddles.

2.3	BURIED UTILITY WARNING AND IDENTIFICATION TAPE

Polyethylene plastic and metallic core or metallic-faced, acid- and alkali-resistant, polyethylene plastic warning tape manufactured specifically for warning and identification of buried utility lines.  Provide tape on rolls, 3-inch-minimum width, color coded as stated below for the intended utility with warning and identification imprinted in bold black letters continuously over the entire tape length.  Warning and identification to read, “CAUTION, BURIED (intended service) LINE BELOW” or similar wording.  Color and printing is to be permanent, unaffected by moisture or soil.

Warning Tape Color Codes

Red: Electric

Orange: Telephone and other communications

Blue: Water systems

2.4	IDENTIFICATION TAGS AND PLATES

Provide valves with tags or plates numbered and stamped for their usage.  Plates and tags shall be of brass or nonferrous materials and shall be mounted or attached to the valve.

2.5	FLEXIBLE COUPLING

Flexible couplings shall be single spool type consisting of a tube, body or a carcass and a cover.  The tube shall be a leak proof lining of natural rubber.  The body shall consist of fabric and various rubber compounds reinforced with steel rings for strength.  The cover shall be formed from natural rubber.  A special Hypalon paint shall be applied to resist weathering.  Flanges supplied with flexible couplings shall be of duck and rubber construction to resist stresses and form a tight seal with companion pipe flanges without need for gaskets.  Flanges shall be full-faced with 150 #ASME standard drilling.

2.6	REPAIR COUPLING

Repair couplings shall be single spool complete circumferential with stainless steel band and gasket resistant to volatile organic compounds and a pressure rating not less than that of the pipe.

2.7	WALL PENETRATION SEAL

Seal the space between sleeves and all pipe penetrations through concrete as shown on Contract Drawings or with a mechanical seal constructed for such purpose so as to effect a watertight seal and not exert excessive stresses to the pipe.  Seal shall be Link-Seal or approved equivalent.

PART 3	EXECUTION

3.1	INSTALLATION

Piping shall be installed principally as shown on the drawings.  Refer to the drawings to ensure all required valves, instruments and gages are provided.  In addition, provide whatever piping and fittings are necessary, whether shown on the drawings or not, for a complete and working system.  Provide also vent valves at all high points and drain valves at all low points, whether shown on the drawings or not.  Provide flanged connectors for all process valves, instruments, and gages to facilitate removal (except those items with end connections of 2 inches or less may be threaded or provided with a threaded or socket union).

These requirements shall apply to all piping except as specified otherwise.

3.1.1	General

3.1.1.1	No defective pipe or fittings shall be used in piping systems.  Any piece discovered to be defective shall be removed and replaced by a sound and satisfactory piece.

3.1.1.2	Any fitting showing a crack and any fitting or pipe which has received a severe blow that may have caused an incipient fracture, even though no such fracture can be seen, shall be marked as rejected and removed at once from work.

3.1.1.3	Every pipe and fitting shall be cleaned of all debris and dirt before being used and shall be kept clean until accepted in completed work.

3.1.1.4	Pipe and fittings shall be accurately installed to required lines and grades.  Care shall be taken to preserve a good alignment.

3.1.1.5	All joints shall be made in clean dry conditions and in strict accordance with manufacturer's recommendations.

3.1.1.6	The entire installation shall comply with the ANSI code for Pressure Piping, B31.3 or B31.9.

3.1.2	Pipe Laying and Jointing

Inspect pipe, fittings, valves, and accessories before and after installation; those found defective shall be replaced with new materials.  Remove fins and burrs from pipe and fittings.  Before placing in position, clean pipe, fittings, valves, and accessories, and maintain in a clean condition.  Provide facilities for lowering sections of pipe into trenches.  Do not drop or dump pipe, fittings, valves, or any other piping material into trenches.  Cut pipe accurately to measurements established at the site and work into place without springing or forcing.  Replace pipe or fitting that does not allow sufficient space for proper installation of joint material with new pipe or fittings or proper dimensions.  Blocking or wedging between bells and spigots will not be permitted.  Lay bell-and-spigot pipe with the bell end point in the direction of laying.  Grade the piping in straight lines; avoid the formation of any dips or low points.  Support pipe at its proper elevation and grade;  ensure firm and uniform support.  Wood support blocking will not be permitted.  Lay pipe so that the full length of each section of pipe and each fitting will rest solidly on the pipe bedding; excavate recesses to accommodate bells, joints, and couplings.  Provide anchors and supports where necessary for fastening work into place.  Make proper provisions for expansion and contraction of piping.  Keep trenches free of water until joints have been completely assembled.  At the end of each day’s work, close open ends of pipe temporarily with wood blocks or bulkheads.

3.1.3	Polyethylene Pipe and Fittings (not including perforated distribution piping)

All pipes shall be marked in accordance with the latest acceptable standards for the “Marking of Pipe” such as specified by ASME.  Mark number and weight and/or pipe schedule shall be conspicuously painted on each piece.

Any pipe which has received a severe blow that may have caused an incipient fracture, even through no such fracture can be seen, shall be marked as rejected and removed at once from the work.

Polyethylene pipe may also be joined using the sidewall fusion method in strict accordance with manufacturer’s recommendations and procedures.  Install fusion machine on main pipeline.  Clean pipe (main and branch) with a clean cotton cloth and prepare surface for fusion by roughing with 60 grit or courser utility cloth.  Align branch on the main piping and tighten clamp.  Check branch for square alignment on main.  Retract moveable clamp, roll in and center heater plate with adapter between base of branch and main.  For all sizes, apply a strong, firm, continuous pressure until complete melt bead can be seen on main.  Release pressure to light pressure.  Continue heat soak cycle on branch and main.  Watch base of branch for:

Main			Heat Soak Cycle Fitting Base Bead

1-1/4"				1/16" Melt Bead

2"					1/8" Melt Bead

3" and larger			1/8"-3/16" Melt Bead

Retract removable clamp and cleanly remove heater plate.  Bring melted surfaces together rapidly.  DO NOT SLAM.  Apply continuous progressive pressure until proper fusion bead is formed.  Maintain pressure until joint has cooled.

3.1.4	Bedding Requirements

Pipe bedding shall be as indicated on the contract drawings and comply with the requirements of Section 02225, “Excavation, Backfilling and Compacting.”

3.1.5	Pipe Anchorage

Support piping in structures in accordance with MSS SP-58, Type 1 hangers and braces.

3.2	FIELD TESTS AND INSPECTIONS

Perform all field tests, and provide all labor, equipment, and incidentals required for testing.  The Contractor shall produce evidence, when required, that any item of work has been constructed in accordance with the contract requirements.

3.2.1	Testing Procedure

The piping system shall be tested during the progress of the work over completed pipe sections as determined by the RE until all pipe has been tested.  The Contractor shall first clean and flush all lines and remove all debris.  The section of pipe being tested shall be plugged and adequately braced.  All air shall be bled from the line and completely filled with water and pressurized to 100 psi, per ANSI B31.3.  The test pressure is then maintained for one hour during which time two pressure gauges, one at each end of the piping system, are monitored for pressure loss.  The line must remain at the test pressure (+ 2%) for a minimum of one hour to pass the test procedure. Hydrostatic test water shall be properly disposed upon completion of the pressure test.

Testing for PVC pipe shall be conducted per Section 7.3 of AWWA C605 and HDPE pipe testing shall be conducted per PPITR-31.

Leakage in excess of this standard shall be repaired and pipe retested until passing.  Any visible leakage shall be repaired regardless of testing results.

3.2.2	Final Testing

All equipment shall be tested in operation for a period of 30 days to demonstrate compliance with the contract requirements.  Compliance with the contract requirements shall mean zero defects for 30 consecutive days.

END OF SECTION

SECTION 02730

ROTARY-DRILLED GROUND WATER MONITORING WELLS AND DIRECTIONAL DRILLED SYSTEM PIPING

PART I	GENERAL

1.1	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI)

B2. 1-68	Pipe Threads (Except Dryseal)

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM):

ASTM C150		1992 Portland Cement

ENVIRONMENTAL PROTECTION AGENCY (EPA)

570/9-75-001	Manual of Water Well Construction Practices

NEW JERSEY ADMINISTRATIVE CODES (NJAC)

NJAC 7:9-9.1	December 1977, Sealing of Abandoned Wells

NJAC 7:10	Safe Drinking Water Act

NEW JERSEY DEPARTMENT OF ENVIRONMENTAL PROTECTION

Field Sampling Procedures Manual, August 2005

1.2	SUBMITTALS

1.2.1	SD-06 Statements; GA

Sand Placing Equipment and Methods; GA

Provide a description of equipment and methods required to place the sand into the well borehole (see Article 3.4).

1.2.2	SD-09 Reports; GA

- Well Data and Completion Report; GA

- Permit Application Forms; GA

c.	NJDEP Monitoring Well Certification Forms A and B; GA

1.2.2.1	Well Data

Submit a geologic log with coarseness and fineness modules of each strata and time penetration log (time to drill through each formation).  Record split spoon blow count results on log.  Submit well completion diagram on each log.

1.2.2.2	Permit Application Forms

Contractor shall prepare and submit permit application form(s) for the drilling of well(s) and bore holes into ground water in accordance with NJAC 7:10-12.1 et. seq.  The Contractor shall be responsible for all fees assessed per well permit.  All wells and borings into ground water must be drilled by a New Jersey licensed well driller.  A copy of all permit applications shall be provided to the Resident Engineer (RE).

1.2.2.3	NJDEP Forms

The Contractor shall submit NJDEP forms A and B for all completed wells.  These forms can be found at the following websites:

http://www.state.nj.us/dep/srp/dl/wcerta.pdf

http://www.state.nj.us/dep/dwq/pdf/well_b.pdf

1.2.3	SD-13 Certificates; GA

a.	Well Driller License; GA

Contractor shall provide a copy of the driller's New Jersey well driller's license to the Resident Engineer (RE).

1.3	DESCRIPTION OF WORK

The work includes installing shallow monitoring wells using hollow stem auger techniques.  Each well including equipment, materials, installation, and workmanship shall be in accordance with the EPA Manual of Water Well Construction Practices, except as modified herein.

In the manual referred to herein, the advisory provisions shall be considered mandatory, as though the word “shall” has been substituted for the word “should” wherever it appears.  Reference to the “Project Representative” and the “Owner” shall be interpreted to mean the RE.  Other applicable requirements are included under Section 01560, “Environmental Protection”.

The work also includes the installation of conveyance piping using directional drilling techniques.

1.4	ABANDONMENT OF WELLS

In the event that the Contractor fails to properly construct a well and the well must be abandoned because of loss of tools or for any other cause, the Contractor shall fill the abandoned hole with cement/bentonite grout and remove the casing, at no additional cost to the government.  Refer to NJAC 7:9-9.1 et seq. for requirements for well abandonment.  All wells or borings shall be abandoned by a New Jersey licensed well driller.

PART 2	PRODUCTS

2.1	MATERIALS

Shall conform to the respective Project Documents and other requirements as specified herein.

2.1.1	Casings

Monitoring well casings will be constructed of Schedule 40 PVC materials as shown on the Contract Drawings.

2.1.2	Well Screens

Monitoring well with screens will be constructed of PVC well screen as shown on the Contract Drawings.

2.1.3	Filter Sand

Provide clean, round, uniform filter sand from U.S. Silica, Mauricetown, New Jersey or equivalent.  Silica (SiO2) content of filter sand shall exceed 95%.  The gradation of the filter sand shall be such that the uniformity coefficient is not more than 2.5.

2.1.4	Cement/Bentonite Grout

Provide cement/bentonite grout consisting of the following ratio of materials:  94 lbs of  cement/5 lbs of bentonite/6 gallons of water.

2.1.5	Bentonite Grout Powder

Provide neat bentonite grout, type Volclay( grout, a high solids (20%), polymer free grout.  The mixed grout shall contain no more than 24 gallons of water per 50 pound bag.

2.1.6	Cement

Use Portland Cement meeting the requirements of ASTM C150.

PART 3	EXECUTION

3.1	GENERAL

The Contractor shall be required to install Monitoring Wells at the locations shown and to the details and depths as indicated on the Contract Drawings.

The Contractor shall also install HDPE conveyance piping using directional drilling techniques.

3.2	WELL DRILLING

The driller shall install the monitoring wells using hollow stem auger techniques.  For the 2-inch monitoring wells, a minimum 4.25-inch inside diameter hollow stem auger shall be utilized.  Drill cuttings shall be spread on the ground surface adjacent to the well locations.

3.2.1	Special Considerations

During installation of the wells, all soil cuttings and development water shall be prevented from entering adjacent wetlands or stream using silt fencing, diking, or other means.

3.3	CASING AND WELL SCREEN

Provide threaded joints for all well casing and screen.  The monitoring well screen length is indicated on the Contract Drawings.  Install the casing and well screens concentrically in the drill hole.  Well screen and casing shall not be dropped or allowed to fall uncontrolled into the borehole.  The well screen and casing shall be lowered into the borehole by a method which will allow for control of the rate of fall at all times.

3.4	FILTER SAND ENVELOPE

Following completion of the borehole, and the screen and casing has been concentrically set in the borehole, fill the annular space between the screen and wall of the borehole with filter sand (lower filter sand).  A filter sand conductor pipe having an inside nominal diameter of not less than 1 inch shall be lowered to the bottom of the annular space between the screen and the inside of the hollow stem augers.  The filter sand conductor pipe shall be arranged and connected at the surface to water pumping and graveling equipment so that water and filter sand fed at uniform rates are discharged as the filter sand fills the annular space from the bottom up.  The filter sand conductor pipe and hollow stem augers shall be raised at a rate that will keep the bottom of the pipe and the augers at the surface of the filter sand at all times.  Dumping filter sand from the surface of the ground and agitating the well in an effort to settle the filter sand will not be allowed.  Place the filter sand at the depth intervals shown on the Contract Drawings.  The gradation of the lower filter sand shall be such that the uniformity coefficient is not more than 2.5.  Following installation of the lower filter sand, it shall be tamped with a flat ended rod to ensure the lower filter sand is tightly packed.  After placement of the lower filter sand has been completed, a layer of sand size #000 (US Silica Mauricetown, NJ or equivalent) shall be placed by the filter sand conductor pipe directly on top of the lower filter sand as shown on he Contract Drawings.  Control speed of sand placement and withdrawal of hollow stem augers to prevent bridging and to allow for settlement of the sand.  Following installation of the upper filter sand, it shall be tamped with a flat ended rod to ensure the upper filter sand is tightly pressed against the lower filter sand pack.  Equipment and methods required to place the sand shall be approved by the RE prior to commencement of work.

3.5	GROUTING

Following installation of the upper filter sand envelope, a cement/bentonite grout shall be installed.  The grout shall be installed by extending a tremie pipe to the top of the upper filter sand and grouting slowly by filling the annular space with grout and retracting the grout pipe and hollow stem augers at the rate the grout fills the space.

3.6	WELL DEVELOPMENT

Following the completion of each monitoring well, well development shall be conducted by the surge block and submersible pump technique.  The surge block will be used to draw fine-grained material into the wells and a submersible pump outfitted with drinking-grade polyethylene tubing will be used for removing water from the wells.  The monitoring wells will be developed for approximately two hours or until such time as turbidity readings remain less than 30 NTU and stabilize for a period of 30 minutes.  The surge block and submersible pump shall be properly decontaminated as described in NJDEP’s Field Sampling Procedures Manual (August 2005) prior to being used in each well.  Clean, new tubing shall also be used for each well.

Well development water originating from the monitoring wells shall be discharged directly onto the ground into a temporary sediment structure (see Article 3.2.1), to mitigate soil erosion.

3.7	DIRECTIONAL DRILLING

System piping shall be installed via directional drilling for one wetlands crossing, at Area B as indicated on the Contract Drawings.  The directional drilling shall allow the installation of the piping to the required depth without any disturbance to existing structures, piping or wetlands.  The directional drilling shall be installed as described below.

Directional drilling is governed by the geometry of each situation.  The drill rig shall be positioned on the ground surface with the drill angled at the necessary entry angle (typically 12 to 14 degrees from the horizontal).  The direction of the drill shall be controlled by a sensor placed behind the drill head or other mean approved by the RE.  The sensor shall allow manual tracking of the depth and position of the drill head.  The directional drill crossing procedure shall use a bentonite-based slurry to drive the cutting or jetting head and stabilize the hole against collapse.  Drilling slurry returns shall be collected in a bentonite receiving pit located at the drill entry point.  The Contractor shall construct an earth dug pit as shown on the Project Plans surrounded by lined straw bales or silt fence.  Once bentonite returns to the pit, it shall be pumped into steel tanks and processed through a solids control system which removes spoil from the drilling slurry, allowing the slurry to be reused.  No drilling slurry or spoils shall be discharged on-site.  Any drilling slurry or spoils remaining upon completion of the directional drilling shall be collected, properly handled and disposed of in accordance with Federal, state and municipal regulations.  Once the initial borehole is completed, if necessary, a larger backreaming bit shall be used to expand the borehole diameter.  The backreaming process shall be repeated with larger diameter backreaming bits until the borehole reaches the required diameter as indicated on the Contract Drawings.  After the final backreaming pass, the HDPE piping shall be pulled through the drill hole without the use of steel casing.

The upland staging areas for drilling equipment at entry and exit points shall be enclosed with straw bales and Best Management Practices shall be used for protection of the environment and to prevent soil erosion and sedimentation, as indicated on the Contract Drawings.  Material excavated from the entry and exit points shall be temporarily sidecast in upland areas.  Disturbed areas shall be restored to pre-construction grade and reseeded immediately upon completion of piping installation.

Contractors may propose alternate directional drilling or pushing techniques to the RE for approval.  The RE retains the right to approve or disapprove any alternate techniques.

SECTION 02831

FENCE, CHAIN LINK

PART 1	GENERAL

1.1	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM F 883		1990 Padlocks

ASTM C 94		1992 (Rev. A) Ready-Mixed Concrete

FEDERAL SPECIFICATIONS (FS)

FS RR-F-191	(Rev. K) Fencing, Wire and Post Metal (and Gates, Chain-Link Fence Fabric, and Accessories) (General Specification)

FS RR-F-191/1	(Rev. D) Fencing, Wire and Post, Metal (Chain-Link Fence Fabric) (Detail Specification)

FS RR-F-191/2	(Rev. D) Fencing, Wire and Post, Metal (Chain-Link Fence Gates) (Detail Specification)

FS RR-F-191/3	(Rev. D) Fencing, Wire and Post, Metal (Chain-Link Fence Posts, Top Rails and Braces) (Detail Specification)

FS RR-F-191/4	(Rev. D) Fencing, Wire and Post, Metal (Chain-Link Fence Accessories) (Detail Specification)

1.2	SUBMITTALS

Submit the following in accordance with Section 01330, “Submittal Procedures.”

1.2.1	SD-02, Manufacturer’s Catalog Data

a.	Chain-link fencing components

b.	Accessories

1.2.2	SD-04, Drawings

a.	Gates

b.	Post spacing

c.	Location of gate, corner, end, and pull posts

1.2.3	SD-06, Instructions

a.	Fence

1.2.4	SD-10, Test Reports

a.	Weight in ounces for zinc coating

1.2.4.1	Required Report Data

Submit reports of listing of chain-link fencing and accessories regarding weight in ounces for zinc coating.

1.2.5	SD-13, Certificates

a.	Fabric

b.	Posts

c.	Braces

d.	Framing

e.	Rails

f.	Tension wires

g.	Gates

h.	Padlocks

1.3	DELIVERY, STORAGE, AND HANDLING

Deliver materials to SITE in an undamaged condition.  Store materials off the ground to provide protection against oxidation caused by ground contact.

PART 2	PRODUCTS

2.1	CHAIN-LINK FENCING AND ACCESSORIES

FS RR-F-191 and detailed specifications as referenced and other requirements as specified.  All posts, fabric, clips, caps, rods, etc., shall be galvanized steel.

2.1.1	Fabric

FS RR-F-191/1; I, zinc-coated steel, 9-gage core wire size.  Diamond mesh size, 2 inches.  Provide selvage knuckled at one selvage and twisted and barbed at the other.  Height of fabric, as indicated.

2.1.2	Gates

FS RR-F-191/2; Type II, double swing.  Shape and size of gate frame, as indicated on Contract Drawings.  Framing and bracing members, round of galvanized steel.  Gate frames and braces of minimum sizes listed in FS RR-F-191/3 for each Class and Grade except that steel pipe frames shall be 1.90 inches O.D., 0.120 inches minimum wall thickness.  Gate fabric, as specified for fencing fabric.  All steel latches, stops, hinges, keepers, and accessories, shall be galvanized.  Gate leaves less than 8 feet wide shall have truss rods or intermediate braces.  Attach gate fabric to gate frame in accordance with manufacturer’s standards, except that welding will not be permitted. Arrange padlocking latches to be accessible from both sides of gate, regardless of latching arrangement.

2.1.3	Fencing Accessories

FS RR-F-191/4.  Provide accessories with coatings similar to that specified for chain-link fabric or framework.  Provide all necessary accessory items (posts, post caps, clips, ties, bands, loop caps, collars, gate latches, gate stops, keepers, etc.) to provide a complete working fence system.

2.1.4	Post, Braces, and Rails

Steel pipe, Class 1, Grade B galvanized

2.1.5	Tension Wire

Seven (7) gauge

2.1.6	Concrete

Provide 3,000 psi concrete (ASTM C 94).

2.1.7	Padlocks

ASTM F 883, with chain.

PART 3	EXECUTION

3.1	SITE PREPARATION

3.1.1	Clearing and Grading

Where necessary, clear fence line of trees, brush, and other obstacles to install fencing as specified in Section 02110, “Clearing and Grubbing”.  Establish a graded, compacted fence line prior to fencing installation.  Compact fill used to establish fence line.

3.1.2	Excavation

Excavate to dimensions indicated for concrete-embedded items, except in bedrock.  Clear post holes of loose material.

3.2	FENCE INSTALLATION

Install fence on prepared surfaces to line and grade indicated.  Install fence in accordance with fence manufacturer’s written installation instructions except as modified herein.

3.2.1	Post Spacing

Provide line posts spaced equidistantly apart, not exceeding 10-feet on center.  Provide gate posts spaced as necessary for size of gate openings.  Do not exceed 500 feet on straight runs between braced posts.  Provide corner or pull posts, with bracing in both directions, for changes in direction of 15 degrees or more, or for abrupt changes in grade.  Provide drawings showing location of gate, corner, end, and pull posts.

3.2.2	Post Setting

Set posts plumb.  Allow concrete to cure a minimum of 72 hours before performing other work on posts.

3.2.2.1	Earth

Provide concrete bases of dimensions indicated.  Compact/agitate/vibrate concrete to eliminate voids, and finish to a dome shape.

3.2.3	Bracing

Brace gate, corner, end, and pull posts to nearest post with a horizontal brace used as a compression member, placed at least 12 inches below top of fence, and a diagonal truss rod and truss tightener used as a tension member.

3.2.4	Top Rail and Tension Wires

Install top rail and top tension wire tension wire as shown on the drawings.  Before installing chain-link fabric, pull wires taut.  Place top rail/tension wires within 8 inches of respective fabric line.

3.2.5	Fabric

Pull fabric taut and secure fabric to top wire and bottom wire, close to both sides of each post and at maximum intervals of 24 inches on center.  Secure fabric to posts using stretcher bars, ties or clips spaced 15 inches on center, or by integrally weaving to integral fastening loops of end, corner, pull, and gate posts for full length of each post.  Install fabric on opposite side of posts from area being secured.  Install fabric so that bottom of fabric is 2 inches above ground level.  Install fence fabric to provide approximately 2-inch deflection at center of fabric span between two posts, when a force of approximately 30 pounds is applied perpendicular to fabric.  Fabric should return to its original position when force is removed.

Where deer fencing is specified, the fence fabric shall be installed in a shallow trench with the fabric extending to two feet below grade.

3.3	ACCESSORIES INSTALLATION

3.3.1	Post Caps

Install post caps as recommended by the manufacturer.

3.3.2	Gates

Install swing gates to swing through 180 degrees from closed to open.  Install forked type or plunger bar type latch to permit operation from either side of gate.  Provide keeper for all vehicle gates, which will automatically engage the gate leaf and hold it in the open position until manually released.  Provide gate stops for all double gates, consisting of mushroom type of flush plate with angles.  Set in concrete to engage center drop rod or plunger bar.

3.3.3	Padlocks

Provide padlocks for gate openings and provide chains that are securely attached to gate or gate posts.  Provide padlocks keyed alike, and provide two keys for each padlock.

3.3.4	Supporting Arms

Design supporting arms to accommodate top rail.  Install supporting arms as recommended by manufacturer.  In addition to manufacturer’s standard connections, permanently secure supporting arms to posts.  Studs driven by low-velocity powder-actuated tools may be used with steel, wrought iron, ductile iron, or malleable iron.  Do not use studs driven by powder-actuated tools with gray iron or other material that will fracture.

3.4	CLEANUP

Remove waste fencing materials and other debris from the station.

END OF SECTION

SECTION 02935

TURF

PART 1	GENERAL

1.1	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by basic designation only.

FEDERAL SPECIFICATION (FED. SPEC.)

O-F-241D		Fertilizer, Mixed, Commercial

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM C 602		Agricultural Liming Materials

ASTM D 977		Emulsified Asphalt

ASTM E 11		Wire-Cloth Sieves for Testing Purposes

DEPARTMENT OF AGRICULTURE (DOA)

Statutory Authority:	Federal Seed Act 7 U.S.C. 1551-1611

1.2	EXTENT OF WORK

Provide seedbed preparation, topsoiling, liming, fertilizing, seeding, and mulching of all newly graded finish earth surfaces, unless indicated otherwise, and at all areas inside or outside the limits of construction that are disturbed by the Contractor’s operation.

1.3	SUBMITTALS

The following shall be submitted in accordance with Section 01300, “Submittal Procedures”.

1.3.1	SD-07 Schedules; GA

a.	Equipment List

A list of proposed seeding and mulching equipment to be used in performance of turfing operation, including descriptive data and calibration tests.

1.3.2	SD-08 Statements

a.	Maintenance Report; GA

Written record of maintenance work performed.

b.	Turf Establishment Period

Written calendar time period for the turf establishment period.  When there is more than one turf establishment period, the boundaries of the turfed area covered for each period shall be described.

c.	Delivery Schedule

Submit at least 10 days before delivery.

d.	Topsoil Supplier

Written statement giving the location of the properties from which the Topsoil is to be obtained, the names and addresses of the suppliers, and, if applicable, crops grown on the properties during the past 2 years.

1.3.3	SD-09 Reports

- Soil Laboratory Analytical Reports; GA

Submit copies of all analytical reports from the testing service.

1.3.4	SD-13 Certificates; GA

Certificates of compliance certifying that materials meet the requirements specified, prior to the delivery of materials.  Certified copies of the reports for the following materials shall be included:

a.	Seed

For mixture, percent pure live seed, minimum percent germination and hard seed, maximum percent weed seed content, date tested and state certification.

b.	Fertilizer

For chemical analysis, composition percent.

c.	Agricultural Limestone

For calcium carbonate equivalent and sieve analysis.

d.	Topsoil

For pH, particle size, chemical analysis and mechanical analysis.

1.4  	DELIVERY

1.4.1	Fertilizer and Lime

Deliver materials to the site in original, unopened containers bearing the manufacturer’s chemical analysis, name, trade name, trademark, and indication of conformance to state and federal laws.  In lieu of containers, furnish fertilizer and lime in bulk with a certificate indicating the above information accompanying each delivery.

1.4.2	Seed

Deliver seed to the site in original sealed packages bearing the producer’s guaranteed analysis for percentages of mixtures, purity, germination, weed seed content, and inert material.  Label in conformance with USDA Federal Seed Act and applicable state seed laws.  Wet, moldy, or otherwise damaged seed with be rejected.

1.5	STORAGE AND HANDLING

Store lime, fertilizer, and seed in dry locations and away from contaminants.  Protect seed from drying out.  Do not drop or dump materials from vehicles.

1.6	ENVIRONMENTAL PROTECTION

All work and Contractor operations shall comply with the requirements of Section 01560, “Environmental Protection.”

PART 2	PRODUCTS

2.1	SEED

State-certified seed of the latest season’s crop shall be provided in original sealed packages bearing the producer’s guaranteed analysis for percentages of mixture, purity, germination, hard seed, weed seed content, and inert material.  Mix seed on site in the presence of the RE or authorized representative.

Seed mixtures shall be proportioned by weight as follows:

Mixture Percent		Percent Pure

Common Name		    by Weight			   Live Seed

Red Fescues		     50				      95

Redtop			     20 				      92

Perennial Ryegrass		     30				      95

Weed seed shall not exceed 1 percent by weight of the total mixture.  Wet, moldy, or otherwise damaged seed shall be rejected.

2.2	SOIL AMENDMENTS

Soil amendments shall consist of lime, fertilizer, organic soil amendments and soil conditioners meeting the following requirements.

2.2.1	Lime

ASTM C 602, commercial agricultural limestone containing a minimum of 94 percent of total carbonates, 80 percent calcium, and 14 percent magnesium.  Provide the following ASTM E 11 gradation: minimum 100 percent passing the No. 20 sieve and 75 percent passing the No. 100 sieve.

2.2.2	Fertilizer

Fed. Spec. O-F-241, Type I, Class II, except provide Type II for hydroseeding.  Granular fertilizer shall contain a minimum percentage by weight of 10 percent nitrogen, 10 percent available phosphoric acid, and 10 percent potash.

2.3	TOPSOIL

Natural, friable soil representative of productive, well-drained soils in the area; free of subsoil, stumps, rocks larger than 1.0 inch in diameter, brush, weeds, toxic substances, and other material detrimental to plant growth.

Furnish topsoil from approved sources off the site meeting the requirements described in the following Table 2.3-,1 and the testing requirements of Article 3.5.

TABLE 2.3-1

USDA Soil Survey Investigation

Report No. 1, Laboratory Test for:	Acceptable Limits

Sand Content	20 - 75 percent by weight

Silt Content	10 - 60 percent by weight

Clay Content	5 - 30 percent by weight

Organic Material (Walkley-Block)	1.5 percent

pH	5.5 to 7.0

Soluble Salts	600 ppm maximum

2.4	MULCH

Mulch shall be free from weeds, mold, and other deleterious materials.

2.4.1	Straw

Straw shall be stalks from oats, wheat, rye, barley, or rice furnished in air-dry condition and with a consistency for placing with commercial mulch-blowing equipment.

2.4.2	Hay

Hay shall be native hay, sudan-grass hay, broomsedge hay, or other herbaceous mowings furnished in an air-dry condition suitable for placing with commercial mulch-blowing equipment.

2.4.3	Wood Cellulose Fiber

Wood cellulose fiber shall not contain any growth or germination-inhibiting factors and shall be dyed an appropriate color to facilitate visual metering during application.  Composition on air-dry weight basis:  9 to 15 percent moisture, pH range from 3.5 to 5.0.

2.6	WATER

Unless otherwise approved, contaminant-free potable water not containing

elements toxic to plant life.

2.7	EROSION CONTROL MATERIAL

Soil erosion control shall conform to the following:

2.7.1	Soil Erosion Control Blanket

Machine produced mat of wood excelsior formed from a web of interlocking wood fibers, covered on one side with either knitted straw blanket-like mat construction, covered with biodegradable plastic mesh, or interwoven biodegradable thread, plastic netting or twisted kraft paper cord netting.

2.7.2	Soil Erosion Control Fabric

Knitted construction of polypropylene yarn with uniform mesh openings 3/4 to 1 inch square with strips of biodegradable paper.  Filler paper strips shall last 6 to 8 months.

2.7.3	Soil Erosion Control Net

Heavy, twisted jute mesh weighing approximately 1.22 pounds per linear yard and 4 feet wide with mesh openings of approximately 1 inch square.

2.7.4	Soil Erosion Control Chemicals

High-polymer synthetic resin.

2.7.5	Hydrophilic Colloids

Hydrophilic colloids shall be physiologically harmless to plant and animal life, without phytotoxic agents.  Colloids shall be naturally occurring, silicate powder based, and shall form a water insoluble membrane after curing.  Colloids must resist mold growth.

2.7.6	Anchors

Erosion control anchor material shall be as recommended by the manufacturer.

PART 3	EXECUTION

3.1	SEEDING TIMES AND CONDITIONS

3.1.1	Seeding Time

Seed shall be sown from March 1st to May 15th for spring planting and from September 1st to October 30th for fall planting.

3.1.2	Turfing Conditions

Turf operations shall be performed only during periods when beneficial results can be obtained.  When drought, excessive moisture or other unsatisfactory conditions prevail, the work shall be stopped when directed.  When special conditions warrant a variance to the turf operations, proposed times shall be submitted to and approved by the Resident Engineer (RE).

3.2	SITE PREPARATION

3.2.1	Grading

The RE shall verify that finished grades are as indicated on drawings, and the placing of topsoil has been completed in accordance with Section 02225, “Excavation, Backfilling, and Compacting".

3.2.2	Subgrade

After areas to be seeded have been brought to the required subgrade, thoroughly till to minimum depth of 6 inches by scarifying, disking, harrowing, or other approved methods. After tillage, remove debris and stones larger than 1.0 inch remaining on the surface.

3.2.3	Final Grade

Immediately prior to placing topsoil, scarify subgrade to a 2-inch depth for bonding of topsoil with subsoil.  Spread topsoil evenly to a minimum depth of 4 inches.  Do not spread topsoil when frozen or excessively wet or dry.

3.2.3.1	If there is insufficient on-site topsoil meeting specified requirements for topsoil, then provide topsoil from offsite sources meeting the requirements of paragraph 2.3 of this section.

3.2.3.2	Correct irregularities in finished surfaces to eliminate depressions.  Protect finished topsoil areas from damage by vehicular or pedestrian traffic.

3.2.4   	Application of Soil Amendments

3.2.4.1   	Lime

Lime shall be applied at the rate of 3000 pounds per acre or 70 pounds per 1000 square feet.  Lime shall be  incorporated into the soil to a minimum depth of 4 inches or may be incorporated as part of the tillage operation.

3.2.4.2   	Fertilizer

Fertilizer shall be applied at the rate of 1000 pounds per acre or 23 pounds per 1000 square feet.  Fertilizer shall be incorporated into the soil to a minimum depth of 4 inches and may be incorporated as part of the tillage or hydroseeding operation.

3.3	SEEDING

3.3.1	General

Prior to seeding, any previously prepared seedbed areas compacted or damaged by interim rain, traffic or other cause, shall be reworked to restore the ground condition previously specified.  Seeding operations shall not take place when the wind velocity will prevent uniform seed distribution.

3.3.2	Equipment Calibration

The equipment to be used and the methods of turfing shall be subject to the inspection and approval of the RE prior to commencement of turfing operations.  Immediately prior to the commencement of turfing operations, the Contractor shall conduct turfing equipment calibration tests in the presence of the RE.

3.3.3	Applying Seed

Apply seed within 24 hours after seedbed preparation.  Sow seed with approved sowing equipment using one or a combination of the following methods at a rate of 240 pounds per acre.  Sow one-half the seed in one direction, and sow the remainder at right angles to the first sowing.

3.3.3.1	Broadcast Seeding

Seed shall be uniformly broadcast using broadcast or drop seeders.  Seed shall be covered uniformly to a maximum depth of 1/4 inch in clayey soils and ½ inch in sandy soils.  Cover seed by spike tooth harrow, raking, or other approved devices.

3.3.3.2	Drill Seeding

Use cultipacker seeders or grass seed drills or other approved methods.  Drill seed uniformly to maximum depth of 1/4 inch in clayey soils and ½ inch in sandy soils.  Cover seed by spike tooth harrow, cultipacker, or other approved devices.

3.3.3.3   	Rolling

Immediately after seeding, except for slopes 3-horizontal-to-1 vertical and greater, the entire area shall be firmed with a roller not exceeding 90 pounds for each foot of roller width.  Areas seeded with seed drills equipped with rollers shall not be rolled.

3.3.4   	Hydroseeding

Seed and fertilizer shall be added to water and thoroughly mixed at the rates specified.  Wood cellulose fiber mulch shall be added at the rates recommended by the manufacturer after the seed, fertilizer and water have been thoroughly mixed, to produce a homogeneous slurry.  Seed shall not remain in water containing fertilizer for more than 1 hour prior to application, unless otherwise approved.  Keep liquid fertilizer agitated during application.  Slurry shall be uniformly applied under pressure over the entire area.  Immediately following application of slurry mix, make separate application of wood cellulose mulch at the rate of 1000 pounds (dry weight) per acre. When hydraulically sprayed on the ground, material shall form a blotter-like cover impregnated uniformly with the grass seed.  Cover shall allow rainfall or applied water to percolate to underlying soil.  The hydroseeded area shall not be rolled.

3.3.5   	Mulch

3.3.5.1   	Straw or Hay Mulch

Straw or hay mulch shall be spread uniformly at the rate of 1.5 tons per acre.  Mulch shall be spread by hand, blower-type mulch spreader or other approved method.  Mulching shall be started on the windward side of relatively flat areas or on the upper part of a steep slope and continued uniformly until the area is covered.  The mulch shall not be bunched.  All seeded areas shall be mulched on the same day as the seeding.

3.3.5.2   	Mechanically Anchoring

Immediately following spreading, the mulch shall be anchored to the soil by a V-type-wheel land packer, a scalloped-disk land packer designed to force mulch into the soil surface, or other suitable equipment.

3.3.5.3	Non-Asphaltic Tackifier

Hydrophilic colloid shall be applied at rate recommended by manufacturer. Apply with hydraulic equipment suitable for mixing and applying uniform mixture of tackifier.

3.3.5.4	Spreading Asphalt Adhesive Coated Mulch

Spreading asphalt adhesive coated mulch will not be allowed.

3.3.5.5	Wood Cellulose Fiber

Wood cellulose fiber mulch for use with the hydraulic application of seed and fertilizer shall be applied as part of the hydroseeding operation.

3.3.6   	Water

Watering shall be started within 7 days after completing the seeded area.  Water shall be applied at a rate sufficient to ensure moist soil conditions to a minimum depth of 1 inch.  Run-off and puddling shall be prevented.

3.4	EROSION CONTROL

3.4.1	Erosion Control Material

Erosion control material, where indicated or required, shall be installed in accordance with manufacturer’s instructions.  Placement of the erosion control material shall be accomplished without damage to installed material or without deviation to finished grade.

  - TOPSOIL TESTING

Topsoil shall be tested in accordance with the following laboratory analytical methods: Gradation - ASTM D 422, Priority Pollutant Semivolatile Organic Compounds (SVOCs) - EPA Method 8270, Priority Pollutant Volatile Organic Compounds (VOCs) -  EPA Method 8260, Priority Pollutant Metals - EPA Method 6010 (HG Method), Pesticides -  EPA Method 8081, PCBs -  EPA Method 8082, Herbicides -  EPA Method 8151, and Soil pH - EPA Method 9045D.

The services of a qualified testing laboratory shall be engaged by the Contractor to make tests and determine acceptability of the material as listed below.  The laboratory shall be New Jersey certified for the applicable tests.

Tests for Topsoil material from off-site shall be performed at a frequency of 1 per 3,000 cubic yards if from a natural borrow source or 1 per source, whichever is more stringent. Material that is not from a natural borrow source shall be tested at a frequency of 1 per 1,000 cubic yards or 1 per source, whichever is more stringent.  The RE shall make the final determination if a source is natural or not.

Topsoil shall be acceptable if environmental test results show that all contaminant levels are below the lowest (most restrictive) soil cleanup criteria established by the NJDEP.

3.6	RESTORATION AND CLEAN UP

3.6.1	Restoration

Existing turf areas, pavements and facilities that have been damaged from the turfing operation shall be restored to original condition at Contractor’s expense.

3.6.2	Clean Up

Excess (other than surplus topsoil, if applicable) and waste material shall be removed from the planting operation and shall be disposed of off the site in accordance with applicable regulations.  Adjacent paved areas shall be cleaned.

3.7	PROTECTION OF TURFED AREAS

Immediately after turfing, the area shall be protected against traffic or other use by erecting barricades and providing signage as required, or as directed by the RE.

3.8	TURF ESTABLISHMENT PERIOD

3.8.1	Commencement

The Turf Establishment Period for establishing a healthy stand of turf shall begin on the first day of work under this section and shall end three (3) months after the last day of turfing operations required by this contract. Written calendar time period shall be furnished to the RE for the Turf Establishment Period.  When there is more than one turf establishment period, describe the boundaries of the turfed area covered for each period.

3.8.2	Satisfactory Stand of Turf

3.8.2.1	Seeded Area

A satisfactory stand of turf from the seeding operation for a field area is defined as a minimum of 10 grass plants per square foot.  The total bare spots shall not exceed 2 percent of the total seeded area.

3.8.3   	Maintenance During Establishment Period

3.8.3.1	General

Maintenance of the turfed areas shall include eradicating weeds, eradicating insects and diseases, protecting embankments and ditches from erosion, maintaining erosion control materials and mulch, protecting turfed areas from traffic, mowing, and watering.

3.8.3.2   	Mowing

Lawn areas shall be mowed to a minimum height of 2 inches when the average height of the turf becomes 4 inches.  Clippings shall be removed when the amount of cut turf is heavy enough to damage the turfed areas.

3.8.3.3	Watering

Watering shall be at intervals to obtain a moist soil condition to a minimum depth of 1 inch.  Frequency of watering and quantity of water shall be adjusted in accordance with the growth of the turf.  Run-off, puddling and wilting shall be prevented.

3.8.3.4	Repair

The Contractor shall re-establish as specified herein, eroded, damaged or barren areas.  Mulch shall also be repaired or replaced as required.

3.8.3.5	Maintenance Report

A written record shall be furnished to the RE of the maintenance work performed.

3.9	FINAL ACCEPTANCE

3.9.1	Preliminary Inspection

Prior to the completion of the Turf Establishment Period, a preliminary inspection shall be held by the RE.  Time for the inspection shall be established in writing.  The acceptability of the turf in accordance with the Turf Establishment Period shall be determined.  An unacceptable stand of turf shall be repaired as soon as turfing conditions permit.

3.9.2	Final Inspection

A final inspection shall be held by the RE to determine that deficiencies noted in the preliminary inspection have been corrected.  Time for the inspection shall be established in writing.

END OF SECTION

SECTION 03410

PRECAST STRUCTURAL CONCRETE

PART 1	GENERAL

1.1	SUMMARY

1.2	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

AMERICAN IRON AND STEEL INSTITUTE (AISI) PUBLICATION

Stainless and Heat Resisting Steels - 1974

AMERICAN CONCRETE INSTITUTE (ACI) PUBLICATIONS

ACI 211.1-74(75)	Selecting Proportions for Normal and Heavy- Weight Concrete

ACI 2ll.2-69(77)	Selecting Proportions for Structural Light- Weight Concrete

ACI 2l4-65	Evaluation of Compression Test Results of Field Concrete

ACI 304-73       	Measuring, Mixing, Transporting, and Placing Concrete

ACI 305-72       	Hot Weather Concreting

ACI 306-66(72)   	Cold Weather Concreting

ACI 308-71       	Curing Concrete

ACI 315-92       	Detailing Reinforced Concrete Structures

ACI 318-95       	Building Code Requirements for Reinforced Concrete

ACI 517-70(76)   	Atmospheric Pressure Steam Curing of Concrete

AMERICAN SOCIETY FOR TESTING MATERIALS (ASTM) PUBLICATIONS

A82-76      	Cold-Drawn Steel Wire for Concrete Reinforcement

A123-73	Zinc (Hot Galvanized) Coatings on Products Fabricated from Rolled, Pressed, and Forged Steel Shapes, Plates, Bars, and Strip

A185-73 	Welded Steel Wire Fabric for Concrete Reinforcement

A615-76a        	Deformed and Plain Billet-Steel Bars for Concrete Reinforcement

A616-76         	Rail-Steel Deformed and Plain Bars for Concrete Reinforcement

A6l7-76         	Axle-Steel Deformed and Plain Bars for Concrete Reinforcement

C33-77           	Concrete Aggregates

C42-68(74)      	Obtaining and Testing Drilled Cores and Sawed Beams of Concrete

C143-74          	Slump of Portland Cement Concrete

C150-77          	Portland Cement

C173-75         	Air Content of Freshly Mixed Concrete by the Volumetric Method

C231-75         	Air Content of Freshly Mixed Concrete by the Pressure Method

C260-74          	Air Entraining Admixtures for Concrete

C330-77          	Lightweight Aggregates for Structural Concrete

C494-77          	Chemical Admixtures for Concrete

C567-71          	Unit Weight of Structural Lightweight Concrete

C595-76          	Blended Hydraulic Cements

C618-77         	Fly Ash and Raw or Calcined Natural Pozzolan for Use as a Mineral Admixture in Portland Cement Concrete

AMERICAN WELDING SOCIETY (AWS) PUBLICATIONS

AWS D1.1-96      	Structural Welding Code

AWS D12.1-75     	Welding Reinforcing Steel

PRESTRESSED CONCRETE INSTITUTE (PCI) PUBLICATION:

MNL-116-77      	Manual for Quality Control for Plants and Production of Precast Prestressed Concrete Products

UNDERWRITERS LABORATORIES, INC. (UL)

Fire Resistance Index

U.S. ARMY CORPS OF ENGINEERS REGULATIONS

Engineer Regulation (ER) 1110-1-2002

1.2.1	General Requirements

All work shall be as specified herein.  Where conflicts between referenced publications exist, ACI 3l8 shall govern. Precast units shall be the product of a manufacturer specializing in the production of precast concrete units.

1.3	SUBMITTALS

1.3.1  	SD-04  SHOP DRAWINGS; GA

Shop drawings indicating details of construction and erection shall be submitted to the Resident Engineer (RE) for record in accordance with the requirements of Division l.  Drawings shall show dimensions, details of bonding, inserts, cutouts, sleeves, pickup points, and accessories, and the relationship of all pieces to adjacent materials. Reinforcing steel shall be detailed in accordance with ACI 315.  Any revision to the design as shown on the engineering drawings, in order to adapt them to the manufacturer's method of operation, including handling, shall be shown on the shop drawings, and appropriate design calculations shall be submitted to the RE for approval.

1.3.2  	SD-10 CERTIFIED TEST REPORTS; GA

Before delivery of materials and equipment, four certified copies of the tests reports specified herein shall be submitted to the RE for approval, along with manufacturer’s certification that the tested material and equipment are of the same type, quality, and manufacture as that proposed to be supplied.

1.3.3  	SD-09, Contractor Furnished Mix Design

The Contractor shall prepare, and submit for approval, a concrete mix design for each type of concrete required.  The strength of concrete at 28 days shall be at least 4,000 PSI. The design shall be prepared in accordance with ACI 3l8.  The concrete may be proportioned from additional data derived from ACI 211.1, ACI 211.2 and ACI 214 for an assumed coefficient of variation of 15 percent and a probability of one test in ten falling below the specified strength, f'c, provided that the mix design reflects actual concrete plant standard deviations and the resulting production concrete conforms to the specified requirements.  The mix-design shall be based on current materials previously evaluated by the concrete producer whose established methods of statistical quality control is in conformance with ACI 318.  In the absence of such data, the Contractor shall sample and test the aggregates for the design of concrete.

PART 2	PRODUCTS

Materials shall conform to the specifications and to the other requirements specified herein.

2.1  	PORTLAND CEMENT

ASTM C150.  Cement used shall be obtained from a single mill.  Type III cement may be used, when approved, at no increase in cost to the Government.

2.2 	WATER

Water shall be clean and free from injurious amounts of oils, acids, alkalis, salts, organic materials, or other substances that may be harmful to concrete or steel.  Water shall not contain harmful amounts of chloride ion.

2.3  	AGGREGATES

Aggregates shall be free from any materials which could react with the alkalies in the cement in a deleterious manner.

2.3.1  	Aggregates for Normal Weight Concrete

ASTM C33.

2.3.2	Aggregates for Lightweight Concrete

Coarse aggregates, ASTM C330; fine aggregates, ASTM C33 or C330.

2.3.3  	Aggregate Maximum Size

The maximum size of aggregate shall not exceed one inch.

2.3.4 	All Aggregates

All aggregates of each size, used for exposed concrete, shall be obtained from a single source.

2.4	ADMIXTURES, INCLUDING AIR ENTRAINING (IF USED)

ASTM C260 (air entraining); ASTM C494 (chemical).  All admixtures shall have prior approval of the Resident Engineer (RE), shall be from one manufacturer, and shall be certified by the manufacturer to be free of chlorides.  All admixtures shall be added at the mixer.

2.5	REINFORCING

2.5.1	Welded Wire Fabric Reinforcing

ASTM A185, sized as indicated.

2.5.2	Reinforcing Bars

ASTM A615, A616, and A617, Grade 60.  Welded splices shall be in accordance with AWS D12.1.

2.6  	ATTACHMENT ACCESSORIES

Bolts, shims, washers and nuts, dowels, and clamps shall be corrosion resisting steel conforming to AISI Type 304 or 316. Anchors, setting loops, lifting hooks, and like accessories set in castings shall be steel, hot-dipped zinc-coated in accordance with ASTM Al23, malleable iron, or plated ferrous metal as best suited to prevent rust staining of members and to meet structural requirements.

2.7  	ELASTOMERIC BEARING PADS (IF APPLICABLE)

Elastomeric bearing pads shall conform to the following:

2.7.1	Pads l/2-inch and less in thickness shall be all elastomer.  The total out-to-out thickness of a pad shall not be less than the thickness indicated nor more than l/4-inch greater than the thickness.  Variation of total thickness within an individual pad shall not exceed l/8inch.

2.7.2 	The length and width of a pad shall not vary more than l/8-inch from the dimensions indicated.  Pads of all elastomer may be cut from large sheets.  Cutting shall be performed in such a manner as to avoid heating of the material, to produce a smooth edge with no tears or other jagged areas, and to cause as little damage to the material as possible.  Corners and edges of molded pads may be rounded at the option of the Contractor.  Radius at corners shall not exceed 3/8-inch and radius of edges shall not exceed 1/8-inch.

2.7.3	The sole polymer in the elastomeric compound shall be neoprene and shall not be less than 60 percent by volume of the total compound.

2.8	CAULKING AND SEALANTS

See Sections 07920 “Sealants” and 02420, “Manhole Structures”.

2.9  	MISCELLANEOUS CONNECTIONS

Anchors, dowels, bolts, steel welding inserts, and connecting plates indicated and/or necessary in connection with the fabrication and erection of precast concrete members shall be in position rigidly to prevent displacement while concrete is being placed.  On-site and off-site welding shall be in accordance with AWS Dl.l and Dl2.l, as applicable.

PART 3	EXECUTION

3.1	FABRICATION

Fabrication of the members shall be for the design load conditions indicated and shall make structural provision for all required openings.  Each precast member shall be marked to indicate its location in the structure, its top surface, and date of fabrication.  Identification marks shall correspond to the placing plans.

3.1.1 	Forms

Forms shall be well braced and stiffened against deformation, and shall be accurately constructed.  The forms shall be such as to produce a smooth dense surface.  A bond-breaking substance may be applied to the forms. Exposed edges shall be chamfered to a 3/4-inch radius. Form ties shall be either the threaded or snap-off type, so that no form wires or metal pieces will be left at the surface of the finished concrete.

3.1.2	Tolerances

The dimensions of the finished product shall be as noted on the drawings.

3.1.3	Cast-in Items

Groups of inserts or cast-in items which must be located in close tolerance to each other shall not be separated into two panels by a joint.

3.1.4  	REINFORCING

Steel reinforcing shall be fabricated as indicated and placed in position in the forms within the tolerances specified in ACI 318. Reinforcement shall be adequately secured so as to remain in the proper position during placement of the concrete.  Where cover over reinforcing steel is not indicated, it shall be in accordance with ACI 318.

3.1.5 	CONCRETE

3.1.5.1	Concrete Mixing

Mixing operations shall be such as to produce batch-to-batch uniformity.

3.1.5.2 	Concrete Placing

Concrete placing shall be in accordance with ACI 304 and ACI 305 and 306.

3.1.5.3	Concrete Curing

Curing shall be commenced immediately following the initial set or completion of surface finishing and shall conform to ACI 308. The application of heat at a controlled rate, combined with an effective method of supplying or retaining moisture in order to accelerate the curing process, shall be accomplished as described below.

3.1.5.3.1	Steam Curing

Steam curing shall conform to ACI 517.

3.1.5.3.2	Curing with Radiant Heat and Moisture

The application of radiant heat to beds, whether by means of pipes circulating steam, hot oil or hot water, or by electric blankets or heating elements, shall be accomplished without pipes, blankets, or elements making contact with concrete, form surfaces, or test cylinders.  Effective means shall be provided to prevent rapid loss of moisture in any part of the member.  The ambient curing temperature shall not exceed l75 degrees F at any time.  The curing procedures shall be carefully controlled.

3.1.6	Finishing

Honeycombed sections shall be inspected by a qualified structural engineer.  If any unit is found to be structurally impaired, it shall be rejected.  Where accepted, honeycombed sections shall be repaired unless the repair is specifically waived by the Resident Engineer (RE).  The repair shall be as follows:

All loose material shall be removed and the areas cut back until the coarse aggregate breaks under chipping instead of falling out.  The area shall be saturated, allowed to approach a condition of surface dryness, coated with a thin layer of neat cement slurry, and hammer-packed with stiff dry mortar.  A proven bonding material shall be used, as per manufacturer's recommendations, for bonding the patching mortar.

3.1.6.1	Structural members will be accepted with form finished appearance but with leakage fins removed.  All faces shall have true, well-defined surfaces. Exposed ragged edges shall be corrected by rubbing or grinding.

3.1.6.2 	Standard Finish

Small surface holes caused by air bubbles, normal form joint marks, and minor chips and spalls will be tolerated, but no major or unsightly imperfections, honeycomb, or structural defects will be accepted.  However, the RE may accept such defects subject to approved corrective measures.

3.1.6.3 	Grade B Finish

All air pockets and holes over 1/4-inch in diameter shall be filled with a sand-cement paste.  All form offsets or fins over 1/8-inch shall be ground smooth.

3.2  	ERECTION

Members shall be erected in accordance with approved shop drawings and erection schedules.  The proposed sequence of operations shall be approved before erection begins.  The work shall be supported, braced, guyed, and otherwise maintained in proper position pending completion of necessary structural connections.  All temporary supports shall be maintained until the steel has been welded and the grout or fill at the base of rigid frames and interior columns has attained a strength equal to 70 percent of the design strength.  Welding shall conform to AWS D1.1.

3.2.1	Bearing Surfaces

Units shall be installed on bearing surfaces which are level and free of irregularities.  The Contractor shall correct bearing surface irregularities by leveling with a stiff cement mortar.  The units shall be installed at right angles to bearing surfaces, drawn up tight without forcing or distortion, and with sides plumb.

3.2.3	Grouting

Except where indicated otherwise, keyways between units and other spaces shall be cleaned and filled solidly with grout.  Grout seeping through to surfaces in spaces below shall be removed before hardening.

Grout shall consist of a mixture of cementatious materials and aggregate as specified hereinafter; water shall be added in sufficient quantity to produce a stiff fluid mixture.  Fine grout shall be provided in grout spaces less than 2 inches in any horizontal dimension or in which clearance between reinforcing and masonry is less than 3/4-inch.  Coarse grout shall be provided in grout spaces 2 inches or greater in any horizontal dimensions or in which clearance between members is not less than 3/4inch.

Fine grout shall be mixed in proportions of one part Portland cement, 1/4 part lime paste, and 3 parts sand.

Coarse grout shall be mixed in proportions of one part Portland cement, 1/4 part lime paste, 3 parts sand, and 3 parts coarse aggregate passing a 3/8-inch sieve.

3.2.4	Caulking and Sealants

Seals, gaskets, sealant, and sealant backup shall be placed in vertical and horizontal joints between units in accordance with drawing details and as specified in Sections 07920, “Sealants”, and 02420, “Manhole Structures”.

3.3 	SAMPLING AND TESTING

Samples and tests required below shall be made at the Contractor’s expense.  The tests shall be performed by an independent commercial testing laboratory, or, if approved by the RE, at the precaster’s quality control laboratory. Certified test reports shall include all test data and results.

3.3.1	Concrete Testing

Plastic concrete, as delivered to the casting site, shall be sampled and tested as indicated below and in the paragraph entitled “Evaluation and Acceptance of Concrete” of ACI 318.  A minimum of four cylinders shall be made during each concreting cycle of the same mix. Statistical evaluation of compressive test results shall be in accordance with ACI 214.

3.3.2 	Slump

In accordance with ASTM C143.

3.3.3  	Air Content

Tests shall be made at the same time that specimens for compression tests are made.  Tests shall be made in accordance with ASTM C173 or ASTM C231.

3.3.4  	Lightweight Concrete

Unit weight of lightweight concrete shall be tested in accordance with ASTM C567.

3.3.5  	Slump and Air Content Test Results

If the measured slump or air content falls outside the limits specified, a check test shall be made.  In the event of a second failure, the load of concrete represented shall be rejected.

3.3.6  	Compressive Strength Test Results

If the compressive strength tests fail to meet the above requirements, core testing shall be made in accordance with ASTM C42.  If the core tests prove unsatisfactory, load tests shall be made in accordance with ACI 3l8. Precast units failing to meet the requirements of the load tests shall not be used.  Core tests and load tests shall be performed at the expense of the Contractor.

3.3.7   	Mill Certificates

The Contractor shall furnish mill certificates attesting to the quality of the cement.  Cement shall be provided by a qualified source in accordance with the Corps of Engineers Cement Quality Management System.

Plant and specialist qualifications shall be in accordance with the following options:

3.3.7.1  	Contractor’s Option

Precast structural concrete shall be the product of a manufacturer having capacity and facilities for producing materials of the quality and finish specified herein, and of the quantity indicated without delay to progress of work.  The manufacturer shall have an established quality assurance program in effective operation at his plant, attested to by a current certification of the plant in the PCI “Certification Program for Quality Control”.

3.3.7.2  	Contractor’s Option

Performance tests shall be executed on members selected at random by the RE for plants or specialists not currently enrolled in the PCI “Certification Program for Quality Control” or for precast concrete jobs cast by specialists.

END OF SECTION

SECTION 07920

SEALANTS

PART 1	GENERAL

1.1	SUMMARY

1.2	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM C834		Latex Sealing Compounds

ASTM C920		Elastomeric Joint Sealants

1.3	SUBMITTALS

Submit to the Resident Engineer (RE) the following:

1.3.1	SD-02  Manufacturer's Catalog Data; GA

a.	Sealants

b.	Primers

c.	Backstop materials

d.	Bond Breakers

e.	Concrete Waterproofing

Data for the sealants shall include shelf life and recommended cleaning solvents.

1.3.2	SD-03  Manufacturer’s Standard Color Charts; GA

a.	Sealants

Where colors are not indicated, submit not less than 3 different colors for selection by the RE.

1.3.3	SD-06  Manufacturer’s Instructions; GA

a.	Sealants

b.	Concrete Waterproofing

Submit application instructions, precautions and mixing instructions for multicomponent sealants and concrete waterproofing.

1.3.4	SD-14  Samples; GA

a.	Sealants

Submit one sample of each color for each sealant type to verify that products match the colors indicated.

1.3.5	SD-10  Test Reports; GA

a.	Sealants

Indicate sealant compatibility with commonly used substrates.

1.3.6	SD-13  Certificates of Compliance; GA

a.	Sealants

b.	Primers

c.	Backstops

d.	Bond Breakers

e.	Concrete Waterproofing

Submit certificates from the manufacturers attesting that materials meet the specified requirements.

1.4	ENVIRONMENTAL CONDITIONS

The ambient temperature shall be within the limits of 40 and 100 degrees F when sealant is applied.

1.5	DELIVERY AND STORAGE

Deliver materials to the job site is unopened in manufacturers’ external shipping containers, with brand names, date of manufacture, color, and material designation clearly marked thereon.  Elastomeric sealant containers shall be labeled to identify type, class, grade, and use.  Carefully handle and store materials to prevent inclusion of foreign materials or subjection to sustained temperatures exceeding 100 F degrees or less than 40 degrees F.

PART 2	PRODUCTS

2.1	SEALANTS

Provide sealant that has been tested and found suitable for the substrates to which it will be applied.

2.1.1	Interior Sealant

Not used.

2.1.2	Exterior Sealant

Except where specified otherwise:  For Joints in vertical surfaces, provide ASTM C920, Type S or M, Grade NS, Class 25, Use NT.  For joints in horizontal surfaces, provide ASTM C920, Type S or M, Grade P, Class 25, Use T.  Location(s) of sealant shall be as follows:

Location:

a.	Voids where items pass through exterior walls.

b.	Metal-to-Metal joints where sealant is indicated or specified.

c.	Interior face of expansion joints in exterior walls where metal expansion joint covers are not required.

2.1.3	Floor Joint Sealant

Not used.

2.2	PRIMER FOR SEALANT

Provide a nonstaining, quick-drying type and consistency recommended by the sealant manufacturer for the particular application.

2.3	BOND BREAKERS

Provide the type and consistency recommended by the sealant manufacturer for the particular application.

2.4	BACKSTOPS

Provide glass fiber roving or neoprene, butyl, polyurethane, or polyethylene foams free from oil or other staining elements as recommended by sealant manufacturer.  Backstop material shall be compatible with sealant.  Do not use oakum and other types of absorptive materials as backstops.

2.5	CLEANING SOLVENTS

Provide type(s) recommended by the sealant manufacturer.

2.6	CONCRETE WATERPROOFING

Provide a bitumastic waterproof coating on all exterior concrete surfaces, including manholes.

PART 3	EXECUTION

3.1	SURFACE PREPARATION

Surfaces shall be clean, dry to the touch, and free from dirt frost, moisture, grease, oil, wax, lacquer, paint, or other foreign matter that would tend to destroy or impair adhesion. When resealing an existing joint, remove existing caulk or sealant prior to applying new sealant.

3.1.1	Steel Surfaces

Remove loose mill scale by sandblasting or, if sandblasting is impractical or would damage finish work, scraping and wire brushing.  Remove protective coatings by sandblasting or using a residue-free solvent.

3.1.2	Aluminum or Bronze Surfaces

Remove temporary protective coatings from surfaces that will be in contact with sealant.  When masking tape is used as a protective coating, remove tape and any residual adhesive just prior to sealant application.  For removing protective coatings and final cleaning, use nonstaining solvents recommended by the manufacturer of the item(s) containing aluminum or bronze surfaces.

3.1.3	Concrete Surfaces

3.2	SEALANT PREPARATION

Do not add liquids, solvents, or powders to the sealant.  Mix multicomponent elastomeric sealants in accordance with manufacturer's instructions.

3.3	APPLICATION

3.3.1	Joint Width-to-Depth Ratios

a.	Acceptable Ratios:

Joint Width	  	              Joint Depth

Minimum  		  Maximum

For metal, glass, or other

nonporous surfaces:

1/4 inch (minimum)	1/4 inch		1/4 inch

over 1/4 inch of width	1/2 inch		Equal to width

For wood, concrete, masonry

or stone:

1/4 inch (minimum)	1/4 inch		1/4 inch

Over 1/4 inch to 	1/4 inch		Equal to

1/2 inch width

Over 1/2 inch to 2 inches	1/2 inch		5/8 inch

Over 2 inches	(As recommended by sealant manufacturer)

b.	Unacceptable Ratios: Where joints of acceptable width-to-depth ratios have not been provided, clean out joints to acceptable depths and grind or cut to acceptable widths without damage to the adjoining work.  Grinding shall not be required on metal surfaces.

3.3.2	Backstops

Install backstops dry and free of tears or holes.  Tightly pack the back or bottom of joint cavities with backstop material to provide a joint of the depth specified.  Install backstops in the following locations.

a.	Where indicated.

b.	Where backstop is not indicated but joint cavities exceed the acceptable maximum depths specified in paragraph entitled, “Joint Width-to-Depth Ratios”.

3.3.3	Primer

Immediately prior to application of the sealant, clean out loose particles from joints.  Where recommended by sealant manufacturer, apply primer to joints in porous surfaces in accordance with sealant manufacturer's instructions.  Do not apply primer to exposed finish surfaces.

3.3.4	Bond Breaker

Provide bond breakers to the back or bottom of joint cavities, as recommended by the sealant manufacturer for each type of joint and sealant used, to prevent sealant from adhering to these surfaces.  Carefully apply the bond breaker to avoid contamination of adjoining surfaces or breaking bond with surfaces other than those covered by the bond breaker.

3.3.5	Sealants

Provide a sealant compatible with the material (s) to which it is applied.  Do not use a sealant that has exceeded shelf life or has jelled and can not be discharged in a continuous flow from the gun.  Apply the sealant in accordance with the manufacturer's instructions with a gun having a nozzle that fits the joint width.  Force sealant into joints to fill the joints solidly without air pockets.  Tool sealant after application to ensure adhesion.  Sealant shall be uniformly smooth and free of wrinkles.  Upon completion of sealant application, roughen partially filled or unfilled joints, apply sealant, and tool smooth as specified.

3.3.6	Concrete Waterproofing

Apply bitumastic concrete waterproofing to all exterior surfaces in accordance with manufacturer's recommendations.

3.4	PROTECTION AND CLEANING

3.4.1	Protection

Protect areas adjacent to joints from sealant smears.  Masking tape may be used for this purpose if removed 5 to 10 minutes after the joint is filled.

3.4.2	Final Cleaning

Upon completion of sealant application, remove remaining smears and stains and leave the work in a clean and neat condition.

a.	Porous Surfaces:  Immediately scrape off  fresh sealant that has been smeared and rub clean with a solvent as recommended by the sealant manufacturer.  Allow excess sealant to cure for 24 hour then remove by wire brushing or sanding.

b.	Metal and Other Non-Porous Surfaces:  Remove excess sealant with a solvent-moistened cloth.

END OF SECTION

SECTION 13999

OPERATION AND MAINTENANCE REQUIREMENTS

PART 1	GENERAL

1.1	SUMMARY

This section describes the overall operation and maintenance requirements for the expansion of the discharge system during construction and before the Recharge Bed system shakedown, testing, and initial operation and maintenance. Some notable requirements to this section are: Operation & Maintenance Data, Maintenance Schedule, Pollution Liability Insurance, Sampling & Analysis Plan, Checkout Plan, and Operation & Maintenance Manual.  Present information in sufficient detail to clearly explain user Operation & Maintenance (O&M) requirements at the system equipment, component, and subassembly level.  Submit in accordance with Section 01330, “Submittal Procedures”.  The O&M requirements for the Recharge Bed will be incorporated into the current O&M Manual for the ground water treatment system of Areas B, D, 41, and E at the FAA facility.

1.2	REFERENCES

The publication listed below forms a part of this specification to the extent referenced.  The publication is referred to in the text by the basic designation only.

DEFENSE LOGISTICS AGENCY (DLA)

DLA H4/H8		Federal Cataloging Handbook Commercial and Government Entity (CAGE), Sections A and B, United States and Canada, Sections C and D, NATO, Supply Code for Manufacturers

ENVIRONMENTAL PROTECTION AGENCY (EPA)

EPA SW-846		(Rev 0; Updated I, II, IIA, IIB and III) Test Methods for Evaluating Solid Waste (Vol IA, IB, IC and II)

NEW JERSEY DEPARTMENT OF ENVIRONMENTAL PROTECTION (NJDEP)

NJDEP	Field Sampling Procedures Manual

NJDEP		NJAC 7:26E Technical Requirements for Site Remediation

1.3	DEFINITIONS

NJPDES-DGW Permit

New Jersey Pollution Discharge Elimination System Discharge to Ground Water Permit.  The existing NJPDES-DGW Permit for this site requires analysis of ground water and treatment system effluent for VOCs, SVOCs and Priority Pollutant Metals.

1.4	SUBMITTALS

1.4.1	SD-08, Statements, GA

a.	Pollution Liability Insurance

1.4.1.1	Submission of Pollution Liability Insurance

Three (3) copies of proof of pollution liability insurance in the amount of $2,000,000.00 and show coverage by the insurance carrier that the FAA is additional named insured.  The submittal shall occur thirty (30) days prior to the start-up or annual renewal date.

1.4.2	SD-09, Reports, GA

a. Operation and Maintenance Data

b. Maintenance Schedule

c. Ground Water Sampling and Analysis Plan

d. Checkout Plan

1.4.2.1	Submission of Operation & Maintenance Data

Submit operation and maintenance (O&M) data which is specifically applicable to this contract and a complete and concise depiction of the provided equipment or product.  Data shall include items such as: manufacturer’s manuals, equipment specifications, and drawings.  Data containing extraneous information to be sorted through to find applicable instructions will not be accepted.  See paragraph 1.5.  The data will be incorporated into the current O&M data for the ground water treatment system.

1.4.2.2	Submission of Maintenance Schedule

Submit a maintenance schedule which specifically and clearly identifies procedures, recommended requirements and techniques for preventative and scheduled maintenance to minimize corrective maintenance and repair.  See paragraph 1.6.

Once the recharge system is in operation, submittal of completed reports, “Monthly Scheduled Maintenance Checklist” to the FAA will be required.  Three (3) copies of these monthly scheduled maintenance checklists with items checked that were performed, are required.  Where parts or components are worn, damaged and replaced, they shall be noted on the checklist.  Copies of all receipts for parts, supplies and labor shall be furnished with the checklist.  Notes on continually used supplies such as oils and lubricants shall be kept with the list.  The checklist for the Recharge Bed shall be coordinated with the existing requirements for the ground water treatment system.  The checklist shall be signed by the system operator and the system manager.

1.4.2.3	Submission of Ground Water Sampling & Analysis Plan

Within 30 days after the effective date of this contract, the Contractor shall submit to the FAA a Ground Water Sampling and Analysis Plan which specifically and clearly identifies procedures and techniques for ground water sampling at the SITE.  The plan shall be consistent with existing NJPDES-DGW Permit requirements for the ground water treatment system.  The sampling plan shall be site specific and address the following items:

a.	sample locations and sample collection;

b.	ground water elevation data collection;

c.	equipment decontamination procedures;

d.	sample preservation and shipment;

e.	sample chain of custody;

f.	sample analytical methods; and

g.	analytical deliverable packages.

The sampling plan shall address the expanded discharge system at the Recharge Bed and shall be incorporated into the current Sampling and Analysis Plan for the ground water treatment system.  The sampling plan shall be developed in accordance with the methods and procedures as specified in the latest edition of the NJDEP’s Field Sampling Procedures Manual.

1.4.2.4	Submission of Checkout Plan

Thirty (30) days prior to system checkout, the Contractor shall prepare a Checkout Plan that describes how all equipment and controls will be tested.  Describe criteria that will be utilized to determine acceptability of test results for equipment or controls.  Include all applicable manufacturer’s requirements.  Describe methodology that will be used to calibrate all instrumentation.  Describe methodology that will be used to ensure that all components function within the full required operating range and that all energized components function within acceptable manufacturer’s operating parameters.

1.4.3	SD-19, Operation & Maintenance Manuals GA

Operation and Maintenance Manuals described within paragraph entitled “Operation and Maintenance Manuals” in Part 3 of this section.  The Manuals will be incorporated into the existing documents for the ground water treatment system.

1.5	OPERATION AND MAINTENANCE DATA REQUIREMENTS

1.5.1	General

1.5.1.1	Quantity

Submit five copies of the manufacturers’ information specified herein for the components, assemblies, subassemblies, attachments, and accessories.  The items for which O&M data is required are listed in the technical sections which specify that particular item.

1.5.1.2	Package Content

For each product, system, or piece of equipment requiring submission of O&M data, submit the package required in the individual technical section for the specific item referenced.  Package content shall be as required in the paragraph entitled, "Schedule of Operations and Maintenance Data Packages.”

1.5.1.3	Delivery

Submit O&M data to the Resident Engineer (RE) for review and acceptance; submit data specified for a given item 30 calendar days prior to delivery of the item to the contract site.

1.5.1.4	Changes to Submittals

Manufacturer-originated changes or revisions to submitted data shall be furnished by the Contractor if a component of an item is so affected subsequent to acceptance of the O&M data.  Changes, additions, or revisions required by the RE for final acceptance of submitted data, shall be submitted by the Contractor within 30 calendar days of the notification of this change requirement.

1.5.2	Operating Instructions

Include specific instructions, procedures, and illustrations for the following phases of operation:

a. Safety Precautions

b. Operator Prestart

c. Startup, Shutdown, and Post-shutdown Procedures

d. Normal Operations

e. Emergency Operations

f. Operator Service Requirements

g. Environmental Conditions

1.5.2.1	Safety Precautions

List personnel hazards and equipment or product safety precautions for all operating conditions.

1.5.2.2	Operator Prestart

Include requirements to set up and prepare each system for use.

1.5.2.3	Startup, Shutdown, and Post-shutdown Procedures

Include a control sequence for each of these operations.

1.5.2.4	Normal Operations

Include control diagrams with data to explain operation and control of systems and specific equipment.

1.5.2.5	Emergency Operations

Include emergency procedures for equipment malfunctions to permit a short period of continued operation or to shut down the equipment to prevent further damage to systems and equipment.  Include emergency shutdown instructions for fire, explosion, spills, or other foreseeable contingencies.  Provide guidance on emergency operations of all utility systems including valve locations and portions of systems controlled.

1.5.2.6	Operator Service Requirements

Include instructions for services to be performed by the operator such as lubrication, adjustments, and inspection.

1.5.2.7	Environmental Conditions

Include a list of environmental conditions (temperature, humidity, and other relevant data) which are best suited for each product or piece of equipment and describe conditions under which equipment should not be allowed to run.

1.5.3	Schedule of Operation and Maintenance Data Packages

Furnish the O&M data packages specified in individual technical sections.  The required information for each O&M data package is as follows:

1.5.3.1	Data Package 1

Data package #1 would be used for a simple item requiring only simple maintenance and replacement.

a.	Safety precautions

b.	Maintenance and repair procedures

c.	Warranty information

d.	Contractor information

1.5.3.2	Data Package 2

Data package #2 would be used for an item that is less simple; having a motor or simple sequence of operation.

a.	Safety precautions

b.	Normal operations

c.	Environmental conditions

d.	Lubrication data

e.	Preventive maintenance plan and schedule

f.	Maintenance and repair procedures

g.	Removal and replacement instructions

h.	Spare parts and supply list

i.	Parts identification

j.	Warranty information

k.	Contractor information

1.5.3.3	Data Package 3

Data package #3 would be used for a complex piece of equipment; having a complex troubleshooting method or sequence of operation.

a.	Safety precautions

b.	Normal operations

c.	Emergency operations

d.	Environmental conditions

e.	Lubrication data

f.	Preventive maintenance plan and schedule

g.	Troubleshooting guides and diagnostic techniques

h.	Wiring diagrams and control diagrams

i.	Maintenance and repair procedures

j.	Removal and replacement instructions

k.	Spare parts and supply list

l.	Parts identification

m.	Warranty information

n.	Testing equipment and special tool information

o.	Contractor information

1.5.3.4	Data Package 4

Data package #4 would be used for an extremely complex piece of equipment, or complex troubleshooting sequence, and require frequent operator attention.

a.	Safety precautions

b.	Operator prestart

c.	Startup, shutdown, and post-shutdown procedures

d.	Normal operations

e.	Emergency operations

f.	Operator service requirements

g.	Environmental conditions

h.	Lubrication data

i.	Preventive maintenance plan and schedule

j.	Troubleshooting guides and diagnostic techniques

k.	Wiring diagrams and control diagrams

l.	Maintenance and repair procedures

m.	Removal and replacement instructions

n.	Spare parts and supply list

o.	Corrective maintenance man-hours

p.	Parts identification

q.	Warranty information

r.	Personnel training requirements

s.	Testing equipment and special tool information

t.	Contractor information

1.5.3.5	Data Package 5

Data package #5 is similar to data package #2, but requires slightly less information.

a.	Safety precautions

b.	Environmental conditions

c.	Preventive maintenance plan and schedule

d.	Troubleshooting guides and diagnostic techniques

e.	Wiring and control diagrams

f.	Maintenance and repair procedures

g.	Spare parts and supply list

h.	Warranty information

1.6	SUBMISSION OF MAINTENANCE SCHEDULE

Include the following information for preventive and scheduled maintenance to minimize corrective maintenance and repair.

1.6.1	Lubrication Data

Include lubrication data, other than instructions for lubrication in accordance with paragraph entitled “Operator Service Requirements”:

a.	A table showing recommended lubricants for specific temperature ranges and applications;

b.	Charts with a schematic diagram of the equipment showing lubrication points, recommended types and grades of lubricants, and capacities; and

c.	A lubrication schedule showing service interval frequency.

1.6.2	Preventive Maintenance Plan and Schedule

Include manufacturer’s schedule for routine preventive maintenance, inspections, tests and adjustments required to ensure proper and economical operation and to minimize corrective maintenance and repair.  Provide manufacturer’s projection of preventive maintenance man-hours on a daily, weekly, monthly, and annual basis.

1.6.3	Corrective Maintenance

Include manufacturer’s recommendations on procedures and instructions for correcting problems and making repairs.

1.6.3.1	Troubleshooting Guides and Diagnostic Techniques

Include step-by-step procedures to promptly isolate the cause of typical malfunctions.  Describe clearly why the checkout is performed and what conditions are to be sought.  Identify tests or inspections and test equipment required to determine whether parts and equipment may be reused or require replacement.

1.6.3.2	Wiring Diagrams and Control Diagrams

Wiring diagrams and control diagrams shall be point-to-point drawings of wiring and control circuits including factory-field interfaces.  Provide a complete and accurate depiction of the actual job specific wiring and control work.  On diagrams number electrical and electronic wiring and pneumatic control tubing and the terminals for each type identically to actual installation numbering.

1.6.3.3	Maintenance and Repair Procedures

Include instructions and list tools required to restore product or equipment to proper condition or operating standards.

1.6.3.4	Removal and Replacement Instructions

Include step-by-step procedures and list required tools and supplies for removal, replacement, disassembly, and assembly of components, assemblies, subassemblies, accessories, and attachments.  Provide tolerances, dimensions, settings and adjustments required.  Instructions shall include a combination of text and illustrations.

1.6.3.5	Spare Parts and Supply Lists

Include lists of spare parts and supplies required for maintenance and repair to ensure continued service or operation without unreasonable delays.  Special consideration is required for facilities at remote locations.  List spare parts and supplies that have a long lead time to obtain.

1.6.3.6	Corrective Maintenance Man-Hours

Include manufacturer’s projection of corrective maintenance man-hours.  Corrective maintenance that requires participation of the equipment manufacturer shall be identified and tabulated separately.

1.6.4	Appendices

Provide information required below and information not specified in the preceding paragraphs but pertinent to the maintenance or operation of the product or equipment.  Include the following:

1.6.4.1	Parts Identification

Provide identification and coverage for all parts of each component, assembly, subassembly, and accessory of the end items subject to replacement.  Include special hardware requirements, such as requirement to use high-strength bolts and nuts.  Identify parts by make, model, serial number, and source of supply to allow reordering without further identification.  Provide clear and legible illustrations, drawings, and exploded views to enable easy identification of the items.  When illustrations omit the part numbers and description, both the illustrations and separate listing shall show the index, reference, or key number which will cross-reference the illustrated part to the listed part.  Parts shown in the listings shall be grouped by components, assemblies, and subassemblies.

a.	Manufacturer’s standard commercial practice:  The parts data may cover more than one model or series of equipment, components, assemblies, subassemblies, attachments, or accessories, such as a master parts catalog, in accordance with the manufacturer's standard commercial practice.

b.	Other than manufacturer’s standard commercial practice:  End item manufacturer may add a cross-reference to implement components’ assemblies and parts requirements when implementation in manual form varies significantly from the style, format, and method of manufacturer's standard commercial practice.  Use the format in the following example:

End Item				 Actual

Manufacturer’s		 Manufacturer’s Name	Actual Manufacturer

Alphanumeric Sequence		and FSCM			Part No.

100001		      John Doe & Co. 00000	 	 2000002

List FSCM in accordance with DLA H4/H8.

1.6.4.2	Warranty Information

List and explain the various warranties and include the servicing and technical precautions prescribed by the manufacturers or contract documents to keep warranties in force.

1.6.4.3	Personnel Training Requirements

Provide information available from the manufacturers to use in training designated personnel to operate and maintain the equipment and systems properly.

1.6.4.4	Testing Equipment and Special Tool Information

Include information on test equipment required to perform specified tests and on special tools needed for the operation, maintenance, and repair of components.

1.6.4.5	Contractor Information

Provide a list that includes the name, address, and telephone number of the General Contractor and each subcontractor installing the product or equipment.  Include local representatives and service organizations most convenient to the project site.  Provide the name, address, and telephone number of the product or equipment manufacturers.

1.7	SUBMISSION OF O&M MANUALS

1.7.1	Requirements

1.7.1.1	Quantity

Submit five copies of the Operation and Maintenance Manual for the Recharge Bed to be incorporated into the current O&M Manual for the entire treatment facility.

1.7.1.2	Delivery

Submit O&M manual to the RE for review or acceptance according to the following schedule:

a.	Outline:  90 days before System Checkout.

b.	Initial O&M Manual:  30 days before System Checkout.

1.8.2	System Startup, Shakedown, and Initial Operation and

Maintenance

The management and operation of the recharge bed system (i.e. all management, maintenance, testing, and adjustments necessary to provide startup, shakedown and operation of the system) and the monitoring of ground water (both contaminants and level) after the system checkout is completed is not part of this contract.

PART 2	PRODUCTS

PART 3	EXECUTION

3.1	OPERATION AND MAINTENANCE MANUALS

Develop and implement an Operation and Maintenance Manual for the Recharge Bed, expanded sprinkler system, conveyance piping, and controls. The manual shall also include a periodic maintenance schedule and maintenance procedure, troubleshooting methods, MSDS, and safety issues.  The O&M Manual for the Recharge Bed will be incorporated into the current O&M Manual for the ground water treatment system.

3.1.1	Initial Operation and Maintenance Manual

Prepare an Initial Operation and Maintenance Manual which shall be used as a guide to plan startup during the shakedown period.  Submit Initial O&M manual 30 days before System Checkout.  Submit outline 90 days before System Startup Checkout.

3.1.1.1	Manual contents:

The Initial Operation and Maintenance Manual is subject to RE approval and shall contain the following information:

a.	Description of normal operation and maintenance

1.	Description of operating conditions

2.	Description of tasks for operation

3.	Description of tasks for maintenance

4.	Frequency of each operation and maintenance task

b.	Description of potential operating problems

1.	Description and analysis of potential operating problems

2.	Sources of information regarding the problem

3.	Common remedies

c.	Description of routine and existing NJDPES-DGW permit requirements and monitoring and laboratory testing

1.	Description of monitoring tasks

2.	Description of required laboratory tests and their implementation

3.	Required quality assurance/quality control (QA/QC)

4.	Schedule monitoring and testing frequency

5.	Additional monitoring and testing requirements

d.	Description of alternative operation and maintenance

1.	Alternative procedures to prevent undue hazard

2.	Analysis of vulnerability and additional resources

3.	Requirements should a failure occur

e.	Safety plan

1.	Description of general precautions and equipment for site personnel

2.	Safety plans required in emergencies

f.	Equipment maintenance

1.	General maintenance requirements and frequency

2.	Equipment record system

3.	Site and equipment maintenance

g.	Annual operation and maintenance budget

3.2	SYSTEM CHECKOUT

Furnish a qualified system checkout team responsible for demonstrating proper operation of all system components.

During checkout, test the function of all equipment and controls and perform any necessary instrument calibrations.

Once Recharge Bed checkout has been accomplished and all systems are working to the satisfaction of the RE, petition the RE to accept the system and begin System Startup and Shakedown.

END OF SECTION

SECTION 15011

MECHANICAL GENERAL REQUIREMENTS

PART 1	GENERAL

1.1	REFERENCES

The publications listed below form a part of this specification to the extent referenced. The publications are referred to in the text by the basic designation only.

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM B 117	(1997) Operating Salt Spray (Fog) Apparatus

U.S. NATIONAL ARCHIVES AND RECORDS ADMINISTRATION (NARA)

29 CFR 1910.147	Control of Hazardous Energy (Lock Out/Tag Out)

1.2 	QUALITY ASSURANCE

1.2.1 	Material and Equipment Qualifications

Provide materials and equipment that are standard products of manufacturers regularly engaged in the manufacture of such products, which are of a similar material, design and workmanship. Standard products shall have been in satisfactory commercial or industrial use for 2 years prior to bid opening. The 2-year use shall include applications of equipment and materials under similar circumstances and of similar size. The product shall have been for sale on the commercial market through advertisements, manufacturers’ catalogs, or brochures during the 2 year period.

1.2.2 	Alternative Qualifications

Products having less than a two-year field service record will be acceptable if a certified record of satisfactory field operation for not less than 6000 hours, exclusive of the manufacturer’s factory or laboratory tests, can be shown.

1.2.3 	Service Support

The equipment items shall be supported by service organizations. Submit a certified list of qualified permanent service organizations for support of the equipment which includes their addresses and qualifications. These service organizations shall be reasonably convenient to the equipment installation and able to render satisfactory service to the equipment on a regular and emergency basis during the warranty period of the contract.

1.2.4 	Manufacturer’s Nameplate

Each item of equipment shall have a nameplate bearing the manufacturer's name, address, model number, and serial number securely affixed in a conspicuous place; the nameplate of the distributing agent will not be acceptable.

1.2.5 	Modification of References

In each of the publications referred to herein, consider the advisory provisions to be mandatory, as though the word, “shall” had been substituted for “should” wherever it appears. Interpret references in these publications to the “authority having jurisdiction,” or words of similar meaning, to mean the Contracting Officer (CO) or Resident Engineer (RE).

1.3	DELIVERY, STORAGE, AND HANDLING

Handle, store, and protect equipment and materials to prevent damage before and during installation in accordance with the manufacturer’s recommendations, and as approved by the RE. Replace damaged or defective items.

1.4 	SAFETY REQUIREMENTS

1.4.1 	Equipment Safety

Provide positive means of locking out equipment so that equipment cannot be accidentally energized during maintenance procedures.  Provide catwalks, maintenance platforms, and guardrails where required for safe operation and maintenance of equipment. Provide ladders or stairways to reach catwalks and maintenance platforms. Ensure that access openings leading to equipment are large enough to carry through routine maintenance items such as filters and tools.

1.4.2 	Warning Sign

Provide a permanent placard or sign at the entrance to confined spaces contained in the equipment. The sign shall warn personnel not to enter the space until the atmosphere inside has been tested and systems have been de-energized.

1.4.3 	Lockout of Energy Sources

Provide appropriate lockout devices for energy isolating valves and for machines or other equipment to prevent unexpected start-up or release of stored electrical, mechanical, hydraulic, pneumatic, thermal, chemical, or other energy in accordance with 29 CFR 1910.147. Lockout devices for valves shall provide a means of attachment to which, or through which, a lock can be affixed or shall have a locking mechanism built into it so that the valve cannot be moved from the lockout position until the lock is removed.

1.5 	ELECTRICAL REQUIREMENTS

Furnish motors, controllers, disconnects and contactors with their respective pieces of equipment. Motors, controllers, disconnects and contactors shall conform to and have electrical connections provided under DIVISION 16, “ELECTRICAL.”  Furnish internal wiring for components of packaged equipment as an integral part of the equipment. Extended voltage range motors will not be permitted. Controllers and contactors shall have a maximum of 120 volt control circuits, and shall have auxiliary contacts for use with the controls furnished. When motors and equipment furnished are larger than sizes indicated, the cost of additional electrical service and related work shall be included under the section that specified that motor or equipment. Power wiring and conduit for field installed equipment shall be provided under and conform to the requirements of DIVISION 16.

1.6 	INSTRUCTION TO GOVERNMENT PERSONNEL

When specified in other sections, furnish the services of competent instructors to give full instruction to the designated Government personnel in the adjustment, operation, and maintenance, including pertinent safety requirements, of the specified equipment or system. Instructors shall be thoroughly familiar with all parts of the installation and shall be trained in operating theory as well as practical operation and maintenance work. Instruction shall be given during the first regular work week after the equipment or system has been accepted and turned over to the Government for regular operation. The number of man-days (8 hours per day) of instruction furnished shall be as specified in the individual section. When more than 4 man-days of instruction are specified, use approximately half of the time for classroom instruction. Use other half of the time for instruction with the equipment or system. When significant changes or modifications in the equipment or system are made under the terms of the contract, provide additional instruction to acquaint the operating personnel with the changes or modifications.

1.7	ACCESSIBILITY

Install all work so that parts requiring periodic inspection, operation, maintenance, and repairs, are readily accessible.

1.8	VERIFICATION OF DIMENSIONS

Coordinate the proper relation of the work to the building structure and to the work of all trades.  Visit the premises and become familiar with the dimensions in the field, and advise the RE of any discrepancy before performing any work.

PART 2 	PRODUCTS

Not used.

PART 3 	EXECUTION

Not used.

END OF SECTION

SECTION 15060

VALVES AND PIPING APPURTENANCES

PART 1	GENERAL

1.1	DESCRIPTION

All materials supplied and the installation shall conform to the applicable standards referenced in paragraph 1.3 below.

1.2	QUALITY ASSURANCE

All materials supplied and the installation shall conform to the applicable standards referenced.  All materials provided shall be new.

Provide materials and equipment that are standard products of manufacturers regularly engaged in the manufacture of such products, which are of similar material design and workmanship.  Standard products shall have been in satisfactory commercial or industrial use for 2 years prior to bid opening.  The 2 year use shall include applications of equipment and materials under similar circumstances and of similar size.

1.3	REFERENCES

The publications listed below form a part of this specification to the extent referenced. The publications are referred to in the test by the basic designation only.

AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI)

ANSI B31 		Code for Pressure Piping

ANSI B31.3	Process Piping

ASME/ANSI B31.9	Building Service Piping

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM A 126	Gray Iron Castings for Valves, Flanges, and Pipe Fittings

ASTM A 240	Standard Specification for Heat Resisting Chromium and Chromium-Nickel Stainless Steel Plate, Sheet, and Strip for Pressure Vessels

ASTM D 1784	Standard Specification for Rigid Poly (Vinyl Chloride) (PVC) Compounds and Chlorinated Poly (Vinyl Chloride) (CPVC) Compounds

ASTM D 1785	Standard Specifications for Poly (Vinyl Chloride) (PVC) Plastic Pipe, Schedules 40, 80, and 120.

ASTM D 2464	Standard Specifications for Threaded Poly (Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 80

ASTM D 2466	Standard Specification for Poly (Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 40

ASTM D 2657 	Heat Fusion Joining Polyolefin Pipe and Fittings

ASTM D 2564	Standard Specification for Solvent Cements for Poly (Vinyl Chloride) (PVC) Plastic Piping Systems

ASTM D 3035	Standard Specification for Polyethylene (PE) Plastic Pipe (PR) Based on Controlled Outside Diameter

ASTM D 3212	Joints for Drain and Sewer Plastic Pipes Using Flexible Elastomeric Seals

ASTM D3350	Polyethylene Plastic Pipe and Fittings Materials

AMERICAN WATER WORKS ASSOCIATION (AWWA)

AWWA C800	Underground Service Line Valves and Fittings

AWWA C901	Polyethylene (PE) Pressure Pipe and Tubing, ½ Inch Through 3 Inch, for Water Services

BUILDING OFFICIALS AND CODE ADMINISTRATORS INTERNATIONAL (BOCA)

BOCA		National Building Code (1996 or latest version in effect at time of construction).

BOCA 		National Plumbing Code (1996 or latest version in effect at time of construction).

BOCA 		National Mechanical Code (1996 or latest version in effect at time of construction).

BOCA		National Building Code (1996 or latest version in effect at time of construction).

BOCA 		National Plumbing Code (1996 or latest version in effect at time of construction).

BOCA 		National Mechanical Code (1996 or latest version in effect at time of construction).

THE PLASTIC PIPE INSTITUTE (PPI)

TR-31		Underground Installation of Polyolefin Piping

1.4	SUBMITTALS

Submit the following in accordance with section 01330, “Submittal Procedures”.

    - SD-01, Manufacturer’s Catalog Data; GA

- Combination Vacuum and Air Relief Valves

- Flow Control Valves

- Sprinkler System Components

- Gaskets not submitted with other component information

    - SD-04, Drawings; GA

- Submit copies of manufacturer's literature and shop drawings for items in Article 1.4.1 and appurtenances not specifically listed in Article 1.4.1, which are not part of or integral to other pieces of equipment.

- Submit a plan showing the proposed location of all sprinkler heads for the Area B sprinkler system expansion.

1.4.3	SD-19, Addenda to Operation and Maintenance Instructions; GA

The Contractor shall provide 6 copies of operation and maintenance instruction listing routine maintenance procedures, possible breakdowns and repairs, and trouble shooting guides for all items addressed in Sections 1.4.1 and 1.4.2.  The instructions will be included as an addenda to the existing Operation and Maintenance Plan for the ground water treatment system.  Refer to section 13999, “Operations and Maintenance Requirements”.

1.5	EQUIPMENT TAGGING

All piping, valves and components shall be tagged.

1.6 	DELIVERY, STORAGE, AND HANDLINE

Inspect materials delivered to site for damage; unload and store with minimum handling.  Store materials on-site in enclosures or under adequate cover to prevent damage, protect materials not suitable for outdoor storage to prevent damage during periods of inclement weather, such as subfreezing temperatures, precipitation, and high winds.  Store materials susceptible to deterioration by direct sunlight under cover and avoid damage due to high temperatures.  Do not store materials directly on ground.  If special precautions are required, prominently and legibly stencil instructions for such precautions on outside of equipment or its crating.

PART 2	PRODUCTS

2.1	VALVES

Contractor shall furnish and install valves as indicated on drawings.  All valves furnished under these specifications shall be product of a manufacturer who has had long experience in design of valves and whose products have proven reliable in service in similar installations over a reasonable period of years.  Unless specified otherwise, all valves shall be of the same size as the line in which they are installed.

Piping shall be installed principally as shown on the drawings.  Refer to the drawings to ensure all required valves and instruments are provided.  In addition, provide whatever piping and fittings are necessary, whether shown on the drawings or not, for a complete and working system.  Provide flanged connectors for all process valves, instruments, and sensors to facilitate removal (except those items with end connections of 2 inches or less may be threaded or provided with a threaded or socket union).

2.1.1	Combination Vacuum and Air Relief Valves

Combination vacuum and air relief valves shall be standard single body, double orifice combination air valves and conforming to ASTM A126, with Buta-N seals and have threaded connections.  Floats shall be constructed of heavy stainless steel, hermetically sealed, designed to withstand 1000 psi, and shall conform to ASTM A240.

The larger orifice shall allow large volumes of air to discharge or enter during pipeline during filling and drainage, respectively.  The smaller orifice shall be capable of continuously venting air pockets as they accumulate in the piping.  The body inlet shall be baffled to protect the lower float from direct forces of rushing air and water to prevent premature valve shut-off.  The top large orifice plug or float shall be protected in a similar manner for the same purpose.  The Buna-N seat shall be fastened to the valve cover, without distortion, for drop tight shut-off.  The top plug or float shall be center guided through hex bushings for positive shut-off.  The valve shall be APCO (manufactured by APCO Williamette Valve and Primer Corporation) combination air valve Model 143C.

2.1.2	Control Valves

2.1.2.1	Flow Control/Isolation Valve

Cast Iron body butterfly valve.  Stainless steel shaft.  Elastomeric body seat.  Nylon Bearings.  Valve disc shall be ASTM A – 126 Class B cast iron with a 316 stainless steel edge.  Fully open, the valve shall create no more friction than a 45 degree elbow.  Minimum 150 psig working service.  Provide curb box and valve turning handle with valve.

2.1.2.2	Throttle Valve (larger than 4")

The throttle valves shall be PVC butterfly valves sized the same size as the pipe.  All solid thermoplastic butterfly valves sizes > 4” through 16" shall be constructed from PVC type I cell classification 12454.  All valve seats and O-rings shall be Viton.  Seat shall be a non-lenear type interlocked to valve body.  Bolt hole patterns shall conform to ANSI/ASME B16.5 Class 150.  Disc shall be offset design with fully isolated Type 316L stainless steel stem and Type 316 stainless steel hardware.  Valve bodies shall accept field installable lug inserts or shall be factory installed true lug type.   Lugs shall be stainless steel or zinc plated steel.  Valves shall be pressure rated at 150 psig for water at 73(F.  Gear operators shall be worm gear design, self locking with diecast aluminum body.

The throttle valve shall include an electric operator.  The electric operator shall be provided complete with actuators, speed controls and accessories.  The actuators shall operate on 120 VAC, 60 Hz with a 75 percent duty cycle and shall be equipped with an AC thermal overload protector with automatic rest, reversing (bi-directional) operation for use with quarter-turn valves, or rotating equipment to full rotation.  Gearing shall be a two-stage planetary, permanently lubricated self locking gear train with self-lubricating bearings; connections via male output staff.  The startup torque shall be 120-foot pounds.  The stall torque shall be 150 foot-pounds.  Travel stop limit switches with cams, internal, independent, adjustable, and actuated by cams shall be mounted on the dive shaft.  A side mounted hand turn wheel shall be provided for a manual override.  The actuators shall have a NEMA 250 Type 4 enclosure with a corrosion resistant, baked epoxy finish as standard.  The actuator shall operate in a temperature range of –40 to 150 degrees F.  Actuators shall fail in last position unless otherwise indicated.

Valves shall be capable of modulation based on signals from the valve position indicators.  The positioners for modulating actuators shall control valve positions as a function of the input signals.  The positioner shall operate on 120 VAC, 60 Hz voltage.  Modulating valve positioners shall operate on a 4 to 20 mA input signal unless otherwise indicated.  Corrosion resistant enclosures for positioners shall be splash and moisture-proof with gasketed covers.

All actuated valves shall be supplied with a manual operator.  The force in a manual operator shall not exceed 39.3 pounds under any operating condition, including initial breakaway.  The operator shall be equipped with gear reduction when force exceeds 39.3 pounds.  The manual operator shall be a self-locking type or shall be equipped with a self-locking device.  A position indicator shall be supplied on quarter-turn valves.  Worm and gear operators shall be a one-piece design with worm-gears of gear bronze material.  Worm shall be hardened alloy steel with the threaded ground and polished.  Traveling nut type operators shall have threaded steel reach rods with an internally threaded bronze or ductile iron nut.

Exposed operators shall have galvanized and painted handwheels.  Lever operators are allowed on quarter-turn valves less than 8 inches.  Cranks shall be supplied on gear type operators.

2.2	Sprinkler/Irrigation System Components

2.2.1	Sprinkler/Irrigation System Above Grade Piping

Provide 2” (SDR-17) and 1 ½” (SDR-11) flexible, smooth walled, pressure rated polyethylene (PE) piping and fittings manufactured to AWWA C901 and ASTM D3035.  Pressure class shall be at least 100 psi.  Provide Driscoplex Series 4100 piping and fittings, or approved equivalent.

Piping and fittings shall be resistant to corrosion, aggressive soils, biological growth, ultraviolet light, and thermal degradation.  The pipe shall be homogeneous throughout and free from visible cracks, holes, foreign materials, blisters, wrinkles and dents.  The pipe shall be marked with an easily legible and permanent surface mark specifically identifying the manufacturer by name or trademark and the size, schedule, and type of pipe.

All PE piping and fittings shall be joined by the heat fusion or electro fusion process, producing homogenous sealed, leak-tight joints in accordance with the manufacturer’s recommendations and procedures.

2.2.2	Sprinkler/Irrigation System Zone Valves

Each sprinkler/irrigation system zone valve shall be an electrical solenoid actuated, industrial-strength, glass-filled nylon globe valve rated for 200 psi, with self-cleaning scrubber, stainless steel screen, and nylon-reinforced rubber diaphragm.  Valve shall be slow closing to prevent water hammer.  Solenoid shall be 24V 50/60Hz cycle with a captured plunger and spring design for easy servicing.  Valves shall be Rain Bird Model No. 200-PESB (2 inch size) or approved equal.

2.2.3	Sprinkler/Irrigation System Valve Boxes

Valve boxes shall be of sufficient size to house the zone valve, fittings, and electrical conduit as shown on the Contract Drawings with at least two inches of space on all sides.  The sides shall be corrugated with built in knockouts.  Provide Rain Bird Jumbo Valve Box (12.1” H x 19.8” W x 26.3” L) or approved equal.

2.2.4	Sprinkler Heads

Sprinkler heads shall be ¾” male NPT, full circle, heavy duty brass impact type, with stainless steel springs and fulcrum pin, chemically resistant washers, and dual nozzle ports.  Nozzles shall be brass straight bore with 3/16” nozzle with vane.  Broadcast radius shall be 50 feet at a flow rate of 6.40 gpm and 40 psi at the nozzle, with a trajectory angle of 27 degrees.  Period of warranty shall be at least two years.  Sprinkler heads shall be Rain Bird A10713-12.

2.2.5	Sprinkler Stands

Provide portable sprinkler stands for the sprinkler heads to ensure adequate clearance of low lying vegetation and proper broadcast of spray.  Stands shall consist of galvanized steel or aluminum parts, including an adjustable telescoping riser, support legs or stand, and all parts and fittings necessary to connect the sprinkler system piping to the bottom of the riser, and connect the sprinkler head to the top of the riser.  Quick connect type fittings shall be used to allow rapid connection and disconnection of the sprinkler piping from the stand.  Riser shall be adjustable or telescope to a height ranging from approximately 4 feet to 6 feet.  The diameter of the riser for shall be no less than sprinkler head bearing size and no greater than the diameter of the sprinkler system piping to be connected to the bottom of the riser.

Sprinkler stand shall remain stable, without tipping, during full 360 degree rotation of sprinkler head operating at the intended maximum pressure and flow rate, and during high winds.

Sprinkler stands shall be either be of the commercially fabricated type available from such manufacturers or vendors as Wade Manufacturing Co., Larchmont Engineering and Irrigation Supplies, or Jain Irrigation Systems Limited, or shall be custom fabricated by the contractor to meet the specified requirements.  The Contractor should be aware that lead times may vary significantly depending on the supplier.

2.3	MISCELLANEOUS ITEMS & FITTINGS

2.3.1	Quick Connects

Quick connects shall be aluminum with Viton gaskets as manufactured by Cam-Lok or approved equal.  Provide caps for male end connections and plugs for female end-connections.

2.3.2	Hose Connections

Hose connections shall be as manufactured by OPW, or approved equal.

2.4	IDENTIFICATION TAGS AND PLATES

Provide valves with tags or plates numbered and stamped for their usage.  Plates and tags shall be of brass or nonferrous materials and shall be mounted or attached to the valve.

PART 3	EXECUTION

3.1	INSTALLATION

3.1.1	No defective materials shall be used.  Any piece discovered to be defective shall be removed and replaced by a sound and satisfactory piece.

3.1.2	Any material showing a crack and which has received a severe blow that may have caused an incipient fracture, even though no such fracture can be seen, shall be marked as rejected and removed at once from work.

3.1.3	All materials shall be cleaned of all debris and dirt before being used and shall be kept clean until accepted in completed work.

3.1.4	Materials shall be accurately installed to required lines and grades.  Care shall be taken to preserve a good alignment.

3.1.5	All components shall be installed in accordance with manufacturer’s recommendations.  All joints shall be made in clean dry conditions and in strict accordance with manufacturer's recommendations.

3.1.6	All components shall be installed principally as shown on the drawings.  Refer to the drawings to ensure all required valves, instruments and sensors, as well as associated appurtenances are provided.  In addition, provide whatever piping and fittings are necessary, whether shown on the drawings or not, for a complete and working system.  Provide flanged connectors for all process valves, instruments, and sensors to facilitate removal (except those items with end connections of 2 inches or less may be threaded or provided with a threaded or socket union).

3.1.7	The Contractor shall use appropriate fittings to prevent kinks or other restrictions in the pipe.  All resulting joints shall be watertight.

3.1.8	Provide facilities for lowering components into position.  Do not drop or dump fittings, valves, or any other piping material into manholes.  Cut pipe accurately to measurements established at the site and work into place without springing or forcing.  Replace pipe or fitting that does not allow sufficient space for proper component installation.  Support components at their proper elevation and grade; ensure firm and uniform support.

END OF SECTION

SECTION 16010

GENERAL REQUIREMENTS FOR ELECTRICAL WORK

PART 1	GENERAL

## 1.0	REFERENCES

A.	Refer to the GENERAL REQUIREMENTS and applicable parts of DIVISION 1 for other general requirements.

1.	GENERAL REQUIREMENTS and DIVISION 1 paragraphs may be repeated in other Specification Sections within this Division for emphasis or for inclusion of more stringent/additional related requirements. Such repetition shall NOT be construed to reduce the requirements of those Divisions NOR to eliminate other requirements under those Divisions.

B.	Refer to other Sections of this Division for detailed specifications on the work of this Division.

## 1.2	INTENT

A.	It is the intent of the Contract Documents to require finished work, tested and ready for operation.

B.	It is not intended that Contract Documents show every pipe, wire, conduit, fitting and appurtenance; however, such parts as may be necessary to complete the systems in accordance with best trade practice and Code requirements and to Resident Engineer’s (RE) satisfaction shall be deemed to be included.

C.	Drawings are diagrammatic and indicate the general arrangement of systems and work included in the Contract.  Contractor shall confirm all clearances, elevations, equipment layout, equipment sizes, etc., based on actual Contractor proposed components and installation.

1.3	.	EXAMINATION OF SITE AND CONTRACT DOCUMENTS

A.	Before submitting prices or beginning work, thoroughly examine the site and the Contract Documents.

B.	No claim for extra compensation will be recognized if difficulties are encountered which would have been revealed by examination of site conditions and Contract Documents prior to executing Contract.

C.	Where discrepancies occur within Contract Documents, notify the RE, in writing, of discrepancy and request clarification.  Until notified of RE’s decision, include item or arrangement of better quality, greater quantity or higher cost in Contract price.

1.	For material, device and equipment identified on Contract Drawings by manufacturer and model:  check Specification for ancillary requirements such as pilot lights or alarms, and include same with furnished item.  If Specifications require different model, notify RE of discrepancy and request clarification.

D.	Notify RE, in writing, of materials and apparatus believed to be omitted, inadequate or unsuitable, or in violation of laws, ordinances, rules or regulations of authorities having jurisdiction.  In absence of such written notice, it is mutually agreed that bid price for work under each Section has included the cost of items required for acceptable satisfactory functioning of entire system.

1.4		DEFINITIONS

A.	Where more than one material, item, or grade is listed in same paragraph, first one named is preferred choice.

B.	The following terms are used in this Division and are defined as follows:

1.	“Indicated”, “shown”, “noted”, “scheduled”, “specified”:  These terms are a cross-reference to graphics, notes or schedules on the Drawings, to other paragraphs or schedules in the Specifications, and to similar means of recording requirements in Contract Documents.  NO limitation of location is intended except as specifically noted.

2.	“Directed”, “requested”, “authorized”, “selected”, “required”, “permitted”:  Where not otherwise explained, these terms mean “directed by the RE”, “requested by the RE”, etc.  However, NO such implied meaning will be interpreted to extend the RE’s responsibility into Contractor’s area of construction supervision.

3.	“Provide”:  To furnish and install, ready for safe and regular operation the item, material or service indicated.

4.	“Furnish”:  To purchase, acquire and deliver to the site, complete with related accessories.

5.	“Install”:  To erect, mount and connect completely, by acceptable methods.

6.	“Work”:  Labor, materials, equipment, apparatus, controls and accessories required for proper and complete installation.

7.	“Concealed”:  Embedded in masonry or other construction; or installed in furred spaces, trenches or crawl spaces; or installed within double partitions or hung ceilings; or in enclosures.

8.	“Exposed”:  Visible to building occupants, excluding mechanical room and utility tunnel locations.

9.	“Acceptable equivalent” or “Equal”:  Of weight, size, design, capacity and efficiency to meet requirements specified and shown, and of acceptable manufacture, as determined in the opinion of the RE.

10.	“Acceptable”:  Acceptable, as determined in the opinion of the RE.

11	“Contractor”:  General Contractor.

12	“Named” Product:  Manufacturer’s name for product, as recorded in published documents of latest issue as of date of Contract Documents.  Obtain RE’s permission before using products of later or earlier model.

C.	Standards, specifications and tests of following technical societies, organizations and governmental bodies, as referenced in Contract Documents, are hereby made part of Contract Documents.

1.	IES:  Illuminating Engineering Society.

2.	ANSI:  American National Standards Institute

3.	ASTM:  American Society for Testing and Materials

4.	EPA:  Environmental Protection Agency

5.	FSSC:  Federal Specification

6.	IEEE:  Institute of Electrical and Electronics Engineers

7.	IRI:  Industrial Risk Insurers

8.	ISO:  Insurance Services Office

9.	NBS:  National Bureau of Standards

10.	NEC:  National Electrical Code.

11	NEMA:  National Electrical Manufacturers Association

12	NFPA:  National Fire Protection Association

13.	NSC:  National Safety Council

14.	OSHA:  Occupational Safety and Health Administration

15.	UL:  Underwriters Laboratories

16.	FAA:  US Federal Aviation Administration

17.	FED. SPECS.: Federal Specifications

18.	CODE:  Codes and regulations of the Federal, State and local governments and of utility companies having jurisdiction, as appropriate.

D.	Use of singular or plural reference form in these Specifications shall not be construed to limit number of units required.  Specifications are intended to define quality and performance characteristics; quantity of units supplied shall be as needed to meet requirements as specified and as shown on Contract Documents.

1.5		PERMITS, LAWS, ORDINANCES AND CODES

A.	Contractor shall obtain and pay for all permits, inspections, licenses and certificates required for work under this Division.

B.	Complete Utility connections as indicated or needed, extension to Project, metering as required, and connection to building systems, including:

1.	Apply for all services and pay for all fees, assessments and charges of the Utility for each connection, all in a timely manner and according to the Project Schedule.

2.	Provide and install all metering equipment and accessories as required by Utility.  Install entire service in accordance with the Utility’s requirements or other applicable regulation.

3.	Coordinate with Utility to determine scope of work provided by Utility and the part provided by Contractor so that a complete Utility connection is made.

4.	Schedule all work required by utility companies in order to maintain project schedule.

C.	Contractor shall pay utility company charges associated with work of this Division.

D.	Contractor shall comply with laws, ordinances, rules and regulations of local, state and federal authorities having jurisdiction; and shall comply with rules and regulations of National Board of Fire Underwriters, National Electrical Code and local utility companies.

E.	Contract Documents shall govern whenever they are more stringent than Code requirements.

1.6		SHOP DRAWING SUBMITTALS

A.	Prepare and submit Shop Drawings through the Contractor to the RE for review.

B.	The selection and intention to use a product specified by name shall NOT excuse the need for timely submission of shop drawings for that product.

C.	Prior to submitting shop drawings, submit for review preliminary list of intended or proposed manufacturers for all items for which shop drawings are required.

D.	Submission of shop drawings of an unnamed manufacture or shop drawings at variance with the Contract Documents is NOT a proper request for substitution.

E.	Samples that are submitted in lieu of shop drawings shall be clearly identified and shall be submitted in duplicate.  Only one sample will be returned and that accepted sample shall be kept available at appropriate job site office.  Accepted sample retained by RE will be kept available at RE’s home office.

F.	Submittals shall include the following information:

1.	Descriptive and product data necessary to verify compliance with Contract Documents.

2.	Manufacturer’s specifications including materials of construction, metal gauge, thickness and finish.

3.	Certified dimensional drawings including clearances required for maintenance or access.

4.	Performance data, ratings, operating characteristics, and operating limits.

5.	Electrical ratings and characteristics.

6.	Wiring and control diagrams, where applicable.

7.	Certifications requested, including UL label or listing.

8.	List of accessories which are required but are NOT being provided by the product manufacturer or are NOT being furnished under this Section.  Identify the Section(s) under which the accessories are being furnished.

G.	In addition, submittals shall be clearly marked for the following:

1.	Specification Section and Paragraph, or Drawing Schedule/Note/Detail/etc., where equipment is specified.

2.	Equipment or fixture identification corresponding to that used in Contract Documents.

3.	Accessories and special or non-standard features and materials which are being furnished.

1.7		PRODUCT SELECTION

A.	Contractor’s options for selecting products are limited by Contract Document requirements and governing regulations and are NOT controlled by industry traditions or procedures experienced by Contractor on previous construction projects. Required procedures include, but are NOT necessarily limited to, following various methods of specifying:

1.	Single Product Manufacturer Named:  Provide product indicated.

2.	Two or More Manufacturers’ Products Named:  Provide one of the named products, at Contractor’s option, but excluding products which do NOT comply with requirements.

3.	“Acceptable equivalent” or “Or Equal”:  Where named products are accompanied by this term or words of similar effect, provide one of named products or proposed substitute products.  Substitute products must meet all the requirements of the named produce.  The Contractor is responsible for ensuring the substitute product is acceptable in accordance with this requirement prior to submitting the product for approval.

4.	Standards, Codes and Regulations:  Where specification requires only compliance with a standard, code or regulation, Contractor may select any product which complies with requirements of that standard, code or regulation.

5.	Performance Requirements:  Provide products which comply with specific performances indicated and which are recommended by manufacturer (in published product literature or by individual certification) for application intended.  Overall performance of product is implied where product is specified with only certain specific performance requirements.

6.	Prescriptive Requirements:  Provide products which have been produced in accordance with prescriptive requirements using specified materials and components, and complying with specified requirements for fabricating, finishing, testing and other manufacturing processes.

7.	Visual Matching:  Where matching with an established material is required, RE’s judgement of whether proposed product matches established material shall be final.

8.	“Color as Selected by RE”:  Unless otherwise noted, where specified product requirements include “color as selected by RE” or words of similar effect, the selection of manufacturer and basic product complying with Contract Documents is Contractor’s option and subsequent selection of color is RE’s option.

B.	Inclusion by name, of more than one manufacturer or fabricator, does NOT necessarily imply acceptability of standard products of those named.  All manufacturers, named or proposed, shall conform, with modification as necessary, to criteria established by Contract Documents for performance, efficiency, materials and special accessories.

1.8		ADDITIONAL SUBMITTALS REQUIREMENT

A.	The following shall be submitted in accordance with Section 01330, “Submittal Procedures”.

B.	SD-01, Manufacturer’s Data

1.	Submittals for each manufactured item shall be current manufacturer’s descriptive literature of cataloged products, equipment drawings, diagrams, performance and characteristic curves, and catalog cuts.

C.	SD-13 Certificates

1.	Certificates of Compliance

Submit manufacturer’s certifications as required on products, materials, finish, and equipment indicated in the technical sections.  Certifications shall be documents prepared specifically for this contract.  Preprinted certifications and copies of previously submitted documents will not be acceptable.  The manufacturer’s certifications shall name the appropriate products, equipment, or materials and the publication specified as controlling the quality of that item.  Certification shall not contain statements to imply that the item does not meet requirements specified, such as “as good as”; “achieve the same end use and results as materials formulated in accordance with the referenced publications”; or “equal or exceed the service and performance of the specified material.”  Certifications shall simply state that the item conforms to the requirements specified.  Certificates shall be printed on the manufacturer's letterhead and shall be signed by the manufacturer’s official authorized to sign certificates of compliance.

2.	Publication Compliance

Where equipment or materials are specified to conform to industry and technical society publications of organizations such as American National Standards Institute (ANSI), American Society for Testing and Materials (ASTM), and Underwriters Laboratories Inc. (UL), submit proof of such compliance.  The label or listing by the specified organization will be acceptable evidence of compliance.  In each of the publications referred to herein, consider the advisory provisions to be mandatory, as though the word “shall” had been substituted for “should” wherever it appears.  Interpret references in these publications to the “authority having jurisdiction,” or words of similar meaning, to mean the RE.  In lieu of the label or listing, submit a certificate from an approved independent testing organization, adequately equipped and competent to perform such services, stating that the item has been tested in accordance with the specified organization’s test methods and that the item conforms to the specified organization’s publication.

## 1.9	INSTRUCTION TO GOVERNMENT PERSONNEL

A.	Where indicated in the technical sections, furnish the services of competent instructors to give full instruction to Government personnel in the adjustment, operation, and maintenance of systems and equipment, including pertinent safety requirements as required.  Each instructor shall be thoroughly familiar with all parts of the installation and shall be trained in operating theory as well as practical operation and maintenance work.  Instruction shall be given during the first regular work week after the equipment or system has been accepted and turned over to the Government for regular operation.  The number of man-days (8 hours) of instruction furnished shall be as specified in each individual section.

1.10	RECORD DRAWINGS

A.	Furnish and keep on the job at all times, one complete and separate set of Contract Documents of the Electrical work.

B.	As work progresses, record changes, revisions and additions to Architectural and Electrical work clearly, neatly, accurately and promptly.  Items to be indicated include but are not limited to:

      - Dimensional change

      - Revision to Drawing detail

      - Location and depth of underground utility

      - Revision to conduit routing

      - Revision to electrical circuitry

      - Actual equipment location

      - Duct size and routing

      - Location of concealed internal utility

      - Changes made by Change Order

      - Details not on original Contract Drawing

      - Information on concealed elements which would be difficult to identify or measure later

C.	Indicate daily progress on these prints by coloring in the various lines, fixtures, apparatus and associated appurtenances as they are erected.

D.	Approval of requisition for payment for work installed will NOT be given unless supported by record prints as required above.

E.	At the conclusion of work, prepare record CAD drawings with accompanying electronic files.  Submit record drawings for review by RE.  Refer to Division 1, General Requirements for further requirements.

1.11	OPERATING AND MAINTENANCE MANUALS

A.	Submit for review operating and maintenance manuals for each system or piece of equipment, at least two weeks prior to request for acceptance of same.  Upon acceptance, furnish six copies of each manual (or greater quantity if otherwise specified under Division 1) to Resident Engineer (RE).  Operating and maintenance manual shall include:

1.	Description of Unit (System) and Component Parts, including function, normal operating characteristics and limiting conditions, performance curves, engineering data and tests, and complete nomenclature and manufacturer’s number for replaceable parts.

2.	Operating Procedures, including start-up, break-in, routine and normal operating instructions; regulation, control, stopping, shutdown and emergency instructions; summer and winter operating instructions; and any special operating instructions.

3.	Maintenance Procedures, including routine operations, guide to trouble-shooting; disassembly, repair and reassembly; alignment, adjusting and checking; servicing and lubrication schedule, and list of lubricants; manufacturer's installation and maintenance bulletins and related information.

4.	Sequence of Operation and Control Diagrams, corrected for as-built conditions.

5.	Parts List, including illustrations, assembly drawings and diagrams required for maintenance, predicted life of parts subject to wear, and recommendations for stocking spare parts.

6.	Copies of accepted shop drawings, charts and diagrams.

7.	Names, addresses and telephone numbers of manufacturer’s representative and service company.

8.	Other data, as required under pertinent Sections of these Specifications.

9.	Letters from each manufacturer certifying that his equipment was properly installed and is operating in accordance with manufacturer’s intent.

1.12	GUARANTEE

A.	Furnish standard manufacturers’ guarantees for work under this Division.  Such guarantees shall be in addition to, and NOT in lieu of, other liabilities under the law or by other provisions of the Contract Documents.

B.	Materials, equipment and workmanship shall carry the standard warranty against defects in material and workmanship.  Failure which may develop due to defective or improper material, equipment, workmanship or design shall be made good, forthwith, by and at the expense of the Contractor, including damage done to areas, materials and other systems resulting from this failure.

C.	Guarantee that all elements of the systems are of sufficient capacity to meet the specified performance requirements as set forth in Contract Documents.

D.	Upon receipt of notice from RE of a failure of system(s) or component(s) during the guarantee period, replace affected components within reasonable time period at no additional cost.

E.	Guarantee period shall extend for one year from Date of Substantial Completion.

F.	Before final request for payment, furnish written guarantee covering above requirements.

# PART 2	PRODUCTS

2.1		GENERAL PRODUCT REQUIREMENTS

A.	Products shall be undamaged and unused at time of installation and shall be complete with accessories, trim, finish, safety guards and other devices and details needed for complete installation and for intended use.

B.	Where available, products shall be standard products of types which have been produced and used previously and successfully on other projects and in similar applications.

C.	Labels and stamps which are required for observation after installation shall be located on accessible surfaces which, in occupied spaces, are NOT conspicuous.  Other labels and stamps shall be located on concealed surfaces.

# PART 3	EXECUTION

3.1	.	ARRANGEMENT OF WORK

A.	Consult Architectural Contract Drawings and Details for proposed locations of fixtures and equipment.  If proposed location is not given, obtain information from RE.  Verify measurements in field.  Base measurements on established benchmarks.

B.	Install work as closely as possible to layouts shown on Contract Drawings.  Modify work as necessary to:

1.	Provide maximum possible headroom and space clearance on each side.

2.	Provide adequate clearance and ready access to all parts of the work, for inspection, operation, safe maintenance and repair, and code conformance.

3.	Coordinate and arrange work to avoid conflicts with work of other trades, to avoid unnecessary cutting and patching, and as needed for satisfactory space conditions shown on coordination drawing submittals.

4.	Where space appears inadequate, consult RE before proceeding with installation.

C.	Work shall present a neat coordinated appearance.

3.2		COORDINATION

A.	Examine Contract Documents and coordinate with Contractor and other trades as necessary to facilitate the progress of the work.

B.	Each trade shall keep Contractor and other trades fully informed as to shape, size, and locations of openings, chases, equipment, panels, access doors, sleeves, inserts and anchor bolts required; whether temporary or permanent.  Coordinate sizes, depths, fill and bedding requirements with excavation trades.  Give sufficient advance notice so that coordination may be completed in advance.  If information is not furnished in proper and timely fashion, the trade involved shall do own cutting and patching or have same done by Contractor, without additional cost to FAA.

C.	Particular emphasis is placed on timely installation of major apparatus and furnishing of other trades and Contractor with relevant information.

D.	Do NOT install a system until critical components of system and related systems have been coordinated and applicable shop drawings have been accepted.

3.3		WORKMANSHIP

A.	Work covered under this Division shall be constructed and finished in every respect in a workmanlike and substantial manner.

B.	Equipment and materials shall be new, of first quality, selected and arranged to fit properly into spaces indicated.

C.	Obtain detailed information from manufacturer as to proper methods for installation and connections.  This includes such tests as equipment manufacturer recommends.  Where documentation regarding installation is NOT obtainable, work shall be installed in accordance with best trade practice.

1.	Unless specifically indicated otherwise on Contract Documents, equipment and materials shall be installed in accordance with manufacturer’s recommendations.

2.	Notify RE of conflicts between manufacturer’s recommendations and Contract Documents requirements, and request clarification before proceeding with installation.

D.	Where equipment, piping, ductwork, conduit, etc. is exposed, color of finish or paint shall be as selected by RE.

3.4		OPERATION OF SERVICES AND UTILITIES

A.	During the construction period and until finally inspected, tested and accepted, maintain new services and utilities.

B.	Shutdown of existing services and utilities shall, without exception, be coordinated with the proper utility and with the RE as to date, time of day, and duration.

1.	Notify RE of estimated duration of  shutdown period at least ten days in advance of date when shutdown is proposed.  Approval of shutdown shall be obtained from proper utility and RE, before any service is interrupted.

2.	Work during shutdown period shall be arranged for continuous performance, including overtime if required, to ensure that existing operating services will be shut down only for time actually necessary to complete connections.

3.5		PROTECTION

A.	Contractor shall be responsible for work and equipment until fully inspected, tested and accepted.  Carefully store materials and equipment which are not immediately installed after delivery to site.  Close open ends of work with temporary covers or plugs during construction to prevent entry of obstructing material or damaging water.

B.	Protect work and material of other trades from damage that might be caused by electrical work and make good damage thus caused.

## 3.6	IDENTIFICATION

A.	Basic materials such as piping, tubing, sheet metal, insulation, etc., shall have following information clearly printed on the material:  manufacturer’s name, material grade, gauge, thickness, type, and data to identify required methods of attachment; as applicable.  Unmarked material shall NOT be used.

B.	Permanent nameplates shall be provided on each piece of service-connected or power-operated equipment, on easily accessible surface.  Nameplate shall include product name, model number, serial number, capacity, speed, ratings, and similar essential operating data.

1.	Manufacturer’s nameplate, name, trademark and address shall be attached permanently to equipment and material furnished.  Nameplate showing only distributor or Contractor will NOT be permitted.

2.	Unless otherwise specified or requested, letters and numbers shall be ½- inch high.

3.	Attach nameplates with screws or rivets.  Wherever covers of adjacent units are interchangeable, attach nameplates to wall or backboard rather than covers.

C.	Identification labels shall be provided to number equipment according to designations used in Contract Documents.  Label shall be plastic nameplate with letters and numbers 1-1/2-inches high.  Furnish directory indicating number, location and use of each item.  After finish painting is completed, apply identification label where it will be readily visible from normal operating position on floor.

3.7		LUBRICATION

A.	Equipment shall be furnished and installed so that lubrication points are conveniently and readily accessible for maintenance.  Make these provisions by whatever means is appropriate:  extended fittings, access doors, equipment location, etc.

B.	No equipment shall be operated for temporary service or for testing purposes without proper lubrication.  Items requiring lubrication shall be left freshly and fully lubricated at time of substantial completion.

C.	Prior to substantial completion, deliver to RE, along with itemized list:  one complete new set of special lubrication devices required for servicing, such as grease guns, fittings and adapters.

3.8		ATTACHMENT OF SUPPORTS TO STRUCTURES

A.	Equipment shall be securely attached to building or manhole structure in acceptable manner.  Attachments shall be of strong and durable nature.

B.	Attachment of supports to roof decking is NOT permitted.  Pipes, ducts, boxes, etc. must be supported from bar joists or steel construction or additional members spanning roof steel as determined by structural engineer.

3.9		TESTS

A.	Make final adjustments to equipment before testing.  Manufacturer’s authorized representative shall verify proper installation and adjustment prior to startup of major equipment; refer to paragraph 1.11.A.9.

B.	Furnish labor, materials, instruments, supplies and services necessary for testing required under this Division.  Correct defects appearing during tests, and repeat tests until no defects are disclosed.  Final tests shall be made in RE’s presence.

C.	Use true RMS ammeter to measure current, for equipment that may have harmonic (non-linear) load component.

D.	Notify RE of testing schedule at least 48 hours in advance of tests.

E.	Perform specified tests and tests required by legal authorities and by agencies having jurisdiction over this Work.  Tests shall be performed to the satisfaction of legal authorities, agencies having jurisdiction, and RE.

F.	Each piece of equipment, including motors and controls, shall be operated continuously for minimum test period of one hour.

G.	If manufacturer’s startup services are specified under other Sections in this Division, furnish services of factory-trained service engineering representative to provide following.  If manufacturer's startup services are not required, Contractor shall furnish following services.

1.	Inspection of equipment/system installation.

2.	Assistance in initial startup and adjustment of equipment; including necessary time to achieve proper installation and adjustments.

3.	Instruction of FAA’s staff; see paragraph 3.10, Instructions.

H.	Upon completion of tests, demonstrate the following:

1.	Equipment and systems are installed and operating in accordance with manufacturer’s specifications and instructions and with Contract Documents.

2.	Proper adjustment of equipment and systems.

3.	Systems are properly cleaned and free of contaminants.

4.	Systems are properly phase balanced.

5.	Circuits and motorized equipment are equipped with proper overload protection and are not operating under overload.

6.	Instruments are recording properly.

3.10	INSTRUCTIONS

A.	Arrange for each installer of work requiring continuing maintenance or operation, to meet with FAA’s personnel at project site and instruct them in the operation and maintenance.   Include instruction by manufacturer’s representatives where installers are not expert in the required procedures.  Instruction periods for all trades shall be minimum of 8 hours total; refer to individual SECTIONS for further requirements.

B.	Instruction shall include review of maintenance manuals, record documentation, tools, spare parts and materials, lubricants, fuels, identification system, control sequences, hazards, cleaning and similar procedures and facilities.

C.	Start-up, shut down, emergency operations, noise and vibration adjustment, safety, economy/efficiency adjustments, and similar operations shall be demonstrated.

D.	Applicable warranties shall be reviewed.

E.	Procedures for routine maintenance shall be demonstrated at the equipment involved, to ensure accessibility to components involved.

## 3.11	QUIET OPERATION

A.	Unless shown otherwise, equipment and material provided as part of the Work shall NOT produce sound level greater than 55 decibels (or level required by Code, if more stringent) in adjacent occupied areas.  Sound level shall be as measured on A-weighting scale of sound level meter or sound survey meter.

B.	Methods described in ASHRAE guide and data books may be used to determine sound level of equipment when total of background sound and equipment sound exceeds the required minimum.

C.	Contractor shall ensure that equipment and materials provided as part of the Work do NOT produce excessive noise/vibration and do NOT transmit excessive noise/vibration to occupied spaces.  If objectionable noise/vibration occurs, Contractor shall provide systems, devices, and equipment necessary to eliminate objectionable noise/vibration at no additional cost to FAA.

## 3.12	FINAL CLEANING

A.	Clean each surface of each unit of work, to normal “clean” condition expected for a first-class building cleaning and maintenance program.  Comply with manufacturer’s instructions for cleaning operations.  The following are examples, but not limitations, of cleaning required:

1.	Remove labels which are not required as permanent labels.

2.	Clean transparent materials, removing substances which are noticeable as vision-obscuring.

3.	Clean exposed hard-surfaced finishes, until free of dust, stains, films and similar noticeable substances.

4.	Wipe surfaces of mechanical and electrical equipment clean, remove excess lubrication and other substances.

5.	Remove debris and surface dust from limited-access spaces such as plenums, shafts, and ceiling spaces.

6.	Clean lighting fixtures and lamps; removing dust, smudge marks and protective wraps; so as to function with full efficiency.

END OF SECTION

SECTION 16011

ELECTRICAL GENERAL REQUIREMENTS

PART 1	GENERAL

1.1	APPLICABLE PUBLICATIONS

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

FEDERAL SPECIFICATION (FED. SPEC.)

L-P-387A & Int Am 2 	Plastic Sheet, Laminated, Thermosetting (for Design Plates)

AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI)

C501- 1 & C52.1	Selection Installation and Use of Electric Motors

NATIONAL ELECTRICAL MANUFACTURERS ASSOCIATION (NEMA)

ICS 6-93 (R83) 	Enclosures for Industrial Controls and Systems

ICS 2-322	MCC Wiring Class and Type

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

70B-94 	Electrical Equipment Maintenance; and

70- 99	National Electrical Code

1.2	APPLICATION

This section applies to all sections of Division 16, “Electrical,” of this project except as specified otherwise in each individual section.

1.3	SUBMITTALS

The following shall be submitted in accordance with Section 01330, “Submittal Procedures”.

1.3.1	SD-02, Manufacturer’s Data

Submittals for each manufactured item shall be current manufacturer’s descriptive literature of cataloged products, equipment drawings, diagrams, performance and characteristic curves, and catalog cuts.

1.3.2	SD-04 Shop Drawings

In addition to the requirements of the Contract Clauses, shop drawings shall meet the following requirements.  Drawings shall be a minimum of 8.5 inches by 11 inches in size, except as specified otherwise.  Drawings shall include and installation details of equipment indicating proposed location, layout and arrangement, accessories, piping, ductwork, and other items that must be shown to assure a coordinated installation.  Drawings shall indicate adequate clearance for operation, maintenance, and replacement of operating equipment devices.  If equipment is disapproved, revise drawings to show acceptable equipment and resubmit.

1.3.3	SD-13 Certificates

a.	Certificates of Compliance

Submit manufacturer’s certifications as required on products, materials, finish, and equipment indicated in the technical sections.  Certifications shall be documents prepared specifically for this contract.  Preprinted certifications and copies of previously submitted documents will not be acceptable.  The manufacturer’s certifications shall name the appropriate products, equipment, or materials and the publication specified as controlling the quality of that item.  Certification shall not contain statements to imply that the item does not meet requirements specified, such as “as good as”; “achieve the same end use and results as materials formulated in accordance with the referenced publications”; or “equal or exceed the service and performance of the specified material.”  Certifications shall simply state that the item conforms to the requirements specified.  Certificates shall be printed on the manufacturer’s letterhead and shall be signed by the manufacturer’s official authorized to sign certificates of compliance.

b.	Publication Compliance

Where equipment or materials are specified to conform to industry and technical society publications of organizations such as American National Standards Institute (ANSI), American Society for Testing and Materials (ASTM), and Underwriters Laboratories Inc. (UL), submit proof of such compliance.  The label or listing by the specified organization will be acceptable evidence of compliance.  In each of the publications referred to herein, consider the advisory provisions to be mandatory, as though the word “shall” had been substituted for “should” wherever it appears.  Interpret references in these publications to the “authority having jurisdiction,” or words of similar meaning, to mean the Contracting Officer’s Technical Representative (COTR).  In lieu of the label or listing, submit a certificate from an approved independent testing organization, adequately equipped and competent to perform such services, stating that the item has been tested in accordance with the specified organization’s test methods and that the item conforms to the specified organization's publication.

1.3.4	SD-19, Addenda to Operation and Maintenance Manuals

The Contractor shall submit operation and maintenance data.  This data will be included as an addenda to the current Operation and Maintenance (O&M) manual for the existing ground water treatment system at Areas B, 41, D, and E at the FAA facility.  The instructions shall include the manufacturer’s name, model number, number, service manual, parts list, and brief description of all equipment and their basic operating features. Six complete copies of maintenance instructions listing routine maintenance procedures, possible breakdowns and repairs, and trouble-shooting guides.  The instructions shall include as-built drawings of the piping layout, as installed.  Include in the manual the names, addresses, and telephone numbers of each subcontractor installing the system or equipment and the local representatives for the system or equipment.  The manual shall include:

a.	Internal and interconnecting wiring and control diagrams with data to explain detailed operation and control of the system or equipment.

b.	Description of the function of each principal item of equipment.

c.	Installation and maintenance instructions.

d.	Safety precautions.

e	Diagrams and illustrations.

f.	Testing methods.

g.	Performance data.

h.	Parts list.  The list shall indicate sources of supply, recommended spare parts, and name of servicing organization.

i.	Appendix:  List qualified permanent servicing organizations for support of the equipment, including addresses and certified qualifications.

1.4	INSTRUCTION TO GOVERNMENT PERSONNEL

Where indicated in the technical sections, furnish the services of competent instructors to give full instruction to Government personnel in the adjustment, operation, and maintenance of systems and equipment, including pertinent safety requirements as required.  Each instructor shall be thoroughly familiar with all parts of the installation and shall be trained in operating theory as well as practical operation and maintenance work.  Instruction shall be given during the first regular work week after the equipment or system has been accepted and turned over to the Government for regular operation.  The number of man-days (8 hours) of instruction furnished shall be as specified in each individual section.

1.5	DELIVERY AND STORAGE

Handle, store, and protect equipment and materials in accordance with the manufacturer’s recommendations and with the requirements of NFPA 70B, Appendix I, titled “Equipment Storage and Maintenance During Construction.”  Replace damaged or defective items with new items.

1.6	CATALOGED PRODUCTS/SERVICE AVAILABILITY

Materials and equipment shall be current products by manufacturers regularly engaged in the production of such products.  Products shall have been in satisfactory commercial or industrial use for 2 years prior to bid opening.  The 2-year period shall include applications of equipment and materials under similar circumstances and of similar size.  The 2-year period shall be satisfactorily completed by a product for sale on the commercial market through advertisements, manufacturers’ catalogs, or brochures.  Products having less than a 2-year field service record will be acceptable if a certified record of satisfactory field operation for not less than 6000 hours, exclusive of the manufacturers’ factory or laboratory tests, is furnished.  The equipment items shall be supported by service organizations which are reasonably convenient to the equipment installation in order to render satisfactory service to the equipment on a regular and emergency basis during the warranty period of the contract.

1.7	MANUFACTURER'S RECOMMENDATIONS

Where installation procedures or any part thereof are required to be in accordance with manufacturer’s recommendations, furnish printed copies of the recommendations prior to installation.  Installation of the item shall not proceed until recommendations are received. Failure to furnish recommendations shall be cause for rejection of the equipment or material.

PART 2	PRODUCTS

Not Used

PART 3	EXECUTION

Not Used

SECTION 16050

BASIC MATERIALS & METHODS - ELECTRICAL

PART 1	GENERAL

This Section covers the specification of basic materials and methods for electrical work.

## 1.1	SCOPE

A.	Provide labor, materials, services, equipment and transportation necessary for complete and operational electrical systems as indicated on Contract Drawings and specified herein, including but not limited to following:

1.	Complete secondary distribution system, including:

- Panel boards and motor control centers

- Conduits, wires and cables

- Feeders and branch circuits

- Switches, boxes and motors

- Power and control wiring

- Wiring devices

- Variable Frequency Drives

- Control Panels

2.	Disconnects, controls and starters not integral with or specialized for mechanical equipment provided under DIVISION 11, EQUIPMENT or DIVISION 15, MECHANICAL.

3.	Installation of, and power wiring to and from:  disconnects, controls and starters furnished under DIVISION 11, EQUIPMENT or DIVISION 15, MECHANICAL.

5.	Hangers and supports

6.	System identification

7.	Record drawings

8.	Operating and maintenance manuals

1.2.	STANDARDS

A.	All work of this Division shall conform to following standards:

1.	IES:  Lighting Handbook.

2.	NEMA Standards.

3.	ANSI Standard CI:  National Electrical Code (NFPA 70).

4.	ANSI Standard C50:  Rotating Electrical Machinery.

5.	ANSI Standard C501-1:  Construction and guide for selection, installation and use of electric motors.

6.	ANSI Standard C52.1:  Motors and generators (NEMA MG1).

7.	ADA: Americans With Disabilities Act

8.	IEEE: Standards 81, C62.41, C57.105 and C37.13.

9.	GSA: US General Services Administration Standards

  - SUBMITTALS

The following shall be submitted in accordance with Section 01330, “Submittal Procedures”.

    - SD-01 Data; GA

Submit manufacturer’s published data indicating complete compliance with all referenced standards, these Technical Specifications and the Contract Drawings.  Submit data for all items listed under Article 1.3.3 below.

The label or listing of the Underwriters Laboratories (UL), Inc., shall be accepted as evidence that the materials or equipment conform to the UL agency standards.  In lieu of this label or listing, a statement for a nationally recognized, adequately equipped testing agency indicating that the items have been tested in accordance with required procedures and that the materials and equipment comply with all contract requirements will be accepted.  However, materials and equipment installed in hazardous locations must bear the UL label unless the data submitted from other testing agency is specifically approved by the Resident Engineer (RE).

    - SD-04 Drawings; GA

Detail drawings for all material and equipment specified.  Drawings shall show applicable schematic diagrams; equipment layout and anchorage; and conduit and cable tray runs, anchorage, and support.  Telephone system drawings showing actual layout, including locations, type and gauge of cables, and terminal assignment of wiring.

    - SD-07 Schedules; GA

The electrical component schedule shall consist of a complete list of equipment and materials to be used on the project including but not limited to: cables, wiring, messenger wires and clamps, conduit, wire-ways, cables, raceways, cable ladders, pull boxes, junction boxes, hangers and supports, switches, handholes, utility poles, electrical boxes, and electrical cabinets.

    - SD-09 Reports; GA

Submit Reports for testing conducted in accordance with articles 3.13, 3.14, 3.15, and 3.16.

    - SD-06 Instructions; GA

Include any special installation instruction that may be required for a specific component.

  - UNDERWRITERS LABORATORIES LABELS

A.	Equipment, materials and components, for which there are listings in UL Product Directories, shall bear UL labels.

## 1.5	GENERAL

A.	The installation shall conform to the requirements of NFPA 70 and NFPA 101, unless more stringent requirements are indicated herein or shown.

B.	The drawings indicate the extent and the general location and arrangement of equipment, conduit, and wiring. The Contractor shall become familiar with all details of the work and verify all dimensions in the field so that the equipment shall be properly located and readily accessible.  Equipment and materials shall be located to avoid interference with mechanical or structural features.  Components shall not be supported from sheet metal roof decks. If any conflicts occur necessitating departures from the drawings, details of and reasons for departures shall be submitted and approved prior to implementing any change. The Electrical Contractor shall coordinate the electrical work with the electrical drawings and provide all power related wiring even if they are not shown on electrical drawings.

# PART 2	PRODUCTS

## 2.1	CONDUIT, CABLE AND FITTINGS

A.	Rigid metallic conduit (RMC) shall be UL listed, hot dipped galvanized steel with full cut hot dipped galvanized NPT threads.  RMC shall be chromated on all surfaces for corrosion and abrasion protection.  Connectors and couplings shall be galvanized steel threaded type listed for RMC use.

B.	Intermediate metal conduit (IMC) shall be UL listed, hot galvanized steel with full cut hot galvanized NPT threads and factory-applied interior coating or lining for ease in pulling wires.  Connectors and couplings shall be galvanized steel threaded type listed for IMC use.

C.	Electric metallic tubing (EMT) shall be UL listed, hot galvanized steel with factory-applied interior coating or lining for ease in pulling wires.  Connectors and couplings shall be galvanized steel, either compression type or heavy-duty set screw-type, listed for EMT use.  Indent or crimp-type connectors are NOT allowed.

D.	Flexible metal conduit (FMC) shall be UL listed, single strip, spirally wound, corrosion-resistant, galvanized steel acceptable equivalent to Liquatite “Type BR”.  Use galvanized steel fittings and clamps listed for FMC use.

E.	Wireways shall be steel, UL listed, with hinged or screwed covers by Lee Products, Keystone or acceptable equivalent.

F.	Surface raceways shall be UL labeled, steel with standard buff finish, acceptable equivalent to Wiremold.  Sizes and types shall be as shown on Contract Drawings or as required by RE.

G.	Type MC cable shall be UL listed, 600 V, 90 deg. C rated, flexible metal encased multi-conductor assembly; with cable sheath of interlocked galvanized steel strip, copper conductors with Code gauge THHN insulation, and internal green insulated ground:  acceptable equivalent to AFC ‘Type MC”.  Connectors and fittings shall be galvanized steel, listed for MC cable use.

H.	Non-metallic conduit (NMC) shall be rigid PVC, heavy-wall Schedule 40, UL rated, acceptable equivalent to Carlon “Type 40”.

I.	Cable Ladder

1.	Cable tray support system shall be minimum 12-inches wide aluminum type, with rungs on 6-inch centers, minimum load depth of 3-inches and supports at 10-feet maximum intervals; meeting NEMA Standard VE-1-1991.  Tray shall be by Cope, Mono Systems, Chalfant, B-Line, or acceptable equivalent.

2.	Provide necessary hangers, fittings and supports to complete system.

- Cable tray shall be center support type.

# J.  Cable Tray

1.	Provide continuous, rigid, welded steel mesh cable tray system as manufactured by Cablofil:  EZ Tray system.  Tray shall be welded at all intersections and shall have continuous safety edge T-welded wire lip.

2.  	Provide straight sections 2 inches deep by 12 inches wide.

3.  	Tray material shall be carbon steel wire, ASTM A510, Grade 1008.  Wire shall be welded, bent and surface treated after manufacture.   Wire shall be electro-plated zinc galvanized after welding and bending of mesh.

4.  	Provide FAS support system, hardware and accessories as manufactured by Cablofil.

K.	Minimum Sizes shall be as follows:

1.	Conduit and EMT:  ¾-inch unless otherwise noted.

2.	Flexible metal conduit:  ½-inch.

3.	Wireway:  4-inches x 4-inches.

4.	Cable tray:  12-inches.

L.	Special Fittings

1.	Where conduit is installed in hazardous (classified) locations:  provide sealing fittings acceptable equivalent to Crouse-Hinds “EYS Series”.

2.	Where conduit penetrates waterproof foundation, floor or roof:  provide through-wall seals acceptable equivalent to O.Z./Gedney “Type CSMI” on each side of existing walls and O.Z./Gedney “Type FSK” on new walls.

3.	Where conduit from underground distribution system enters building, provide cable terminators acceptable equivalent to O.Z./Gedney “Type CR”.  Fill the compound chamber with insulating compound acceptable equivalent to O.Z./Gedney “Dozseal #220”.

M.	Applications shall be as follows:

1.	RMC:  underground or below grade, buried in or below floor slabs, in concrete walls, concealed in exterior masonry walls, wiring in fire pump rooms.

2	IMC:  as specified for rigid conduit, except not in hazardous locations, fire pump rooms or applications over 600 V.

3.	EMT:  unless otherwise noted:

- Feeders

- Power wiring in mechanical rooms

- Wiring for fire alarm systems

- Wiring for emergency and exit lighting

- Wiring for emergency communication, security and alarm systems

- Branch circuits

- Control wiring, including work done under Division 15 and/or 16

- Wiring above non-accessible ceilings

- Light fixture branch wiring

4.	FMC:  final connections to motors and equipment-mounted controls from a minimum of 18 inches to maximum of 6 feet in length.

5.	NMC: underground duct bank concrete encased, sleeves and elsewhere where designated.

6.	Wiremold, cable tray:  as shown on Contract Drawings.

7.	In any case not specifically covered, rigid conduit shall be used unless otherwise approved by RE.

8	EMT is NOT permitted as a substitute for rigid conduit; MC cable is NOT permitted as a substitute for flexible metal conduit.

9	AC (BX) cable shall NOT be used.

## 2.2	PULL BOXES AND JUNCTION BOXES

A.	Boxes shall be heavy, stamped steel with covers attached by screws.  Provide locknuts for conduit size to which boxes are connected. In finished areas, boxes shall have neatly mitered frame and flush steel cover screwed to the frame.

B.	Boxes shall be sized according to NEC.

C.	Boxes shall be flush mounted where installed with concealed conduit, and surface mounted elsewhere.

## 2.3	BACKBOARDS & EQUIPMENT CABINETS

A.	Backboards shall be ¾-inch plywood painted on all sides before installation.  Paint shall be one coat primer and two coats latex fire-retardant gray paint equivalent to Benjamin-Moore “Retardo 220”.  Backboards shall be used for mounting grouped switches, starters and other equipment where shown on Contract Drawings.

B.	Telephone and equipment cabinets shall be UL listed, sheet steel cabinet with hinged door with catch and lock; mounted on backboard.  Cabinets shall be flush or surface-mounted, sized as shown on Contract Drawings.

## 2.4	CONDUIT HANGERS AND SUPPORTS

A.	Hangers, clips and accessories supporting conduit shall be UL listed.

B.	Individual large conduits shall be supported by means of adjustable, malleable hangers of acceptable design placed on maximum 8-foot centers.  Individual small conduits may be held in place by one hole malleable clips.

C.	MC cable shall be supported by hangers of acceptable design placed on maximum 4-foot centers.  MC cable shall be supported within 12 inches of each fitting.

## 2.5	WIRES AND CABLES

A.	Secondary conductors shall be new copper with 600 V code gauge insulation, conforming to NEC requirements, and shall be Type THWN or THHN, except as follows:

1.	Type XF or SFF 150 deg C shall be used for fixture wiring.

2.	Type XHHW shall be used for conductors #3 AWG and larger.

3.	Type TFE shall be used for high temperature applications.

B.	When wire sizes are not shown on Contract Drawings, sizes shall be in accordance with NEC but no smaller than following:

1.	Light and power wiring:  #12 AWG.

2.	Control wiring:  #14 AWG.

3.	Wiring and cable for alarm and signal systems:  as recommended by equipment manufacturer.

C.	All multi-purpose feeders and circuits shall include a full size neutral and separate insulated ground conductor.

1.	All 277/120 VAC circuits shall include separate full sized neutral and insulated ground conductors.  Shared neutrals or ground conductors are not permitted.

## 2.6	SPLICES

- Splices for #10 or smaller wires shall be made with UL approved solderless connectors:  spring type acceptable equivalent to Minnesota Mining and Manufacturing Company “Scotchlock’; or crimp-type acceptable equivalent to Thomas & Betts “Sta-Kon”.

- Splices, cable taps and terminals for #8 and larger shall be made with UL approved compression connectors:  compression taps acceptable equivalent to Thomas & Betts “Colored Keyed” “C” taps applied with special tools according to manufacturer’s recommendations; or bolted pressure connectors, bronze or copper construction, by Thomas & Betts, Burndy or acceptable equivalent.

- Splices for M.I. cable shall comply with the manufacturer’s recommendations.

## 2.7	MANUAL TIME SWITCHES

Not used.

## 2.8	SOLID STATE, DIGITAL TIME SWITCHES

Not used.

## 2.9	SAFETY SWITCHES AND FUSES

A.	Work of this Division shall include:

1.	Furnishing and installing an appropriate safety switch for each motor, unless otherwise noted.

2.	Installation of safety switches furnished under DIVISION 15, MECHANICAL.

3.	Fuses for safety switches.

4.	Power wiring to and from safety switches.

B.	Disconnect Switches for Motor Starters

1.	Provide disconnect switch ahead of each magnetic motor starter.  The disconnect switch shall be located in the MCC and receive direction from the PLC.

2.	Where more than one motor is connected to single branch feeder, provide fused disconnect switch for each motor, even if within sight of feeder branch breaker.

3.	Supply each motor with an additional disconnecting means using a fused switch, as close as possible to the motor.

C.	Unless otherwise noted, switches shall have rejection clips for RK fuses where applicable and NEMA 1 enclosure.  Safety switches shall be NEMA Type HD (heavy-duty), manufacturer’s specification grade switches by Square D, General Electric, or Westinghouse, acceptable equivalent to following:

1.	Switches for use on 120/208 V system: rated for 240 V.

2.	Switches for use on 480 V system:  rated for 600 V.

3.	Fused disconnect 2-pole and 3-pole:  Square D “Type H”.

4.	Switches that are used in conjunction with variable frequency drives (VFDs) and elevators shall have auxiliary contacts that open before switch blades to interrupt control circuits.  Auxiliary contacts shall be 120 VAC; 5 Ampere rated.

5.	Switches for use with 6 lead motors: 600 VAC, NEMA 4X enclosure.

a.	Fused: Square D “Type H”

D.	Fuses for safety switches shall be non-renewable dual element cartridge type, Class RK5, UL listed.  Fuses shall be Bussmann #FRN for 208 V usage, and Bussmann #FRS for 460 V usage; or acceptable equivalent by Shawmut or Littelfuse.  Install fuse so that size is readily visible.  Special types and classes are indicated on Contract Drawings.

E.	Provide one spare set of fuses for each type and size used with switches and other equipment.

## 2.10	MOTOR STARTERS

A.	Unless otherwise noted, provide an appropriate motor starter for each motor.  Installation of, and power wiring to and from, the starters furnished under Division 11, Equipment or Division 15, “Mechanical”, shall be done as part of the work of this Division.  Unless otherwise noted, control wiring shall be provided as specified under Section 16901.

B.	Motor starters shall meet NEC, NEMA, UL, CSA and ANSI and shall be suitable for required load, duty, voltage, phase, frequency, service and location.

C.	Starters shall be by Allen-Bradley, Cutler-Hammer/Westinghouse, Square D, General Electric, or acceptable equivalent to following:

1.	Manual motor starters for 115 V or 200 V, single-phase motors less than 2 HP:  Square D “Class 2510” #FG-1P or #FG-2P.

2.	Manual motor starters for three-phase motors:  Square D “Class 2510”.

3.	Magnetic across-the-line starters, for single-phase motors 2 HP and larger and for three-phase motors:  Square D “Class 8536”.

4.	Combination motor starters, with fused disconnect switch (fuse class RK-5):  Square D “Class 8538”.

5.	Combination motor starters, with thermal-magnetic circuit breaker (with interrupting rating as specified elsewhere):  Square D “Class 8539”.

6.	Reduced Voltage starters, solid state (Electronic):  Square D “Class 8660”.

7.	Combination motor starters with fused disconnect switch (fuse class RK-5) or with thermal-magnetic circuit breakers; for two-speed, two winding motors:  Square D “Class 8810”.

D.	For 208V systems, provide 120 V control power by tapping one power phase leg with single-pole fuse in fuse clip and running one #12 AWG neutral to starter.

E.	For 208V or 277/480 VAC systems, provide integral 120 VAC fused control power transformer in each starter, unless otherwise noted.

F.	Unless otherwise noted, motor starter shall have NEMA 1 enclosure.

G.	Magnetic starters shall have the following features:

1.	Two extra N.O. and two extra N.C. auxiliary contacts, for each speed.

2.  “HAND-OFF-AUTOMATIC” switches mounted in cover.

3.	Red “ON” pilot light equipped with neon lamp and mounted in starter cover.

4.	Red and yellow “ON” pilot lights for high and low speeds, on two-speed motors.

5.	Terminal strip for field wiring connections to control circuits.

6.	Cover-mounted reset button.

7.	Three thermal overload relays, with appropriate heaters to provide protection on all motor phase legs.  Relays shall be bimetallic or melting alloy type.

8.	High-Low selector switch that is functional only in “HAND” position on two-speed motors.

9.	Reverse phase and phase failure relay, for motors 100 HP and larger.

10.	Other features specified in motor starter schedule.

H.	For control of HVAC starters, refer to Division 15, Mechanical.

## 2.11	TERMINAL STRIPS

A.	Terminal strips shall be Buchanan or acceptable equivalent, with a numbering strip for identification of individual punchings.

# PART 3	EXECUTION

3.1	SUPERVISION

A.	Furnish services of experienced electrical Superintendent who shall be constantly in charge of electrical work, together with skilled laborers required to unload, transfer, erect, connect, adjust, start, operate and test each system.

B.	Particular emphasis is placed on timely installation of major apparatus and furnishing of other trades and Contractor with relevant information.

## 3.2	MOTOR AND CONTROL CIRCUIT WIRING

A.	Provide wiring required for electrical equipment furnished under other Divisions of this Specification.  Provide disconnects, starting switches and motor protection ahead of each piece of equipment, unless specified otherwise.

B.	Check all protective and control equipment furnished or installed under this Division.  Ensure that such equipment is properly sized for motor or other electrical equipment that it serves.  Replace any material or equipment damaged due to improperly-sized protective control mechanisms.

C.	Electrical controls and starters integral with or specialized for mechanical equipment are specified with equipment in Division 11, Equipment or Division 15, Mechanical.  Disconnects and other controls and starters are specified in this Division.

D.	Output power wiring from variable frequency drive (VFD) to motor shall be run in metallic conduit; other wiring shall NOT be run in this conduit.  VFD shall have separate equipment conductor back to ground bus of source panel or switchboard and shall NOT depend on metallic conduit for grounding.  Power shall NOT be applied to VFD until VFD manufacturer has checked and approved VFD installation.

E.	Control cable to VFD speed input shall be shielded and shall be installed without excess cable so that electrical noise shall be minimized.

## 3.3	IDENTIFICATION

A.	Distribution Equipment

1.	All distribution equipment and associated electrical elements of mechanical equipment shall be identified according to the designations used in the Contract Documents or established in cooperation with the RE as part of the as-built record drawings.  Furnish directory indicating number, location and use of each item.  Equipment requiring such numbering includes, but is not limited to the following:

- High voltage switches and equipment

- Substations

- Switchboards/switchgear

- Switchboard/switchgear individual overcurrent protection devices

- Motor control centers

- Motor control center individual motor starter devices

- Overcurrent protection device enclosures

- Disconnect switches

- Panelboards

- Transformers

- Equipment control panels and enclosures

2.	Nameplates/Labeling:  Center on device, coverplate or enclosure. Place on non-removable surface.

a.	Use abbreviations defined in the contract documents whenever possible.  Use plan designations for labeling, unless indicated otherwise.  Indicate loads served using designating from electrical schedules and designations from the trade furnishing the equipment served.

b.	Label the panel boards with engraved lamicoid nameplates.

c.	Install nameplates inside covers in finished areas and outside covers in unfinished areas including mechanical, electrical and building maintenance areas.

3.	Manufacturer’s nameplate, name, trademark and address shall be attached permanently to equipment and material furnished under this division.  Nameplate showing distributor or contractor will not be permitted.

4.	Equipment designation nameplates shall be engraved lamicoid, sized as follows:

a.	Nameplates on panelboards, distribution panels and service switches:  minimum of 1-1/2-inches by 2-1/2-inches size with name letters not less than ½-inche high and voltage, phase and number of wires not less than ¼-inch high.

b.	Nameplates on starters and other equipment switches and devices: minimum of ¾-inch by 2-1/2-inches size with letters not less than 3/8" high.

5.	Attach nameplates with rivets.  Wherever covers of adjacent units are interchangeable, attach additional nameplates to wall or backboard adjacent to covers.

6.	Panelboard circuit identification:  engraved plastic nameplates for units without panel cover doors, or plastic covered circuit directory cards, type written, mounted on the inside of  the panel cover doors.

- Acceptable manufacturers for nameplates are Lamicoid, Seton, Brady or approved equivalent.

B.	Distribution Raceway Systems

1.	Distribution raceway systems shall require system identification and shall include, but is not limited to the following:

a.	Conduit systems

b.	Pull boxes and junction boxes

2.	Marker pen labeling shall be utilized on conduit and cable system junction boxes.  Marker pen labeling methods shall be submitted for review prior to execution.  Spray painting shall not be permitted.  Systems requiring such identification include and shall be limited to the following:

a.	Junction boxes or portions of junction boxes containing 277/480 volt or 120/208 volt wiring.

b.	Communication and special system pull and junction boxes

c.	Pull boxes and junction boxes installed for future use.

3.	Marker pen labeling shall be on outside of junction and pull box coverplates and on the box itself in unfinished areas including mechanical, electrical and building maintenance areas and inside covers in finished areas.

4.	Marking pen where used shall be permanent, waterproof and quick drying.

5.	Conduits that contain essential power system feeders and branch circuits shall be identified by attaching red vinyl adhesive backed decal with ½-inch high black letters on 1" high labels identifying essential power within 1 foot of each termination or pull box and a minimum of every 25 feet of conduit run.  Referenced labels shall be by Seton or approved equivalent.

6.	Acceptable manufactures for underground warning tape, identification decals and vinyl adhesive backed labels are Seton or Brady.

7.	Fire alarm system, junction boxes and recovery couplings shall be painted red.  Provide vinyl label indicating fire alarm every 25 feet and at terminations.

C.	Conductor and Cabling Systems

1.	480V wiring identification:  480V wiring (including switchboard wiring) shall have orange adhesive tape strips with continuous preprinted legend “480 volts” affixed near terminations and in pull boxes and wireways.  Acceptable manufactures:  preprinted tape shall be by Seton, Nameplates; W. H. Brady or acceptable equivalent.

2.	Label tapes:  Use for feeder, branch circuit control and special system conductors throughout.  Indicate feeder and branch circuit number son both feeders and branch circuit conductors and terminal block termination numbers for control and special system conductors.  Label conductors at origin and destination points and at all junction boxes, pull boxes and cable branch off points where installed in cable trough, wireway, monotray, cable ladder, etc.

3.	Label 5 kV and 15 kv systems similar to the above.

D.	Conductors size #6 and smaller shall have solid color insulation for identification.

E.	Conductors size #4 and larger shall have color identification, six inches minimum length near termination and in splice boxes, junction boxes, panels and manholes. Identification shall be by solid color insulation, tape or paint.

F.	Phase rotation shall be indicated by following color code:

| Phase | 5 KV and 208Y/120V | 15 KV and 480Y/277V |
| --- | --- | --- |
| A | Black | Brown |
| B | Red | Orange |
| C | Blue | Yellow |
| Neutral | White | White with color stripe, or natural gray |
| Ground | Green | Green |

G.	480 V wiring shall have orange adhesive tape strips with continuous pre-printed legend “480 Volts” affixed near terminations and in pull boxes and wireways.  Preprinted tape shall be by Seton Nameplate, W.H.Brady or acceptable equivalent.

H.	All neutral conductors shall be identified with their associated phase conductors at all boxes and panelboards as follows:

1.	Branch circuit wiring in trench headers, panelboard enclosures, termination boxes, junction boxes, pull boxes, etc., shall be bundled together into individual circuits.  Each bundled circuit shall consist of 1, 2 or 3 phase conductors and associated neutral conductor.  Branch circuit wiring shall be installed with bundled circuits identified by circuit numbers.  Bunching of individual branch circuits shall be done with nylon straps made of self-extinguishing nylon with a locking hub or head on one end and a taper on the other end.  Nylon straps shall be type Thomas and Betts “TY-RAP” or acceptable equivalent.

I.	Devices

1.	Device plates for light switches, receptacles and miscellaneous other devices connected to essential branches of the distribution system shall be stainless steel unless otherwise noted.  The required red color coding shall be integral within the device itself.

2.	Device plates for medical and housekeeping receptacles, light switches and miscellaneous other devices connected to the “normal branches” of the distribution system shall be stainless steel unless otherwise noted.

3.	Wall plates provided for flush-mounted control switches in finished areas, excluding light switches, shall be engraved, stainless steel with black-filled letters.  Device switches shall be color coded according to essential or normal power systems, as identified in other sections of this specification.

4.	Label all electrical outlets including electrical outlets furnished as an integral part of furniture and fittings with supply panel and circuit breaker designation, both on cover and tag wiring inside box.  In general identification label shall be affixed to outside of cover plate.  Label shall be engraved lamicoid

5.	Engrave nameplates of receptacles wired to GFI breakers to read “GFI” adjacent to or above receptacle opening.

6.	Engraved letter characters for device outlet labels shall be a minimum of 3/16" high.

7.	Attached device nameplates with rivets only, adhesive backed labels are not permitted.

8.	Acceptable Manufacturers:  Nameplates, wall plates and conductor tape within device back box:  Seton, Brady or approved equivalent.

9.	Low Voltage Cabling Systems Color Code

a.	Cable jacket colors and labeling for the following systems shall be the following standards:

          - Intercom - Brown

          - Fire Alarm - Red

          - Fiber Optics - Orange

          - Data cable/matching icon - Green

          - Telephone cabling - White

          - Telephone icon -Yellow

          - Main Frames  - Black or Orange

b.	Where the above systems are installed in dedicated raceways color the junction boxes and conduit couplings to match the cable jacket color.  Provide identification of system on each junction box.  In lieu of painting the conduits provide adhesive labels with 2 inch lettering every 10 feet identifying the system cabling type installed within.

3.4	ACCESSIBILITY, ACCESS PANELS AND ACCESS DOORS

A.	Locate equipment that must be serviced, including motor starters, switches, panels and junction boxes, in accessible location.

B.	Access doors shall be located to conveniently serve intended purpose and shall be installed so that adjacent piping, equipment and structures do NOT render doors unusable.

C.	Access doors are not required in removable panel ceilings if suitable identifying markers are provided to indicate access locations.

D.	During project closeout, Contractor shall perform walk-through identifying and demonstrating access to equipment for service and/or replacement.  Walk-through shall be arranged at times convenient for RE to attend.

1.	Equipment with insufficient access shall be relocated or provided with additional access panels at no additional cost to FAA.

2.	Trade responsible for access problem shall be responsible for costs of access modifications.  In general, this shall be understood to be the trade installing the equipment.  If access problem was caused by architectural layout changes which occurred subsequent to equipment installation, cost of access modifications shall be borne by trade responsible for architectural changes.

3.5	WATERPROOFING

A.	Where work pierces waterproofing, including waterproof concrete and floor of a wet area, submit method of installation for review by the RE before work is done.

B.	Provide necessary sleeves, caulking and flashing required to make openings waterproof.

## 3.6	INSTALLATION OF CONDUIT, BOXES AND FITTINGS

A.	Ends of conduits shall be reamed before assembly, and bushings and locknuts shall be provided where conduits connect to boxes.

B.	Boxes shall be set plumb and square with building lines.  Exposed conduit shall run parallel to building lines, unless noted otherwise, and shall NOT block ceiling inserts.

C.	Maintain conduit and outlet boxes in position during construction of concrete floors, masonry walls, etc.

D.	Wiring device boxes shall NOT be installed back-to-back in walls.

E.	Conduit shall run to avoid low pockets which might collect water, and, during installation, open ends shall be capped.

F.	RMC or IMC buried in grade or in ductbanks shall have couplings made up tight.  Thread to coupling joint shall be coated heavily with bitumastic paint, ensuring watertightness.

G.	Parallel groups of conduit shall be supported from below, either by horizontal angle irons or channel systems such as “Unistrut”, with vertical hanger rods at appropriate intervals.

H.	Supports for conduit on concrete walls shall be attached to wall either with all metal expansion shields or explosive-type inserts, as permitted.

I.	Conduits in slabs or in grade shall be swabbed internally prior to pulling wire or cable.

J.	Final connections to motors, control devices mounted on equipment, vibrating equipment and vibration isolated equipment shall be made through liquid-tight flexible metal conduit.

K.	Use standard radius bends on concealed conduit; on exposed work, use either standard bends or “L” type fittings acceptable equivalent to Crouse-Hinds.

L.	Wherever MC cable is used, leave sufficient slack for future removal or withdrawal of boxes or fixtures from finished ceiling or partitions.

M.	Exposed wiring shall be kept as close as possible to underside of roof and floor slabs or bottom of beams, unless noted otherwise.  Space above hung ceilings is extremely critical and coordination with mechanical trades is essential.

N.	Conduit and wiring shall NOT be run in roof fill and shall NOT pierce roof deck, unless specifically noted to on Contract Drawings.

O.	Galvanized electrical conduit of ½-inch nominal diameter may be embedded within 4-1/2-inches overall thickness suspended concrete slabs over permanent metal floor forms; galvanized electrical conduit of 1-inch nominal diameter may be embedded within slabs of 6-inches thickness overall.

P.	Conduits concealed in or beneath slab on grade:  Conduits larger than ¾-inch nominal diameter shall be completely buried below vapor barrier within the porous fill layer, such that surface of vapor barrier is smooth and level within +/- ¼-inch tolerance.  Conduits ¾-inch and smaller may be:

1.	Completely buried below the vapor barrier within the porous fill, or

2.	Placed above the vapor barrier, within the slab, at mid-height of slab, or

3.	If within the slab, spaced minimum of 3 diameters away from parallel conduits.

Q.	Field cut IMC and RMC conduits shall be field threaded.  Field threads to be cold galvanized by brush or spray.  Cold galvanize to be minimum 95% zinc and shall cure before attaching to threaded fitting.  Set screw and compression fittings shall not be acceptable.

R.	Conduit shall not be run directly above generator set exhaust system including piping, silencer, emission control equipment, heat recovery exchangers or any other equipment that contains hot exhaust gases.

## 3.7	CABLE TRAY INSTALLATION

A.	Install cable tray system at locations indicated on the drawings and in accordance with manufacturer’s instructions.

B.	Install and support cable management system in accordance with span load criteria of L/240.

C.	Cutting:

1.	Cut wires in accordance with manufacturer’s instructions.

2.	Cut wires with side action bolt cutters to ensure integrity of galvanic protective layer.

3.	Cut each wire with one clean cut to eliminate grinding or touch-up.

D.	Install cable management system using hardware, splice connectors, support components, and accessories furnished by manufacturer.

## 3.8	INSTALLATION OF CABLES

A.	Parallel groups of cables shall be supported from below, either by horizontal angle irons or channel systems such as “Unistrut”, with vertical hanger rods at maximum of three foot intervals.

B.	Supports for cables on concrete walls shall be attached to wall either with all metal expansion shields or explosive-type inserts, as permitted.

C.	Installation of M.I. cable shall follow the manufacturer’s recommendations and as follows:

1.	Examination

a.	Verify that cable and factory temporary seals have remained intact, that the insulation has not been exposed to air, and that no moisture has entered cable insulation.

b.	Verify that work of other trades likely to damage cable has been completed.

2.	Storage

a.	Cable shall be shipped from the manufacturer with ends temporarily sealed against moisture ingress.

b.	When cables are cut in the field, the end shall be sealed using standard sealing compound and PVC tape.

c.	Cable shall be stored in a clean dry location.

3.	Handling

a.	Cable shall be uncoiled by rolling and rotating supply reel.  Do not pull from coil periphery or center.

b.	Take precautions necessary to prevent damage to cable from contact with sharp objects, including pulling over foreign material or sheaves.

4.	Bending:

a.	Not less that five (5) times the cable diameter for cable not more than 3/4 inch.

b.	Not less than ten (10) times the cable diameter for cable more than 3/4 inch.

5.	Pulling:

- For all cables up to and including #1 AWG use ten inch or larger sheaves.

- For #1.0 through 250 kcmil inclusive, use 18 inch or larger sheaves.

- For 350 kcmil and larger cables, use 24 inch or larger sheaves.

- On pulls of over 360 degrees, contact manufacturer for assistance.

- 350 and 500 kcmil cables shall not be pulled more than 360 degrees in total.

6.	Splicing:

- All fire rated splices shall be made in the factory.

- In the event a field splice is necessary, it must be approved by the RE and:

(1)	made in the field by manufacturer’s field technician, or

(2)	made in the field by personnel trained by the cable manufacturer using manufacturer’s components.

7.	Terminations:

a.	Field made terminations shall be made with cable manufacturer’s termination kits only.  Stripping tools, crimping and compression tools available from the manufacturer shall be used for proper cable termination.

b.	Terminations must be completed immediately once started to avoid moisture ingress from surrounding air.  Prior to completing each termination, test insulation resistance and follow manufacturer’s drying procedures until insulation resistance reaches an acceptance level.

c.	Connections to ferrous cabinets for single conductor cables shall incorporate brass plates ¼-inch thick by 4-inch wide by length as required with ½-inch, ¾-inch, 1-inch per 1-1/4-inch drilled and tapped holes.  Install per manufacturers’ drawing.

8.	Sheath induction reduction:

- When multi-phase circuits have paralleled single conductors, cables shall be run in groups having one of each phase and neutral in each group.

- Each set of paralleled conductors shall be separated by at least two single cable diameters.

- Each group of cables shall be fastened tightly together, at least once between each support on horizontal runs and twice on vertical runs, using ½-inch wide by 0.030-inch thick stainless steel straps.

9.	Exposed or Surface installations:

1.	Cable may be secured directly to fire rated building structure using an approved method such as one, or any combination, of the following:

(1)	Straps: ½-inch wide x 1-½ inch long by 0.030 inch thick stainless steel or copper straps.  Each strap shall contain two ¼-inch holes for securing with 3/16-inch by minimum 1-3/4 inch long steel anchors.

(2)	Steel struts and cable tray: Use only the steel strut framing system and support recommended by Pyrotenax.  Aluminum or other materials are not acceptable.

(3)	Other approved method.

b.	Cable supports shall not exceed three (3) feet on center horizontally, or six (6) feet vertically.

c.	Cables shall be installed parallel to building lines.

10	Wall or floor penetrations:

- Provide sleeve to protect cable and penetration opening during pulling.

- Provide approved sealing of all penetrations.

11.	Neatly train and lace cable inside boxes, equipment, and switchboard.

12	Field Quality Control

- Inspect cable for physical damage and proper connection.

- Measure tightness of bolted connections and compare torque measurements with manufacturer’s recommended values.

- Verify continuity of each conductor.

- Prior to energizing cables, measure insulation resistance of each cable.  Tabulate and submit for approval.

- Provide certification from cable manufacturer that installation is in accordance with their requirements.

## 3.9	MOTOR CONTROL

A.	Mount grouped switches, starters and other equipment on backboards.  See Paragraph 2.4, Backboards & Equipment Cabinets.

## 3.10	SLEEVES, INSERTS AND ANCHOR BOLTS

A.	Furnish, set in place, coordinate and be responsible for location of sleeves, inserts and anchor bolts required for work of this Division.  If work is not completed in coordination with work of other trades, trade involved shall do cutting and patching required or have same done, at no additional cost to FAA.

B.	Conduits passing through floors, walls or partitions shall be provided with sleeves which have internal diameter one inch larger than outside diameter of conduit and insulation, if any.

C.	Sleeves through outside walls shall be as shown on the Contract Drawings.

D.	Sleeves through fire-rated concrete floors or interior masonry walls shall be Schedule 40 steel pipe; sleeves through concrete floors or interior masonry walls which are not fire-rated shall be Schedule 40 PVC.  Sleeves shall be flush with finished wall, flush with finished ceiling, and extended two inches above finished floor.

E.	Sleeves through interior partitions shall be Schedule 40 PVC, set flush with finished surfaces of partitions.

F.	Inserts shall be of pressed steel construction, with accommodation for removable nuts and threaded rods up to ¾-inch diameter, permitting lateral adjustment.  Inserts shall be by Carpenter and Patterson, Grinnell or acceptable equivalent.

1.	Individual inserts shall open at top, permitting reinforcing rods up to ½-inch diameter to pass through insert body.

2.	Strip inserts shall have attached rods with hooked ends.

## 3.11	BASES AND SUPPORTS

A.	Unless noted otherwise, provide necessary supports, rails, framing, bases and piers required for equipment furnished or installed under this Division.

B.	Unless otherwise indicated:  all floor-mounted equipment shall be mounted on 3,000 psi, 6” high concrete pads.

1.	Pads shall be six-inch thick, unless shown otherwise, and shall NOT extend more than one inch beyond equipment footprint.  Top edge of pads shall be chamfered.

2.	Furnish dimensional and load information so that shop drawings for pads may be submitted and reviewed prior to pad installation.

3.	Equipment shall be firmly grouted into concrete pads and anchor bolted.

C.	Where mounted on the floor:  Foundations, supports, pads, bases and piers shall be of the same finish quality as the adjacent flooring material.

D.	Equipment supports shall be designed and constructed so that equipment will be capable of resisting both vertical and horizontal movement.

## 3.12	PAINTING

A.	Unless otherwise specified, materials furnished under this Division shall have prime coat and standard manufacturer’s finish.

B.	Finish painting of exposed work and equipment is covered under Division 9.

C.	Paint electrical equipment and appurtenances in concealed and unfinished areas with one coat of rust-inhibiting paint or with an appropriate bitumastic protective product designed for the intended application.  Asphalt paint is NOT acceptable.  Items to be painted shall include, but not be limited to:  non-insulated hangers, supports, piping, conduit, tanks and other ferrous metal work, which are concealed or inaccessible but not galvanized.

D.	Special care shall be taken to avoid painting or spattering equipment nameplates.

E.	Cooperate in identifying systems for painters.  Refer to paragraph 3.3, Identification.

## 3.13	GENERAL WIRING TESTS

A.	Prior to final inspection and tests:  Wiring and connections shall be completed, devices and equipment shall be properly operating, power and lighting circuit and control wiring shall be clearly identified with acceptable tags, and lighting fixtures shall be installed, ready for acceptance.

B.	Before devices are installed, test each wiring system for following:

1.	System shall be free from short circuits.

2.	System shall be free from grounds.

3.	Systems at or below 600 V shall have minimum insulation resistance of 5 megohms when tested with 1000 VDC potential between conductors and between conductors and ground, for minimum of one minute, at 70 deg. F ambient temperature and reasonably dry atmosphere.

C.	Upon completion, demonstrate that systems are properly phase balanced.

## 3.14	MOTOR TESTS

A.	After systems are balanced and ready to be turned over to FAA, test and report motor performance data for motors.

B.	Include following information in test report:

1.	Equipment name and/or number.

2.	Manufacturer’s nameplate data, including RPM, horsepower, volts, full-load amperes per phase, service factor, power factor, manufacturer’s name, motor type and model number.

3.	Motor test data, including amperes for each phase, average amperes, and phase-to-phase voltage at motor, starter or disconnect switch terminals.

4.	Percentage of:  (Average load test amperes) divided by (Nameplate full-load amperes).

5.	Size, number and ampere rating of overload heaters.  Manufacturer’s motor starter heater table.

6.	Breaker and disconnect switch data, including size and manufacturer of switches and fuses and branch circuit wiring.

3.15	OPERATIONAL TESTS

A.	Each piece of electrical equipment, including lighting fixtures, motors and controls shall be operated continuously for minimum test period of one hour.

B.	Demonstrate by operating equipment that circuits and devices are in good operating condition.  Each item of control equipment shall be operated minimum of five times.  Demonstration shall be performed after wiring tests.

3.16	MECHANICAL SYSTEM ADJUSTMENT AND TESTING

A.	Be present during adjustment period and final testing of mechanical systems.  Take readings necessary to ensure that electrical systems are operating properly.  Tests for mechanical work are detailed under Division 11, Equipment or Division 15, Mechanical.

B.	Take ampere readings at each electrical component, such as motor and heating coil, to determine proper operation.

C.	Record readings and submit them to the RE for review.

## 3.17	DEMOLITION AND RENOVATION:  IMPACT ON EXISTING SYSTEMS

Not used.

END OF SECTION

SECTION 16301

UNDERGROUND ELECTRICAL WORK

PART 1	GENERAL

1.1	APPLICABLE PUBLICATIONS

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI)

ANSI C2	National Electrical Safety Code

ANSI/ ICEA S-94-649	Concentric Neutral Cables Rated 5-46

ANSI/ ICEA S-97-682	Utility Shielded Power Cable Rated 5-46 kV

ANSI/ ICEA S-105-692	600 Volt Single Layer Thermoset Insulated Utility Underground Distribution Cable

ANSI/ ICEA S-81-570	Direct Burial, 600 Volt, Ruggedized Insulation

AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

ASTM B 1	Hard-Drawn Copper Wire

ASTM B 8	Concentric-Lay-Stranded Copper Conductors, Hard, Medium-Hard, or Soft

ASTM D 1556	Density and Unit Weight of Soil in Place by the Sand-Cone Method

ASTM D 2466	Poly (Vinyl Chloride) (PVC) Plastic Pipe, Schedule 40

INSTITUTE OF ELECTRICAL AND ELECTRONICS ENGINEERS (IEEE), INC.

IEEE 48	High-Voltage Alternating-Current Cable Terminations

IEEE Std 48 	Standard Test Procedures and Requirements for Alternating-Current Cable Terminations 2.5 kV through 765 kV

IEEE Std 386	Separable Insulated Connector Systems for Power Distribution Systems Above 600 V

IEEE Std 404	Cable Joints for Use with  Extruded Dielectric Cable Rated 5000 V through 138 000 V and Cable Joints for Use  with Laminated Dielectric Cable Rated 2500 V  Through 500,000V

IEEE Std 592	Exposed Semiconducting Shields on  Premolded High Voltage Cable Joints and  Separable Insulated Connectors

NATIONAL ELECTRICAL MANUFACTURER'S ASSOCIATION (NEMA)

NEMA RN 1	Polyvinyl-Chloride (PVC) Externally Coated Galvanized Rigid Steel Conduit and Intermediate Metal Conduit

NEMA TC 2	Electrical Polyvinyl Chloride (PVC) Tubing (EPT) and Conduit (EPC-40 and EPC-80)

NEMA TC 3	PVC Fittings for Use With Rigid PVC Conduit and Tubing

NEMA TC 6	PVC and ABS Plastic Utilities Duct for Underground Installation

NEMA TC 9	Fittings for ABS and PVC Plastic Utilities Duct for Underground Installation

NEMA WC 70	Nonshielded 0-2kV Cables

NEMA WC 71	Nonshielded 2001-5kV Cables

NEMA WC 74	Shielded Power Cable 5-46 kV

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

NFPA 70	National Electrical Code (NEC)

UNDERWRITERS LABORATORIES INC. (UL)

UL 6	Rigid Metal Conduit

UL 467	Grounding and Bonding Equipment

UL 510	Insulating Tape

UL 514A	Metallic Outlet Boxes

UL 514B	Fittings for Conduit and Outlet Boxes

UL 854	Service-Entrance Cables

UL 1242	Intermediate Metal Conduit

1.2	GENERAL REQUIREMENTS

1.2.1	Underground Service

Terminate underground service where shown on drawings and projections thereof, except that service conductors shall be continuous to the terminating point indicated.  Protect ends of underground conduit with threaded metal caps until connections are made.

1.2.2	Electrical Characteristics

Electrical characteristics for this project shall be 480/277 AND 208/120 volts secondary, three-phase, 4-wire.  Final connections to the power distribution system shall be as detailed on drawings.

1.3	SUBMITTALS

The following shall be submitted in accordance with Section 01330, “Submittal

Procedures”.

1.3.1	SD-01, Manufacturer’s Data; GA

a.	Conduit

b.	Splice box

c.	Insulating tape

d.	Terminator

e.	Cable lubricants

f.	Telephone cable and splices

g.	Handholes

1.3.2	SD-04, Drawings; GA

a.	Splice box

b.	Terminator

c.	Telephone cable and splices

d.	Handholes

1.3.3	SD-06, Manufacturer’s Instructions; GA

a.	Manufacturer’s directions for use of ground megger with proposed method indicated

b.	Terminator manufacturer's installation instructions

1.3.4	SD-13, Certificates; GA

a.	Certificates of Compliance

PART 2	PRODUCTS

2.1	GENERAL

Provide materials and equipment listed by UL or approved by Factory Mutual (FM) System when such equipment is listed or approved.

2.2	CONDUIT

2.2.1	PVC-Coated Sch 40 Gal. Steel

Rigid galvanized steel conduit and fittings shall conform to the requirements of UL 6 and UL 1242, for threaded type, respectively, and shall be coated with a polyvinyl chloride (PVC) sheath bonded to the galvanized exterior surface, nominal 40 mils thick, conforming to NEMA RN 1, Type A40, except that hardness shall be nominal 85 Shore A durometer, dielectric strength shall be minimum 400 volts per mil at 60 Hz, tensile strength shall be minimum 3500 psi, and aging shall be minimum 1000 hours in an Atlas Weatherometer.

2.2.2	Rigid Metallic Conduit – RMC

Rigid Metallic Conduit (RMC) shall be UL listed, hot dipped galvanized steel with full cut hot dipped galvanized UFT threads.  RMC shall be chromated on all surface for corrosion and abrasion protection.  Connector and couplings shall be galvanized steel threaded type for RMC use.

2.2.3	Rigid Nonmetallic Conduit - PVC

Rigid nonmetallic PVC conduit shall conform to UL listed Schedule 40 meeting ASTM standard F512 type EB designed to be encased in concrete.

2.2.4	Outlet boxes for use with rigid steel conduit shall be cast-metal cadmium or zinc-coated if of ferrous metal with gasketed closures and shall conform to UL 514A.  Fittings for steel conduit and outlet boxes shall conform to UL 514B.

2.3	PLASTIC INSULATING TAPE

Provide UL 510.

2.4	WIRE AND CABLE

2.4.1	Wire and cable conductor sizes are designated by American Wire Gauge (AWG) and Thousands of Circular Mils (MCM).  Conductor and conduit sizes indicated are for copper conductors, unless otherwise noted.  Insulated conductors shall bear the date of manufacture imprinted on the wire insulation with other identification.  Wire and cable manufactured more than 24 months before delivery to the job site shall not be used.

2.4.2	Conductors rated 600 volts and less, including service entrances, shall conform to UL 854, Type USE, THW, THHW, THWN.  Conductor size and number of conductors in each cable shall be as indicated.  Cable shall be color coded.  Conductor identification shall be provided within each enclosure where a tap, splice, or termination is made.  Conductor identification shall be by color-coded insulated conductors, plastic-coated self-sticking printed markers, colored nylon cable ties and plates, or heat shrink type sleeves.  Control circuit terminations shall be properly identified.  Conductors No. 10 AWG and smaller shall be solid copper.  Conductors No. 8 AWG and larger shall be stranded copper.

a.	Colors for coding conductors shall be:

208-VOLT SYSTEM

Neutral - White

Phase A - Black

Phase B - Red

Phase C - Blue

Grounding Conductor - Green

2.5.	GROUNDING AND BONDING EQUIPMENT

UL 467.  Ground rods shall be copperweld type copper clad steel with diameter adequate to permit driving to full length of the rod, but not less than 3/4 inch in diameter and 10 feet long unless otherwise indicated.

PART 3	EXECUTION

3.1	INSTALLATION

Underground installation shall conform to ANSI C2 and NFPA 70 except as otherwise specified or indicated.

3.1.1	Contractor Damage

The Contractor shall promptly repair any utility lines or systems damaged by Contractor operations.  Damage to lines or systems previously located or “marked out”, which are caused by Contractor operations, shall be repaired at no expense to the government.  If the Contractor is advised in writing of the location of a line or system, such notice shall provide that portion of the line or system with “previously located” status in determining liability for damages.  In any event, the Contractor shall immediately notify the Resident Engineer (RE) of any such damage.  Underground utility line sensor shall be utilized prior to digging any trenches.

3.1.2	Cables

3.1.2.1 Cables shall be in one piece without splices between connections except where the distance exceeds the lengths in which the cable is furnished.

3.1.2.2	Bends in cables shall be not less than those specified in NFPA 70 for the type of cable specified.

3.1.2.3	Horizontal slack of approximately 3 feet shall be left in the ground on each end of cable runs, on each side of connection boxes, and at all points where connections are brought above ground.  Where cable is brought above ground, leave additional slack to make necessary connections.  Splices in lead-sheathed or armored cables shall be enclosed in split-type cast-iron splice boxes; after completion of the connection, tightly clamp the box and fill with insulating filler compound.

3.1.2.4	Identification Slabs Markers

Provide a slab at each change of direction of the cable, over the ends of ducts or conduits which are installed under paved areas and roadways, and over each splice.  Identification slabs shall be concrete, approximately 20-inches by 20-inches by 6 inches thick, and shall be set flat in the ground so that the top surface projects not less than 3/4 inch, nor more than 1-1/4 inches above ground.  The concrete shall have a minimum compressive strength of 3000 psi and shall have a smooth, troweled finish on exposed surface.  Inscribe an identifying legend such as “cable”, “duct”, “splice”, or other applicable designation on the top surface of slab before the concrete hardens.  Inscribe circuit identification symbols on slabs as directed.  The letters or figures shall be approximately 2 inches high and the grooves shall be approximately 1/4 inch in width and depth.  Install the slabs so that the side nearest the inscription on the top shall include an arrow indicating the side nearest the cable.

3.1.3	Conduit Installation

3.1.3.1	Underground Duct Without Concrete Encasement

Conduits shall be PVC-coated galvanized steel or Schedule 40 PVC.

3.1.3.2	Conduits above ground

Conduits shall be rigid threaded heavy wall galvanized steel conduit.

3.1.3.3	Conduit below ground

Electrical primary, tie to point to pad mounted transformer: PVC Concrete encased, size as shown on Contract Drawings.

3.1.3.4	Electrical secondary

Pad mounted Transformer to Buildings:  4 inch galvanized steel rigid threaded heavy wall PVC coated.

3.1.3.5	The top of the conduit shall be not less than 24 inches below grade, shall slope away from buildings and toward manholes and other necessary drainage points, and shall run in straight lines except where a change of direction is necessary.  As each conduit run is completed, a testing mandrel not less than 12 inches long with a diameter 1/4 inch less than the inside diameter of the conduit shall be drawn through each conduit, after which a stiff-bristled brush shall be drawn through until the conduit is clear of earth, sand, or gravel particles.  Conduit plugs shall then immediately be installed.  Ensure a minimum 3-inch clearance from the conduit to each side of the trench.  Grade the bottom of the trenches smooth; where rock, soft spots, or sharp-edged materials are encountered, excavate the bottom for an additional 6 inches; fill with sand or earth, free from particles that would be retained on a 1/4-inch sieve; and tamp level with the original bottom.

3.1.3.6	Under roads, paved areas, and railroad tracks, install conduits in concrete encasement of rectangular cross-section providing a minimum of 3-inch concrete cover around ducts.  The concrete encasement shall extend at least 5 feet beyond the edges of paved areas and roads.

3.1.3.7	Separate multiple conduits with a minimum concrete thickness of 2 inches, except that light and power conduits shall be separated from control, signal, and telephone conduits by a minimum distance of 3 inches.  Stagger the joints of the conduits by rows and layers to strengthen the conduit assembly.  Provide plastic duct spacers that interlock vertically and horizontally.  Spacer assembly shall consist of base spacers, intermediate spacers, and top spacers to provide a completely enclosed and locked-in conduit assembly.  Install spacers per manufacturer’s instructions, but provide a minimum of two spacer assemblies per 10 feet of conduit assembly.

3.1.4	Buried Utility Warning and Identification Tape

Provide detectable aluminum foil plastic-backed tape or detectable magnetic plastic tape manufactured specifically for warning and identification of buried cable and conduit.  Tape shall be detectable by an electronic detection instrument.  Provide tape in rolls, 3 inches minimum width, color coded for the utility involved with warning and identification imprinted in bold black letters continuously and repeatedly over entire tape length.  Warning and identification shall be “CAUTION-BURIED ELECTRIC CABLE BELOW” or similar.  Use permanent code and letter coloring unaffected by moisture and other substances contained in trench backfill material.  Bury tape with the printed side up at a depth of 12 inches below the top surface of earth or the top surface of the subgrade under pavements.

3.1.5	Cable Pulling

Test existing ducts with a mandrel and thoroughly swab out to remove foreign material before the pulling of cables.  Cables shall be pulled down grade with the feed-in point at the manhole or buildings of the highest elevation.  Flexible cable feeds shall be used to convey cables through the manhole opening and into the ducts.  Cable lubricants shall be used and use only the cable manufacturer specifically recommended lubricants.  Cable-pulling tensions shall not exceed the maximum pulling tension recommended by the cable manufacturer.  Do not exceed the specified cable bending radii when installing cable under any conditions, including turn-ups into switches, transformers, switchgear, switchboards, and other enclosures.  Cable with tape shield shall have a bending radius not less than 12 times the overall diameter of the completed cable.  Cable with wire shield shall have a bending radius not less than eight times the overall diameter of the completed cable.  If basket-grip type cable-pulling devices are used to pull cable in place, cut off the section of cable under the grip before splicing and terminating.

3.1.5.1	Secondary cable runs, 600 volts and less, shall include an insulated copper equipment grounding conductor sized as required by the rating of the over current device supplying the phase conductors.

3.1.5.2	Installation of Cables in Handholes

Route cables along walls providing the longest route and the maximum spare cable lengths. Form cables to closely parallel walls without interference to duct entrances.  Support cables on brackets and cable insulators at a maximum of 4 feet.  Identify each cable by corrosion-resistant embossed metal tags attached in each underground structure in accordance with the cable schedule and as approved by the RE.  Example: 208V cable, Circuit 4-Sub. NB - to SP.  Identify each phase of the MV cable.

3.1.6	Cable Terminating

Protect terminations of insulated power and lighting cables from accidental contact, deterioration of coverings, and moisture by the use of terminating devices and materials.  Make terminations by using materials and methods indicated or specified herein or as designated by the written instruction of the cable manufacturer and termination kit manufacturer.  Termination for high-voltage cables shall be rated, and be capable of withstanding test voltages, in accordance with IEEE 48.  Terminations of single and multiconductor cables shall include the securing and sealing of the sheath and insulation of the cable conductors, stress relief and grounding of cable shields of shielded cable, and grounding of neutral conductors, metallic sheaths, and armor.  Adequately support cables and cable terminations to avoid any excessive strain on the termination and the conductor connection.

3.1.7	Splices for 600-Volt Class Cables

Splices in underground systems shall be made only in accessible locations such as manholes and handholes, using a compression connector on the conductor and by insulating and waterproofing by one of the following methods suitable for continuous submersion in water.

3.1.7.1	Cast-type splice insulation shall be provided by means of a molded casting process employing a thermosetting epoxy resin insulating material that shall be applied by a gravity-poured method or by a pressure-injected method.  The component materials of the resin insulation shall be in a packaged form ready for convenient mixing without removing from the package.  Do not allow the cables to be moved until after the splicing material has completely set.

3.1.7.2	Gravity-poured method shall employ materials and equipment contained in an approved commercial splicing kit which includes a mold suitable for the cables to be spliced.  When the mold is in place around the joined conductors, prepare and pour the resin mix into the mold.  Do not allow cables to be moved until after the splicing materials have completely set.

3.1.8	Grounding

Noncurrent-carrying metallic parts associated with electrical equipment shall have a maximum resistance to solid earth ground not exceeding the following values:

500 kVA or less	10 ohms

Grounded secondary distribution system neutral and

noncurrent-carrying metal parts associated with

distribution systems and grounds not otherwise covered	25 ohms

3.1.8.1	Grounding electrodes shall be cone-pointed ground rods, driven full depth plus 6 inches, installed when indicated to provide an earth ground of the appropriate value for the equipment being grounded.

3.1.8.2	Grounding connections which are buried or otherwise normally inaccessible, and excepting specifically those connections for which access for periodic testing is required, shall be made by exothermic weld or compression connector.  Exothermic welds shall be made strictly in accordance with the weld manufacturer's written recommendations.  Welds which are “puffed up” or which show convex surfaces, indicating improper cleaning, are not acceptable.  Mechanical connectors are not required at exothermic weldments.  Compression connector shall be the type which uses a hydraulic compression tool to provide the correct circumferential pressure.  Tools and dies shall be as recommended by the manufacturer.  An embossing die code or other standard method shall provide visible indication that a connector has been adequately compressed on the ground wire.

3.1.8.3	Grounding conductors shall be stranded-bare copper conforming to ASTM B 8, Class B, for sizes No. 6 AWG and larger, and shall be solid-bare copper conforming to ASTM B 1 for sizes No. 8 and smaller.  Cable sheaths, cable shields, conduit, and equipment shall be grounded with No. 6 AWG.  Surge arresters shall be grounded to ground rods with No. 4 AWG.

3.1.8.4	Ground Cable Crossing Expansion Joints

Protect ground cables crossing expansion joints or similar separations in structures and pavements by use of approved devices or methods of installation which provide the necessary slack in the cable across the joint to permit movement.  Use stranded or other approved flexible copper cable run or jumper across such separations.

3.1.9	Special Conditions

During the construction of duct banks and underground structures located in streets, the streets shall remain open to traffic.  Plan and execute the work to meet this condition.  At locations where duct banks cross railroad tracks and the work requires closing of the tracks, secure permission from the RE for each track closure.

3.2	FIELD TESTS

As an exception to requirements that may be stated elsewhere in the contract, notify the RE in writing at least 5 working days prior to each test.  Furnish labor, equipment, and incidentals required for testing, except that the Government will provide electric power required for the tests.  Correct defects in the work provided by the Contractor and repeat tests until the work is in compliance with contract requirements.  Show by demonstration in service that circuits and devices are in good operating condition.  Tests shall be such that each item of control equipment will function not less than five times.

3.2.1	Distribution Conductors 600-Volt Class

After wiring is completed and connected ready for operation, but prior to placing systems in service and before any branch circuit breakers are closed, perform insulation resistance tests in all circuits.  Measure the insulation resistance between conductors and between each conductor and ground.  Use an instrument capable of making measurements at an applied potential of 500 volts.  Take readings after the voltage has been applied for a minimum of 1 minute.  The minimum insulation resistance for circuits of No. 12 AWG conductors shall be 1,000,000 ohms.

3.2.2	Ground Rods

Test ground rods for ground resistance value before any wire is connected.  Perform ground resistance measurements in normally dry weather, not less than 48 hours after rainfall.  Ground resistance shall also be measured for each piece of equipment to the ground electrode.  Use a portable ground testing megger to test each ground or group of grounds.  The instrument shall be equipped with a meter reading directly in ohms or fractions thereof to indicate the ground value of the ground electrode under test.  Provide one copy of the ground megger manufacturer’s directions, indicating the method to be used.

3.2.3	Excavation, Trenching, Backfilling, and Compaction

Except where specified otherwise, provide in accordance with Section 02225, “Excavation, Backfilling, and Compaction”.

3.2.4	Test Report

a.	600-Volt Cables:  Identify each cable and test result.

b.	Grounding Electrodes and Systems:  Identify electrodes and systems for each test, as well as the resistance and soil conditions at the time the measurements were made.

END OF SECTION

SECTION 16400

SERVICE AND DISTRIBUTION

PART 1	GENERAL

This Section covers the specification of secondary electrical service and distribution systems.

## SCOPE

Provide labor, materials, services, equipment and transportation necessary for complete and operational secondary electrical service and distribution systems as indicated on Contract Drawings and specified herein.

## 1.2	SUBMITTALS

    - SD-01, Manufacturer's Catalog Data; GA

Submit all necessary information to demonstrate conformance with the Specifications for:

a.	Fuses

b.	Circuit breaker and TCC curves

- Panel boards

    - SD-04, Drawings; GA

A.	Submit for review shop drawings on the following:

  - Panel board

  - Circuit breakers

  - Fuses

- Submit coordination curves for breakers and fuses with shop drawing submittals for review.  Acceptance of system components will be contingent upon achievement of reasonable coordination of system.  Final sizing of fuses and selection of trip settings shown on Contract Drawings are subject to this coordination review by RE and manufacturer’s representative.

## 1.2.3	SD-09, Reports; GA

## A.	Submit reports for all testing required in Paragraph 3.3.

## 1.3	STANDARDS

A.	Work of this Division shall conform to following standards, as applicable:

1.	NEMA Instructions for Safe Installation, Operation, and Maintenance of Panelboards Rated 600 Volts or less.

2.	NEMA Instructions for Safe Handling, Installation, Operation and Maintenance of Deadfront Distribution Switchboards Rated 600 Volts or less.

3.	NEMA Instructions for Safe Handling, Installation, Operation and Maintenance of Busway and Associated Fittings.

# PART 2	PRODUCTS

## 2.1	PANELBOARDS FOR GENERAL USE

A.	Panelboards shall be by Square D, General Electric, or Cutler Hammer/ Westinghouse. Refer to Contract Drawings for requirements on special ratings and auxiliary devices such as relays, contactors and time switches.  Panelboards shall be UL listed and circuit breaker-equipped.  Design shall be such that individual breakers can be removed without disturbing adjacent units or without loosening or removing supplemental insulation supplied as means of obtaining clearances as required by UL. Where “space only” is indicated, make provisions for future installation of breaker sized as indicated.

B.	Panelboards shall conform to standards of NEMA PB-1.  Panelboards shall have distributed phase bussing throughout.  Support bus bars on bases independent of circuit breakers.  Main buses and back pans shall be designed so that breakers may be changed without machining, drilling, or tapping.  Provide isolated neutral bus in each panel for connection of circuit neutral conductors.  Provide separate ground bus identified as equipment grounding bus for connecting grounding conductors; bond to steel cabinet.  In addition to equipment grounding bus, provide second isolated ground bus, where indicated.

C.	Panelboards shall have copper bussing.

D.	Multiple section panelboards shall have same height boxes.

E.	Each cabinet shall have hinged locking metal door and card holder for directory.  All locks shall be fitted to same key.  Panelboard card directories shall be completely filled out (typewritten) upon completion of project and shall include source of service.  Revise existing directories when new breakers are added.  Cover trims for panelboards shall be hinged to box with full height, semi-concealed piano hinges, fastened to box lip with screws, not trim clamps.  Door shall be hinged.  Trims shall be UL labeled.

F.	Provide oversize gutters for gutter taps where wiring runs through to floor above.  Through-feed lugs will NOT be accepted.

G.	208Y/120 V Panelboards:  Panelboard shall have main, lugs, branches, and circuit breakers as scheduled.  Panelboards shall have a minimum rating of 22,000 A RMS symmetrical interrupting capacity unless scheduled otherwise.  Series ratings are NOT acceptable.

1.	Lighting and small power panelboards shall be Square D #NQOD with bolt-on breakers or acceptable equivalent.

2.	Power panelboards shall be Square D “I-Line” or acceptable equivalent.

H.	480Y/277 V and 480 V DELTA panelboards:  Panelboards shall have main, lugs, branches and circuit breakers as scheduled.  Panelboards shall have a minimum rating of 42,000 A symmetrical interrupting capacity unless scheduled otherwise.  Series ratings are NOT acceptable.

1.	Lighting panelboards fed from a 480Y/277 V source shall be Square D, Type NF with bolt-on breakers or acceptable equivalent.

2.	Lighting or power panelboards fed from a 480 V DELTA source shall be Square D “I-Line” or acceptable equivalent.

I.	Provide bolt-on thermal magnetic-type circuit breakers with interrupting capacity to match panelboard rating.  Breaker terminals shall be UL listed as suitable for the type of conductor provided.  Multiple circuit breaker shall be a common trip-type with single operating handle.  Breaker design shall be such that overload in one pole automatically causes all poles to open.  Maintain phase sequence throughout each panel so that any three adjacent breaker poles are connected to Phase A, B, C, respectively.

# PART 3	EXECUTION

## 3.1	SPECIAL CLEANING

A.	Perform vacuum cleaning and wiping down of bus bars, bus bracing and supports in panelboards, internal enclosure base in motor control centers, and electrical equipment enclosures.

B.	Check bus connections and tighten bolts in panels within work areas, in accordance with manufacturer’s torque requirements.

## 3.2	IDENTIFICATION

A.	Provide nameplates and general identification as required under Section 1610, “General Requirements for Electrical Work”, Section 16050, “Basic Materials and Methods – Electrical”, and under Division 1, and as follows.

B.	Panelboard nameplate shall include following information:

1.	Panelboard reference number.

2.	Source panel reference, including circuit breaker supplying panelboard.

3.	Location of source panel by building, floor level and room number.

## 3.3	TESTING

A.	Acceptance testing for electrical equipment and cable, specified herein, shall be performed by independent testing firm with minimum ten years experience in testing the specified items.  Firm shall be member of International Electrical Testing Association (INETA).

B.	Testing procedures shall be as described in INETA “Acceptance Testing Specifications”.

C.	Obtain circuit breaker and relay characteristic curves from manufacturer, prior to testing, and furnish copies to Resident Engineer (RE).

D.	Testing firm shall notify switchgear manufacturer in advance of dates on which acceptance tests will be performed so that manufacturer’s representative may be present.

E.	Testing firm shall immediately notify Contractor and RE, of any deficiencies requiring correction before switchboard is placed in service and shall confirm information in writing within five days.

F.	Discrepancies found shall be corrected by firm which installed switchboard.  However, testing firm shall make minor field adjustments that may be found necessary.

G.	Test report shall include written test results on firm’s standard test forms.  Refer to paragraph 1.2.3.

## 3.4	CIRCUIT BREAKER SETTINGS

- Verify final trip settings for adjustable circuit breaker elements.  Instantaneous magnetic settings shall be minimum, unless otherwise noted.

# END OF SECTION

SECTION 16901

PROCESS INSTRUMENTATION AND CONTROLS

PART 1	GENERAL

1.1	DESCRIPTION

1.1.1	The work of this Section includes all labor, materials and equipment required to modify the existing control system in accordance with this specification, and the treatment process and controls description on the Project Plans.  This work shall include providing instruments; control panel modification, programming changes; installation and field wiring; system calibration, checkout and control loop tuning.  The work of this Section as herein specified includes, but is not limited to, the following:

- Pressure Instrumentation

- Flow Instrumentation

- Programming of Controllers

- Control Panels

1.1.2.	All design, equipment, calibration, checkout and control loop tuning described in this section shall be the responsibility of a single supplier, referred herein as the Control System Supplier.  The Control System Supplier shall provide whatever equipment and field adjustments are necessary for the system to function as specified in the Contract Documents.  The Control System Supplier shall provide equipment, devices, software, programming or calibration services necessary to meet these requirements whether or not the specific equipment, devices software, programming or calibration service, are specifically identified in this specification or shown on the drawings.

1.2	QUALITY ASSURANCE

1.2.1	Prior to commencing work, submit data showing that the Control System Supplier has successfully completed work on systems of the same type and design as specified herein, or that he has a firm contractual agreement with a subcontractor having the required experience.  Include the names and locations of at least two installations where the Contractor, or the subcontractor referred to above, has installed/modified such systems.  Indicate the type and design of each system and certify that the system has performed satisfactorily for a period of at least 18 months.  Previous satisfactory work has been completed at the site by Kruse Controls Inc. of Baltimore, Md.

1.2.2	All materials and equipment supplied and installed shall conform to the applicable standards referenced in paragraph 1.3 below.  All materials provided shall be new and unused, shall be of the type and materials specified herein and shall meet the intent and requirements specified. All materials found during the progress of work to have cracks, flaws or other defects shall be rejected by the Resident Engineer (RE). All defective materials shall be promptly removed from the work site and replaced.

1.2.3	The Contractor shall use adequate numbers of skilled workmen who are thoroughly trained and experienced in the necessary crafts and who are completely familiar with the specified requirements and the methods needed for proper performance of the work in this section.

1.2.4	Equipment and component parts thereof shall bear manufacturer’s nameplate, giving manufacturer’s name, size, type, model number or serial number, and electrical characteristics to facilitate maintenance and replacements.  Nameplates of distributors or contractors are not acceptable.

1.2.5	Electrical equipment shall be UL listed and approved, and conform to the latest edition of NEC and NEMA; materials and accessories shall be constructed in accordance with latest ASTM standards.

1.2.6	Unless otherwise specified, materials and equipment shall be essentially the standard cataloged products of manufacturers regularly engaged in the production of such equipment and shall be the manufacturer’s latest design that complies with the specifications.  Unless otherwise specified, where two units of the same class of equipment are required, these units shall be products of a single manufacturer.

1.2.7	Provide the services of a representative or technician from the Control System Supplier, experienced in the installation and operation of the type of system being provided, to supervise installation, adjustment, preliminary testing, and final testing of the system and to provide instruction to Government personnel.

1.3	REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

NATIONAL ELECTRICAL MANUFACTURER'S ASSOCIATION (NEMA)

NEMA ICS 1  Industrial Control & Systems

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

NFPA 70  National Electrical Code

UNDERWRITERS LABORATORY (UL)

UL 854   Service Entrance Cables

1.4	SUBMITTALS

Government approval is required for submittals with a “GA” designation.  The following shall be submitted in accordance with Section 01300, “Submittal Procedures”.

1.4.1	SD-04, Shop Drawings;  GA

Shop drawings consisting of a complete list of equipment and materials, including manufacturer’s descriptive and technical literature; performance charts and curves; catalog cuts; and installation instructions.  Shop drawings shall also contain complete wiring and schematic diagrams; equipment layout and anchorage; and any other details required to demonstrate that the system has been coordinated and will properly function as a unit.

a.	Product information for sensors/transducers and field instruments.

b.	Programmable Logic Control and Network Communications Information

(1)  	System Description

(2)  	Hardware Description

(3)  	Software Description

c.	Panels, Consoles, and Cabinets Information

(1)	Layout Drawings

(2)	Panel schematic and internal point-to-point wiring interconnect and/or piping diagrams

(3)  	Electrical control schematics in accordance with JIC standards for all circuits indicated in the specifications or on the Contract Drawings.  No “typical” wiring diagrams will be acceptable and no tables or charts to describe wire numbers will be acceptable.  Wires shall be labeled and shown on the submittal drawings.

(4)  	Plan showing equipment layout.

(5)  	Stock lists or Bill of Materials for each panel including tag number, functional name, manufacturer’s name, manufacturer’s model number, and quantity for components mounted in and on the panel, console, or cabinet.

d.  	Field wiring and piping diagrams and point-to-point wiring diagrams including interconnections between field devices, panels, control stations, and motor starters.

e.  	Instrument loop diagrams for analog display, control and I/O loops prepared using ISA standard symbols.

f.  	System Software Documentation shall include the following as a minimum:

(1)	Complete list and description of control panel operation interface.

(2)  	Complete hard copies of ladder diagram programming for the recharge bed related components.

(3)  	Complete listing of external and internal I/O address assignments, register assignments, and preset constant values along with functional point descriptions for the recharge bed related components.

(4)  	Complete hard copies of program documentation for all types of programs.

(5)	Softcopy electronic deliverables that are properly formatted as appropriate for each subject component. This deliverable shall include, but not be limited to, all source code, electronic files, configuration files, database files and any other softcopy data used in the project formatted for use/reuse in the HMI/SCADA systems and support systems.   Each softcopy document and file shall be properly documented with metadata in appropriate detail to enable complete understanding of the code and function of each system and code component to allow for future troubleshooting and modification.  This shall include, but not be limited to, code line documentation and functional descriptions, detailed database design Metadata, including field, definitions descriptions, compiler versions, manufacturer software make model and version, detailed system design schema in UML, etc.

(6)	User’s manual describing procedures and providing examples for use of programming terminal, accessories, and system utility routines to perform control, program modification, program verification, diagnostics, program documentation, loading and backup, and other required system support functions.

g.	Instrument Index

1.4.2	SD-01, Design Data

a.	Control System Components; GA

b.	Spare Parts, GA

1.4.2.1	Control System Components

Detailed description of the proposed control system and components.  The description shall include, but not be limited to, the following items:

- Wire and cable

- Enclosures

- Pressure-sensor instruments

- Flow instrumentation

- Valve position indicators

1.4.2.2	Spare Parts

After approval of the shop drawings, and not later then 30 days prior to the start of operation, spare parts data for each different item of material and equipment specified.  The data shall include a complete list of parts and supplies, with current unit prices and source of supply.

1.4.3	SD-06, Posting Framed Instructions;  GA

Proposed diagrams and instruction shall be submitted prior to posting.

1.4.4	SD-13, Certificates

a.	Guarantee GA

1.4.4.1	The Contractor and the Control System Supplier shall guarantee all work under this division, in writing, to be free of defective work, materials or parts for a period as required by Section 15011, “Mechanical General Requirements” and Section 16010, “General Requirements for Electrical Work”.

1.4.5	SD-18, Records

a.	Qualifications, GA

1.4.5.1	Qualifications of the Control System Supplier; GA

1.4.6	SD-19 Operation and Maintenance Manual Addenda, GA

The Contractor shall prepare the required instructions including the manufacturer’s name, model number, service manual, parts list, and brief description of equipment and their basic operating features. The information will be added as an addenda to the site’s Operation and Maintenance Manual.  Six complete copies of instructions listing routine maintenance procedures, possible breakdowns and repairs, and trouble shooting guides shall be included in the Addenda.  The instructions shall include simplified diagrams for the system as installed.  Each set shall be permanently bound and shall have a hard cover.  The following identification shall be inscribed on the covers: the words “ADDENDA TO OPERATION AND MAINTENANCE INSTRUCTIONS,” name and location of the facility, name of the Contractor, and contract number.  These instructions shall include, but not be limited to the following:

a.	System layout showing instrumentation and controls and installation requirements.

b.	Approved wiring, logic, and control diagrams prepared in accordance with ISMC S5.1 including a drawing index, legend and symbols list, and abbreviations and identifiers.

d.	Operating and maintenance instructions for each piece of equipment, including checkout, troubleshooting, and servicing.

e.	Manufacturer’s bulletins, cut sheets and descriptive data, parts list, and recommended spare parts.

1.5	DRAWINGS AND SPECIFICATIONS

1.5.1	The Drawings and these Specifications are complementary each to the other, and any labor, or material called for by either, whether or not by both, shall be furnished and installed.

1.6	EQUIPMENT TAGGING

1.6.1	All instrumentation shall be tagged in accordance with Section 15011, “Mechanical General Requirements”.

PART 2	PRODUCTS

2.1	MATERIALS AND EQUIPMENT - GENERAL

2.1.1	Provide materials and equipment in accordance with Section 16010, “General Requirements for Electrical Work” and Section 16050, “Basic Materials and Methods – Electrical”.  All equipment and installations shall comply with the requirements of area classification as defined in Article 500 of the National Electric Code.

2.1.2.	Provide all necessary components, power supplies, input and output modules and racks and all cables and accessories necessary to implement the functional requirements described herein and shown on the Process & Instrumentation Diagrams.

2.1.3.	Conduit

Provide materials for this section as specified in accordance with Section 16050, “Basic Materials and Method – Electrical”.

2.1.4	Wire and Cable

Wire and cable conductor sizes are designated by American Wire Gauge (AWG).  Conductor and conduit sizes indicated are for copper conductors.  Insulated conductors shall bear the date of manufacture imprinted on the wire insulation with other identification.  Wire and cable manufactured more than 24 months before delivery to the job site shall not be used.  Power and wiring for future components (see Project Plans) shall be installed as part of this contract.

Conductors rated 600 volts and less, including service entrances, shall conform to UL 854, Type THW, THHW, THHN.  Conductor size and number of conductors in each cable shall be as indicated.  Cable shall be color coded.  Conductor identification shall be provided within each enclosure where a tap, splice, or termination is made.  Conductor identification shall be by color-coded insulated conductors, plastic-coated self-sticking printed markers, colored nylon cable tiles and plates, or heat shrink type sleeves.  Control circuit terminations shall be properly identified.  Conductors shall be solid copper.

2.1.5	Enclosures

Fabricate panels and enclosures of 16-gage furniture-grade steel or 6063-T5 extruded aluminum alloy, totally enclosed on all sides, with hinged door and keyed lock with manufacturer’s standard shop-painted finish.

Provide UL listed panels for use with line voltage devices.

Provide nylon based double screw type terminal blocks with spare terminal for extra wiring.

2.1.6	Sensor/Instrumentation Power Supply

All sensors and instrumentation shall be supplied with an internal or external power supply to convert from AC to the required DC voltage (or as otherwise required), as necessary to power the sensors.

2.2	PRESSURE INSTRUMENTATION

2.2.1	General

See Section 15060, “Valves and Piping Appurtenances”, for additional products related to pressure instrumentation in piping.

2.2.2	Pressure Sensor/Transmitters

.	The pressure transmitter for measuring the pressure of the Recharge Bed Header (PX-RB1), shall be a pressure transducer with stainless steel and Viton wetted parts.  The unit shall generate a 4-20 mA output signal with an accuracy of 0.25% and be loop powered.  The operating temperature shall be -10(C to 70(F.  Provide all appurtenances (such as vent tubes and moisture traps) recommended by the manufacturer and/or supplier.

The pressure sensor/transmitter shall be KPSI Model 720 or approved equal.  The supplier shall coordinate the model number with the manufacturer as necessary to meet the functional requirements of this Specification.  The monitored pressure range shall be 0 – 25 psig with a 200 psig burst pressure rating.  The unit shall be supplied with a ¼” male NPT pressure port end cap to allow installation on the header piping as shown on the Project Plans.

2.3	WATER FLOW INSTRUMENTATION

2.3.1.	Turbine Flow Meter

The flow transmitter indicators (FXI-RB2) shall be an in-line mounted device wherein the liquid pressure drives the turbine rotor rate of rotation proportional to the volumetric flow rate.  The Rotor’s rotation is magnetically coupled to a hermetically sealed indicator/transmitter.

The device shall be capable of measuring flow in wastewater.  The pressure rating of the unit shall be 150 psi or greater.  The case shall be constructed of epoxy coated cast iron.  The measuring chamber shall be polyethersulfone and the rotor shall be polyamid.  The flanges shall be cast iron with EPDM o-rings.  The register housing shall be bronze.  The pressure drop shall be <1.1 psi at 150 gpm.  The accuracy of the unit shall be ± 1.0% of the rate with a repeatability of ± 0.25% of the rate.  The power supply to the unit shall be 30 VDC, 15-20mA.  The unit shall include a local flow rate display.

The unit shall include a converter to convert the pulsed signal from the flow meter to a 4-20mA output signal that is proportional to the flow rate.

The unit shall be a Niagara WPX Series, Model 221.

2.4	MISCELLANEOUS DEVICES

2.4.1	Valve Position Indicators

Each electrically actuated valve shall include position indication.  Modulated flow control valves shall include a 4–20 mA position transmitter to indicate the actual position (percent open) of the valve.  The position transmitters shall be as manufactured by ASAHI/America or approved equal compatible with the approved valve actuator.  The valve shall modulate as necessary to maintain the percent open as set by the operator in the HMI.

2.5	CONTROL AND COMMUNICATIONS SYSTEM INTEGRATION

All flow, pressure, automated valve operation, and valve position indicator control and monitoring shall be integrated into the existing water treatment Supervisory Control and Data Acquisition/Human Machine Interface (SCADA/HMI) system to address the required system control and communications.  All monitoring and controls shall be through the existing or similar display screens within the existing system.  Alarm functions shall perform as described in this specification section and on the Contract Drawings.  The existing display screens in the existing SCADA/HMI system may be modified to accommodate the new monitoring and controls, or an additional screen may be added for the Recharge Bed components.

2.8.1	Enclosures

Provide NEMA 4 or better enclosures for outdoor use.  The panel dimensions shall be selected by the control system supplier to be of sufficient size to enclose all required splices and or components.

The control panels shall be accessed by a main door which shall be equipped with a lockable handle.

PART 3	EXECUTION

3.1	INSTALLATION

Examine areas and conditions under which electric control systems are to be installed. All necessary programming documentation will be made available to the Contractor.  All control work was previously completed by Kruse Controls of Baltimore, MD.

Do not proceed with work until unsatisfactory conditions have been corrected in a manner acceptable to the installer.  Protect and carefully store all equipment and materials to prevent damage before and during installation.  Replace damaged or defective items.

Install instrumentation principally as shown on the drawings.  Provide all mounting hardware and cables required to install instruments and controls and for the system to operate as described in the plans and specifications.  Install the instrumentation, controls, panels and all appurtenances and accessories in accordance with the installation instructions furnished by the manufacturer.  The equipment shall be installed by workmen thoroughly experienced in installation of such equipment in accordance with manufacturer’s installation instructions.

Certain products specified in this section are for installation in process and other piping; installation of such products shall be in accordance with Section 15060, “Valves and Piping Appurtenances.”  Electrical work shall be as specified in Division 16 Sections.

3.2	WIRING

Wiring shall conform to process control panel wiring codes with wire numbers on each terminating point of a wire and wire colors conforming to standard process control codes.  Wire colors shall be as follows:  black - power, white - neutral, red - control, yellow - remote powered, blue - dc power.  All interconnecting wires shall be brought to terminal boards.

The control devices and instruments shall be grouped by function on the panel and placed in a neat, orderly, and aesthetically pleasing arrangement to facilitate an understanding of the control and its operation.  All components shall be marked with engraved plastic plates (black on white background) on or near them.

The term “control wiring” is defined to include providing wire, conduit, and miscellaneous materials as required for mounting and connecting electric control devices.

Install complete control wiring system for electric control systems.  Provide multi-conductor instrument harness (bundle) in place of single conductors where number of conductors can be run along common path.  Fasten flexible conductors bridging cabinets and doors, neatly along hinge side, and protect against abrasion.  Tie and support conductors neatly.

Number-code or color-code conductors, appropriately for future identification and servicing of control system.

Furnish labels appropriate for the use.  Install labels onto equipment and/or onto panel door to properly identify the function of the device.

All wiring shall be kept trained into wireways or gutters, unless specifically approved by the RE.

All terminals shall be clearly and permanently labeled.

Contractor shall make all wiring terminations and ensure that modified control (and other) panels are fully operational and functional prior to the completion of the project.

3.3	GENERAL SYSTEM FUNCTIONAL REQUIREMENTS

3.3.1	Process Control System

The process control system (which includes but is not limited to the PLCs, servers, HMIs, Remote Interface Software, and related instrumentation and loads) shall be modified, by the Control System Supplier to perform the operations described in this Section.  The process system shall function as described on the Contract Drawings.

3.4	SYSTEM TESTING AND CALIBRATION

After the instrumentation has been installed and the programming has been modified, the system shall be calibrated, tuned and tested to demonstrate the capability of the system to perform as described herein and on the drawings.  The system and all related software shall be operated and exercised for a duration of thirty (30) days to show that it has been properly installed and calibrated and that performance is entirely acceptable to the RE and meets requirements of these specifications.

If any component or the system in its entirety fails to conform to any and all of the specifications and the performance test of the system shows deficiencies in any aspect of the requirements of this specification, the Control System Supplier and/or manufacturer shall make such system corrections, alterations or adjustments as are necessary to meet the requirements.  The operating tests shall then be repeated and the results reevaluated.

The testing shall be completed to the satisfaction of the RE.

3.5	PID LOOP TUNING

The control system supplier shall provide the necessary equipment, personnel, and services necessary to tune the PID loops implemented by the control system.  Tuning shall not be considered complete until the RE is satisfied that the system will operate in a stable manner under various modes and conditions of operation.

The control system supplier shall, at a minimum, tune the system PID loops at the following times:

a	As necessary prior to and During Initial System Testing (Must attain sufficient stability)

b	Once after completion and acceptance of System Testing (Adequate performance must be obtained at this time)

c.	Once at the request of the Owner during the first year of operation.

.	The control system supplier shall tune the PID loops so that the performance meets the intent of the specifications and satisfaction of the RE.

3.6	OWNER TRAINING IN OPERATION AND MAINTENANCE OF SYSTEM

The Contractor shall provide the copies of the Operation and Maintenance Manuals specified under Part 1.4.6. of this Section prior to conducting the training sessions described below. The O&M manuals shall be submitted to the RE for review a minimum of one week prior to conducting the training session.

The Contractor, Control System Supplier and manufacturer representatives shall provide a minimum of one 4 hour day of training for RE and his designated representatives.  The training shall review the operation of each piece of equipment and provide the RE with a thorough understanding of the operation of the System, the operation and maintenance of its components, and the fine tuning and adjustment of the system components.

3.7	POST BREAK-IN ADJUSTMENTS

After the system has been accepted by the RE and has successfully operated for one month without a mechanical or electrical failure or breakdown due to normal operation, the Control System Supplier shall return to modify and adjust logic implemented by the programmable controller in accordance with the directions of the RE.  The Control System Supplier shall provide two days of service at the site to implement and trouble shoot these adjustments.

END OF SECTION