July 22, 1994

Contract #TW0592

SPECIAL  STANDARD SPECIFICATION

SECTION 02665-S

EXTERIOR WATER DISTRIBUTION

Page

PART 1 - GENERAL

1.01	Description Of Work	2

1.02	References	2

1.03	Submittals	4

1.04	Quality Assurance	4

PART 2 - PRODUCTS

2.01	Pipe And Joints	4

2.02	Fittings	5

2.03	Valves	5

2.04	Fire Hydrants	7

2.05	Pressure Reducing Valves	7

2.06	Air And Vacuum Valves	7

2.07	Concrete	7

2.08	Tapping Saddles	7

2.09	Corporation Stops	8

2.10	Thrust Restraints	8

PART 3 - EXECUTION

3.01	Pipe Laying	8

3.02	Location Of Water And Sewer Lines	9

3.03	Thrust Restraints	10

3.04	Valves	10

3.05	Valves Boxes	10

3.06	Valve Stem Extensions	11

3.07	Fire Hydrants	11

3.08	Indicator Posts	11

3.09	Pressure Reducing Valves	11

3.10	Air And Vacuum Valves	12

3.11	Connections To Supply Mains	12

3.12	Service Lines	12

3.13	Flushing	12

3.14	Hydrostatic Testing	13

3.15	Disinfecting	14

3.16	Storage	14

SPECIAL  STANDARD SPECIFICATION

SECTION 02665-S

EXTERIOR WATER DISTRIBUTION

PART 1 - GENERAL

1.01	DESCRIPTION OF WORK

A.	This section shall apply to the materials and operations required for the installation of exterior water distribution including fire lines and exterior lines extending from the main to a building (service lines).

B.	The extent of the work is indicated on the contract drawings.

C.	Related Work:  Refer to the following sections for related work:

1.	Division 2, Section "Earthwork".

2.	Division 3, Section "Cast-in-Place Concrete".

3.	Division 9, Section "Painting".

4.	Division 15, Section "Automatic Sprinkler Systems".

1.02	REFERENCES

A.	American National Standards Institute (ANSI)

A21.11		Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings

A21.53		Ductile-Iron Compact Fittings, 3 in. Through 16 in., for Water and 					Other Liquids

B1.20.1	Pipe Threads, General Purpose (Inch)

B16.1		Cast Iron Pipe Flanges and Flanged Fittings

B16.3		Malleable Iron Threaded Fittings

B16.4		Gray Iron Threaded Fittings

B.	American Society of Testing Materials (ASTM)

A48		Specification for Gray Iron Castings

A53		Standard Specification for Pipe, Steel, Black and Hot-Dipped Zinc 					- Coated Welded and Seamless (Replaces A120)

A536		Specification for Ductile Iron Castings

B62		Specification for Composition Bronze or Ounce Metal Castings

B88		Specification for Seamless Copper Water Tubes

D2000		Classification System for Rubber Products in Automotive 						Applications

D2774		Recommended Practice for Underground Installation of 						Thermoplastic Pressure Piping

F477		Specification for Elastomeric Seals (Gaskets) for Joining Plastic 					Pipe

C.	American Water Works Association (AWWA)

C104		Cement-Mortar Lining for Ductile-Iron Pipe and Fittings for Water

C105		Polyethylene Encasement for Ductile-Iron Piping for Water and 					Other Liquids

C110		Ductile-Iron and Gray-Iron Fittings, 3 in. Through 48 in., for Water 				and Other Liquids

C111		Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings

C115		Standard for Flanged Ductile-Iron Pipe with Threaded Flanges

C151		Ductile-Iron Pipe, Centrifugally Cast, for Water and Other Liquids

C153		Ductile-Iron Compact Fittings, 3 in. Through 16 in., for Water and 					Other Liquids

C500		Gate Valves for Water and Sewerage Systems

C502		Dry-Barrel Fire Hydrants

C504		Standard for Rubber-Seated Butterfly Valves

C509		Resilient-Seated Gate Valves for Water and Sewerage Systems

C600		Standard for Installation of Ductile-Iron Water Mains and Their 					Appurtenances

C651		Disinfecting Water Mains

C800		Underground Service Line Valves and Fittings

C900		Polyvinyl Chloride (PVC) Pressure Pipe, 4 in. Through 12 in., for 					Water Distribution

D.	National Fire Protection Association (NFPA)

24		Standard for the Installation of Private Fire Service Mains and 					Their Appurtenances

1.03	SUBMITTALS

A.	General:	Submit the following in accordance with conditions of Contract and Division 1, Section "Descriptive Submittals".

B.	Product Data:	Submit product data, or manufacturer's specifications including  laboratory test reports and other data to show compliance with specifications (including specified standards).

C.	Test Reports:	Submit test reports conducted on shop- and field-bolted and welded connections.  Include data on type(s) of tests conducted and test results.

1.04	QUALITY ASSURANCE

A.	Codes and Standards:   All work shall comply with the applicable portions of the most current edition of the Uniform Plumbing Code.

B.	The materials and practices comprising the work shall conform to this and other referenced standard specifications.  Where this specification conflicts with the requirements of another referenced specification, this specification shall prevail.

C.	All materials used shall not contain any asbestos fibers.

D.	All persons performing or supervising testing shall be qualified by either training or experience to perform such tests.

PART 2 - PRODUCTS

2.01	PIPE AND JOINTS

A.	Distribution lines and service lines, 4" (101.6 mm and larger, shall be polyvinyl chloride (PVC) unless otherwise indicated on the contract drawings.  Fire protection lines from the PVC to the building shall be as specified in Division 15, Section "Automatic Sprinkler Systems".  All pipe shall be permanently marked to allow identification of type and class and shall conform to the following material requirements:

1.	Ductile Iron Pipe:  4" (101.6 mm) Class 51 minimum, 6" (152.4 mm) and larger Class 50 minimum or as indicated on the contract drawings, conforming to AWWA C151, with rubber-gasket joints conforming to AWWA C111, and cement-mortar lining conforming to AWWA C104.  Flanged pipe shall conform to AWWA C115.

2.	Polyvinyl chloride pipe (PVC) shall be Class 150 (DR 18) minimum or as indicated on the contract drawings, cast-iron pipe equivalent outside diameter, conforming to AWWA C900, with bell and spigot push-on joints and elastomeric gaskets conforming to ASTM F 477.

B.	Service Lines 3" (76.2 mm) and smaller shall conform to the applicable provisions of AWWA C800, and shall conform to the material requirements for one of the following piping materials, as indicated on the contract drawings:

1.	Steel Pipe:  Standard weight, galvanized, and wrapped Type E or S, conforming to ASTM A 53 Rev. B, with general purpose pipe-thread joints conforming to ANSI B1.20.1.

2.	Copper Tubing:  Type K, soft-annealed temper, conforming to ASTM B 88.

3.	Ductile Iron Pipe:  Conforming to the requirements of article 2.01 A for ductile iron pipe.

2.02	FITTINGS

A.	Fittings for mainlines 4" (101.6 mm) and larger shall be gray iron or ductile iron, 250 psi (1 723.69 kPa) pressure rating minimum, mechanical joint or flange joint, conforming to AWWA C110, with cement-mortar lining conforming to AWWA C104.  Mechanical joint fittings, with rubber-gasket joints conforming to AWWA C111 shall be used in all buried installations.  Flanged fittings shall be used in above-ground installations, and inside underground structures, such as valve pits and vaults.

B.	Fittings for service lines 3" (76.2 mm) and smaller shall conform to the applicable requirements of AWWA C800 and the following requirements:

1.	Steel pipe fittings shall be galvanized cast-iron conforming to ANSI B16.4 or galvanized malleable iron conforming to ANSI B16.3.

2.	Copper pipe fittings shall be brass or bronze body with compression connections or flared compression joints.

3.	Ductile iron pipe fittings shall be cast or ductile iron.

C.	Special couplings, reducers, flares, saddles, rings, caps, wyes or other as specified on the drawings shall be gray iron or ductile iron unless otherwise specified or shown, 250 psi (1 723.69 kPa) minimum pressure rating, mechanical or flanged joints conforming to AWWA C110 and shall be cement mortar lined according to AWWA C104.

2.03	VALVES

Distribution, fire and service line valves shall conform to the following requirements:

A.	Gate valves shall have 200 psi (1 378.95 kPa) minimum working pressure, sizes 3" (76.2 mm) through 12" (304.8 mm), double disk, parallel seat, iron body, bronze mounted, non-rising stem, "O"-ring stem seals, conforming to AWWA C500.  Valves shall open counterclockwise.  The operating nut shall be standard 2" (50.8 mm) square with an arrow cast in the metal indicating the direction of opening.  End connections shall be mechanical joints conforming to AWWA C111, unless otherwise indicated.  Valves installed in pits and vaults shall be hand wheel-operated with flanged end connections conforming to ANSI B16.1, Class 125.  Valves installed in fire lines shall be listed by Underwriter's Laboratories (UL) in accordance with NFPA 24.  Valves to be fitted with indicator posts shall be equipped with indicator post flanges.  Gate valves shall be M-H DRESSER, MUELLER or approved equal.

B.	Resilient seat gate valves 12" (304.8 mm) and smaller shall conform to AWWA C509.  The valve shall open when turning counterclockwise.  The stem shall be the non-rising type with inside screw and shall contain "O"-ring seals.  All valve end joints shall be mechanically connected and O-ring retainer shall be secured with nuts and bolts.  Brass and bronze parts shall conform to AWWA C509.  The resilient seat shall be mechanically retained or bonded to the gate or wedge.  Resilient seat gate valves shall be M-H DRESSER, MUELLER or approved equal.

C.	All valves 2" (50.8 mm) and smaller shall be of "O"-ring sealed ball or gate-operating, full-opening port type design.  The valve shall have a cast bronze body, as per ASTM B 62.  The plug or key shall be cast bronze, as per ASTM B 62, machined and/or deburred to create a smooth, true surface and assure a positive, durable seal.  Valves shall be MUELLER or FORD or approved equal.

1.	The inlet and outlet connections shall be tightened by a one-way gripper band or a compression nut.  A positive seal shall be obtained by a replaceable "O"-ring for use with the gripper band system or a beveled BUNA-N gasket, as per ASTM D 2000, for use with the compression nut system.

2.	Curb boxes shall be installed with all valves 2" (50.8 mm) and smaller and shall be MUELLER H-10306, FORD EA 2-25-50, or approved equal.  Curb boxes shall be telescopic type with heavy cast-iron arch pattern base, steel upper section, and heavy cast-iron lid with a bronze bushed, bronze standard waterworks counter-sunk pentagon nut and shall be installed with a 12" x 12" x 4" (304.8 mm x 304.8 mm x 101.6 mm) concrete collar.  Curb boxes shall be adjustable from 18" to 30" (457.2 mm to 762.0 mm) and held at the desired depth by a strong phospor bronze opening.  Upper sections of these boxes must be at least 1-1/4" (31.75 mm) to accept a shut-off rod.  Boxes shall be coated inside and out with a tar-based enamel for corrosion resistance.

D.	Indicator posts shall have a cast-iron body, 1-1/4" (31.75 mm) square operating nut, lockable operating wrench, with "OPEN" and "SHUT" targets appearing in full view when the valve is fully open or closed.  Base shall be flanged and shall bolt onto the indicator post flange provided on top of the valve.  Posts shall be listed by UL and shall be a DRESSER M & H Style 83, MUELLER A-20800 or A-20805, KENNEDY Figure 541 vertical type, or approved equal.

E.	Butterfly valves 14" (355.6 mm) and larger shall be rubber-seated, iron body, short body flanged, Class 150B, conforming to AWWA C504 for valves 14" (355.6 mm) and larger.  Valves shall be installed so that the disc rotates about a horizontal axis.  Operator shall be manual, side-mounted, with standard 2" (50.8 mm) square operating nut, opening counterclockwise.  Butterfly valves shall be MUELLER Lineseal III, KEYSTONE Figure 47 or 504, M-H DRESSER 450, AMERICAN Darling, PRATT, KENNEDY or approved equal.

F.	Valve boxes shall have a gray cast-iron ring and cover as designated on the standard drawing conforming to ASTM A 48, Class 25C.  The word "WATER" shall be cast onto the top of the cover in raised letters.

2.04	FIRE HYDRANTS

Fire hydrants shall be UL and FM approved and have a cast or ductile iron body, traffic, dry barrel, post type, 150 psi  (1 034.21 kPa) working pressure, with two drain outlets constructed of bronze, conforming to AWWA C502.  Main valve shall be compression type, 5-1/4" (133.35 mm) in diameter.  Hydrants shall have one 4-1/2" (114.3 mm) pumper connection and two 2-1/2" (63.5 mm) hose connections, with National Standard Fire Hose Coupling Screw Threads.  Operating nut shall be pentagonal, 1-1/2" (38.1 mm) point to flat, opening counterclockwise.  Show connection shall be 6" (152.4 mm) mechanical joint.  Hydrants shall be capable of being field lubricated.  Normal bury shall be 4 to 4-1/2 feet (101.6 mm to 114.3 mm) minimum. Fire hydrants shall be MUELLER A-423 Centurion, GUARDIAN K-81A, M-H DRESSER 129T Model, CLOW F2500, WATROUS Pacer 100, or approved equal.

2.05	PRESSURE REDUCING VALVES

Pressure reducing valves (PRV) shall be cast-iron body, flanged end connections, globe pattern, single-seated, pilot-controlled, psi diaphragm type, Class 125 pressure rating, adjustable from 15 to 75 psi (103.42 to 517.11 kPa) and shall operate hydraulically.  PRV shall be a CLA-VAL Clayton Model 90-01 Series, size as designated on the contract drawings, or approved equal.

2.06	AIR AND VACUUM VALVES

Air and vacuum valves shall have a cast-iron body, stainless steel float, with baffle, sizes 1/2" through 3" (12.7 mm through 76.2 mm), as designated on the contract drawings.  Valves shall be APCO Model Series 140, with NPT threaded outlet, or approved equal.  Ring and cover for valve pit shall be gray cast-iron conforming to ASTM A 48, Class 30 minimum, and shall be a NEENAH No. R-1910-A or an approved equal.  Cover shall have the word "WATER" cast onto it in raised letters.

2.07	CONCRETE

Cast-in-place concrete for use in concrete thrust blocks, valve box and indicator post collars, and other concrete structures required by the contract drawings, shall conform to the requirements of Division 3, Section "Cast-in-Place Concrete".

2.08	TAPPING SADDLES

Tapping saddles shall have a cast-iron, ductile iron or bronze body, stainless steel or bronze straps, nuts, bolts and washers.  Gaskets shall be vulcanized elastomeric rubber or synthetic rubber compound.  Saddles shall be compatible with MUELLER threaded inlet or approved equal.  Saddles used on PVC pipe shall be double-strap type.

2.09	CORPORATION STOPS

Corporation stops shall have a bronze body, MUELLER thread inlet by compression or flared outlet, 3/4" to 2" (19.05 mm to 50.8 mm), conforming to the applicable requirements of AWWA C800.  Compression connection outlets shall be provided with a stainless steel liner.

2.10	THRUST RESTRAINTS

Cast-in-place concrete blocking, clamps and tie rods, shall conform to the standard drawing.  Corrosive steel or cast-iron hardware shall be fully coated with asphalt or plastic varnish.

PART 3 - EXECUTION

3.01	PIPE LAYING

A.	General:  Provide water pipe of the size, type and class specified and install at the locations and to the elevations and grades indicated on the contract drawings.

B.	Pipe installation shall be in accordance with the applicable provisions or requirements of the following referenced handbooks and standard specifications:

1.	Ductile iron pipe shall conform to AWWA C600.  Where indicated on the contract drawings, pipe shall be encased in polyethylene film according to AWWA C105.

2.	Plastic pipe shall conform to UNI-B-3 "Recommended Practice for the Installation of Polyvinyl Chloride (PVC) Pressure Pipe", Uni-Bell PVC Pipe Association, per AWWA C600, and Uni-Bell "Handbook of PVC Pipe".

3.	Copper tubing shall conform to CDA "Copper Tube Handbook".

4.	Polyethylene service line piping and tubing shall conform to ASTM D 2774

C.	Upon arrival at the job site, each section of pipe shall be inspected for damage and defects, and for compliance with the applicable piping materials products requirements listed in Part 2 of this specification.  Defective sections of pipe may be marked by the Sandia Delegated Representative (SDR).  Any sections of pipe found to be defective shall be immediately removed from the job site and shall be replaced by the Contractor.

D.	Immediately prior to laying, each pipe section shall be visually inspected for defects or damage.  Any damaged or defective pipe section shall not be used.  Each pipe section shall be cleaned so that the interior and joining surfaces of the pipe are free of soil and debris.

E.	Pipe shall be laid on a smoothly graded prepared subgrade soil foundation true to alignment and grade as indicated on the contract drawings.  The allowable vertical and horizontal tolerance from drawing elevations and alignment shall be ( 2" (( 50.8 mm).  Bell holes shall be hand-excavated so that the bottom of the pipe is in continuous contact with the surface of the prepared subgrade material.  Any pipe that has its grade or joints disturbed after laying shall be taken up and relaid.  At times when pipe laying is not in progress, the open ends of the pipe shall be closed by a watertight plug.  Pipe shall not be laid in standing water or when trench or weather conditions are deemed unsuitable by the SDR.  If conditions warrant, the inspector may require that the pipe be anchored to prevent floating.

F.	Minimum depth of cover for water lines shall be 3 feet (914.4 mm) from the top of pipe to finished grade unless otherwise indicated on the contract drawings.

G.	When it is necessary to deflect ductile iron pipe for changes in horizontal or vertical alignment, the amount of deflection shall not exceed 2/3 of the manufacturer's recommended maximum deflection.  A fitting or several shorter lengths of pipe shall be used when necessary.  PVC pipe shall not be deflected at the joints.

H.	All nuts and bolts utilized in underground pipe connections shall be stainless steel, high-strength, cast-iron or high-strength, high-grade steel and shall be of  the proper size and type for the application in which they are utilized.  All iron or high-strength steel bolts shall be cadmium-zinc plated or coated with bituminous material prior to backfilling.

I.	Joints

1.	Push-on-Joints:  Immediately prior to making the joint, the rubber gasket shall be removed and cleaned, the groove cleaned, the gasket replaced, and the bell and spigot ends thoroughly cleaned and lubricated with a suitable sterile soft vegetable soap compound.  Field-cut plastic pipe sections shall be beveled for joining as recommended by the pipe manufacturer.

2.	Mechanical Joints:  The socket and plain ends shall be thoroughly cleaned immediately prior to making the joint.  Wash the seating surfaces and the rubber gasket with a soapy solution.  Seat the plain end fully in the socket before slipping the gasket into the socket.  The joint shall be kept straight during assembly.  If a joint deflection is required, make the deflection after assembly, but before tightening bolts, tighten nuts 180 degrees apart in pairs.  Alternate pairs until all nuts are within the manufacturer's recommended range of torque.  The Contractor shall have a torque wrench on hand at the work site so that the Sandia National Laboratories (SNL) Inspector may verify tightening torques on any joint.

3.	Flanged Joints:  Clean the flanged ends to be joined immediately prior to joining.  Only one gasket shall be permitted in a flange joint.  Nuts shall be tightened similar to mechanical joints to within the torque range recommended by the pipe manufacturer.

3.02	LOCATION OF WATER AND SEWER LINES

A.	Mains:  Water and sewer mains running parallel shall be laid at least 10 feet (3.048 m) apart horizontally, with the water main at a higher elevation than the top of the sewer line.  Water and sewer mains shall be laid in separate trenches in all cases.  Where water and sewer mains are laid closer than 10 feet (3.048 m) or where they are crossing, the bottom of the water main shall be at least 18 inches (45.72 cm)  12" (304.8 mm) higher than the top of the sewer line, otherwise, the sewer line shall be of pressure class pipe, or shall be encased in concrete as indicated on the contract drawings, within 10 feet (3.048 m) either side of the water main.

B.	Service Lines:  Water and sewer service lines shall not be laid in the same trench, unless the bottom of the water line, at all points, is at least 12" (304.8 mm) above the top of the sewer line, and the water line shall be laid on a solid shelf excavated at one side of the common trench.  Where water and sewer service lines cross, the water line shall be at least 12" (304.8 mm) higher than the sewer.

3.03	THRUST RESTRAINTS

A.	General:  Provide thrust blocking or rigid joints at all tees, plugs, caps, bends, and reducers of the types, sizes, and configurations, and at the locations indicated on the contract drawings.  In the event that a line must be returned to use in less than 4 hours, thrust restraint shall be provided with a rigid mechanical joint restraint, and concrete blocking shall also be installed with the joint restraint system.

B.	Concrete blocking shall be installed in accordance to the requirements of Division 3, Section "Cast-in-Place Concrete".  Blocks shall be placed in the general shape and to the minimum dimensions indicated on the standard drawings, and shall be placed between the fitting and the undisturbed wall of the trench.  Concrete shall be placed so that it does not make contact with any bolts or nuts on the fittings.  Pipe shall not be flushed, pressurized, or otherwise disturbed, until the new concrete blocking has reached its initial set or 4 hours.

C.	Mechanical joint restraints shall include a restraining mechanism which, when actuated, imparts multiple wedging action against the pipe, increasing its resistance as the pressure increases.  Flexibility of the joint shall be maintained after burial.  Glands shall be manufactured of ductile iron, conforming to ASTM A 536.  Restraining devices shall be suitable for the type of pipe material used and shall be of ductile iron heat-treated to a minimum hardness of 370 BHN.  Dimensions of the gland shall be such that it can be used with the standardized mechanical joint bell and tee-head bolts conforming to ANSI/AWWA C111/A21.11 and ANSI/AWWA C153/A21.53 of the latest revision.  Twist-off nuts shall be used to ensure proper actuating of the restraining devices.

The mechanical joint restraint device shall have a working pressure of at least 250 psi (1 723.69.25 kPa), with a minimum safety factor of 2:1 and shall be EBAA Iron, Inc., MEGALUG or equal.

3.04	VALVES

Gate and butterfly valves shall be installed at the locations indicated and as detailed on the contract drawings, and in accordance with AWWA C600.  No change in the vertical or horizontal alignment of the pipe shall be allowed at connections to the valve.  Valves shall be installed in accordance with  the manufacturer's recommendations.

3.05	VALVES BOXES

Install valve boxes over all gate and butterfly valves as detailed on the contract drawings, and in accordance with AWWA C600.  Boxes shall be installed plumb and true, and shall be centered on the valve operating nut.  The weight of the valve box shall not bear upon the control valve or pipeline.

3.06	VALVE STEM EXTENSIONS

Where the valve operating nut is at a depth greater than 2 feet (609.6 mm) below the valve box cover, an extension stem shall be installed in the box with the required size square wrench nut.  Extension stems shall be equipped with a minimum of one stem guide or stem guides at intervals not exceeding 10 feet (3.048 m), and shall be affixed to the interior of the valve box.  Stem guides and extensions shall be manufactured for the application for which they are utilized or they shall be approved by the SDR.

3.07	FIRE HYDRANTS

Install fire hydrants at the locations indicated and as detailed on the contract drawing, and in accordance with AWWA C600.  Hydrants shall be set plumb and true to the elevations indicated, with the center of the lowest nozzle at least 16" (406.4 mm) above surrounding finished grade.  The 4-1/2" (114.3 mm) pumper nozzle shall face toward the nearest street, road, drive or parking area or as directed by the SDR.  Not less than 8 cubic feet of crushed rock or gravel, 1/2" (12.7 mm) mean particle size, well-graded, not more than 5% by weight passing #100 sieve, shall be placed around the shoe of the hydrant so that drainage from the hydrant shall run readily from the drain ports and into the rock.  The concrete thrust block at the hydrant shall not block the flow of drainage water from the drain ports.  Each hydrant shall be connected to the main by a 6" (152.4 mm) lateral pipe controlled by a 6" (152.4 mm gate valve as indicated on the contract drawings.  A concrete collar shall be placed around the hydrant barrel at ground level as indicated.  Hydrants shall be painted with one coat of red oxide paint and two finish coats of SINCLAIR "Yellow Traffic-Lac" above grade; and with two coats of asphalt or plastic cement below grade.

3.08	INDICATOR POSTS

Install indicator posts over valves on fire protection lines at locations indicated and as detailed on the contract drawings.  Posts shall be bolted to the flange at the top of the valve and shall be installed plumb and true to the elevations indicated.  A concrete collar shall be painted around the post at ground level as detailed.  Posts shall be painted above grade with one coat of red oxide paint and two finish coats of SINCLAIR No. 390 "Fire Protection Red" where installed on fire protection lines, or two finish coats of Sinclair "Yellow Traffic-Lac" where installed on domestic water lines.  Below grade, posts shall be painted with two coats of asphalt varnish.

3.09	PRESSURE REDUCING VALVES

Install pressure reducing valves in valve vaults at locations and elevations indicated and as detailed on the contract drawings.

3.10	AIR AND VACUUM VALVES

Install air and vacuum (A/V) valves at high points on the water line where indicated and as detailed on the contract drawings.  A/V valves shall be installed in precast reinforced concrete pipe vaults with appurtenant piping, fittings and valves as detailed in the drawings.  Provide water meter type cover with vent and concrete collar as detailed.

3.11	CONNECTIONS TO SUPPLY MAINS

A.	Service connections to existing or new mains shall be made with fittings suitable for the particular conditions encountered and in a manner acceptable to the SDR.  Connections shall be made by cutting the supply main and inserting a standard tee, by pressure-tapping using a tapping sleeve and valve, or by saddle and corporation stop.

B.	All equipment used for drilling, tapping and installation of corporation stops shall be subject to approval by the SDR.

C.	Main lines may be direct-tapped when specifically detailed on the contract drawings.

D.	Saddles used in tapping PVC pipe shall be of the bronze double-strap type or stainless steel felt band type.

E.	Corporation stop taps shall be located at the connection to the main.  When more than one tap in a main line is necessary to deliver the required flow, they shall be staggered around the circumference of the pipe (not in a straight line) and be at least 12" (304.8 mm) apart as measured along the length of the pipe.

F.	Pipe coupons shall not be left inside the water main when the tapping method is used.  All pipe coupons removed shall be turned over to the SDR.

3.12	SERVICE LINES

Install service lines at the locations designated on the contract drawings.  Copper tubing shall be cut by using cutters designed for that purpose.  Bends in copper tubing shall be made using brass fittings or by using proper tubing benders.  Bends in polyethylene tubing shall be made only with the appropriate fittings, and shall not be made by deflecting the tubing.

3.13	FLUSHING

Prior to disinfecting the water lines, the Contractor shall flush all new installations in accordance with an approved flushing plan submitted by the Contractor.  If no fire hydrants or other convenient outlets for flushing are available, the Contractor shall install flush points at no additional cost to SNL.  Flushing shall be of sufficient magnitude to flush foreign material out of the lines, valves and hydrants.  All new valves and hydrants shall be partially operated several times during flushing to dislodge foreign material.  During flushing operations, all valves or connections to existing systems shall be closed and back flow preventors or other approved equipment installed at the source to prevent contamination of existing systems.  Contractor shall protect existing site improvements during flushing operation.  The flushing velocity shall be a minimum of 2.5 fps (762 mm/s).

3.14	HYDROSTATIC TESTING

WARNING:	The testing methods described in this section are specifically for water pressure testing.  These procedures are not permitted for air pressure testing due to the serious safety hazards involved.

A.	New water line installations shall be hydrostatically tested in accordance with AWWA C600 for ductile-iron main,  AWWA M23 for PVC mains, and NFPA 24 for Private Fire Service mains and their appurtenances.  The SDR or his field representative (construction observer or inspector) shall be present at all times for the duration of the test.

B.	All temporary plugs, taps, thrust restraints, gauges, and other necessary testing equipment must meet the same nationally recognized standards as listed in Part 2 - Products.  They shall be provided by the Contractor and shall be subject to approval by SNL, except that SNL may elect to provide the gauges used in the test.

C.	New lines shall be tested without being connected to existing lines.

D.	Test pressure for new lines excluding fire lines, which run from the Post Indicator Valve (PIV) to the sprinkler riser, shall be 150 psi (1 034.21 kPa) or 1.5 times the normal working pressure of the line, whichever is greater.  In addition, test pressure for new fire lines, as defined above, shall be a minimum of 200 psi (1 378.95 kPa) or 50 psi (344.74 kPa) in excess of static pressures greater than 150 psi (1 034.21 kPa), per NFPA 24 Section 8-9.3.  Before applying the specified test pressure, air shall be expelled completely from the pipe, valves, and hydrants.  If permanent air vents are not located at all high points, the contractor shall install corporation cocks at such points so that the air can be expelled as the line is filled with water.  After all the air has been expelled, the corporation cocks shall be closed and the test pressure applied.  At the conclusion of the pressure test, the corporation cocks shall be removed and plugged or left in place at the discretion of the SDR.  Test duration shall be not less than 2 hours.  During the test, the test pressure shall not drop for lines less than 1000 feet (304.8 m) long.  For lines greater than 1000 feet (304.8 m) long, see article 3.14 E.  Each section of the new line between valves shall be tested individually to demonstrate that each valve will hold the test pressure.  In cases where a new main is being connected to an existing main without the installation of a new valve, the end of the new main shall be temporarily capped and restrained, and the test shall be performed on the new line.  Tests shall not be made with an existing main included in the test section.

E.	The allowable leakage rate for lines greater than 1000 feet (304.8 m) long shall be 11.65 gpd, per mile, per inch (.0008 m³/sec, per meter, per 25 mm) nominal diameter while maintaining the test pressure.  The new waterline may be accepted if the total test leakage is less than the calculated allowable leakage.  If the actual leakage is greater than the allowable leakage, the Contractor shall locate the leakage and make repairs as necessary at no additional cost to SNL.  The Contractor shall repeat the test until the leakage is within the specified allowance.  All visible leaks, regardless of the amount of leakage, shall be repaired.

F.	The Contractor shall submit a calculation and the data sheet to SNL for each test, showing all data and measured quantities, including the actual leakage, the location of each test section, and a calculation of the allowable leakage for the test section.  The test sheet shall be signed and dated by the Contractor's representative.  For dedicated Fire Protection lines complete and submit a Contractor's Material and Test Certificate for Underground Piping in accordance with the current NFPA 24.

3.15	DISINFECTING

New water main lines shall be disinfected after flushing using a method that generally follows the tablet method in AWWA C651.  (WARNING:  This procedure shall not be used on solvent-welded plastic or on screwed joint steel pipe due to danger of fire or explosion from the reaction of the joint compounds with the calcium hypochlorite.)  Granules shall be placed at the upstream end of the first section of pipe, at the upstream end of each branch main, and at 200 feet intervals.  The quantity of granules shall be in accordance with AWWA C651.  Liquid chlorine shall be used for solvent-welded plastic or screwed joint steel and shall be poured in the line as the line is being filled with water.

A.	After installation is complete, the main shall be filled with water at a rate such that water within the main will flow at a velocity no greater than one ft/sec (304.8 mm/sec).  Precautions shall be taken to assure that air pockets are eliminated.  This water shall remain in the pipe for at least 24 hours.  After the retention period, the main shall be flushed until chlorine measurements are no greater than the existing water system or is acceptable for domestic use.

B.	After the final flushing and before the water main is placed in service, a sample or samples shall be collected from the end of the line and shall be tested for bacteriological quality.  Samples shall be taken from the nearest existing water source including fire hydrants, spigots, or sinks.

3.16	STORAGE

A.	All plastic pipe shall be protected from sunlight for long-term storage.  Any plastic pipe showing discoloration may be rejected.

B.	Joint materials for pipe shall be stored in as cool and shaded a place as practicable, preferably at 70 degrees F or less.

END OF SECTION