# Emergency Management Program

DATE:     Sample

OPERATING UNIT:		GI Procedures							 OPERATING UNIT MANAGER:

| Mission Critical System | Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | If there is an interruption in operations due to loss of the Critical System, then: Assess the situation for: Action required: |
| --- | --- | --- | --- | --- |
| 1. Lighting (Emergency Lights Available) | Without lighting staff can not carry out their duties. | Facilities Management | Life Safety lighting will remain. Survey area for “extra” lighting requirements In the event of loss of Life Safety lighting, flashlights will be utilized to assist in evacuation Purchase ample supply of batteries Staff should be informed of route of egress for patient evacuation in the event of an emergency. Route of egress should be free and clear of anything staff may trip over in dim lighting. Acquire Ancillary lighting | Determine if Life Safety lighting provides adequate coverage For prolonged outages, determine the need for ancillary lighting | Simulate Life Safety Lighting only to provide staff with advanced assessment of impact Deploy necessary identified ancillary lighting. Contact Facilities Management Service personnel in the event of a complete outage for provision of ancillary lighting for evacuation. |
| 2. Electrical Power (Generator Power Available) | Without power staff can not carry out their duties. | Facilities Management | Only Emergency Cases will be performed at Millenium changeover Emergency Red outlets are provided. Extension cords may be required for continuation of care. | Determine the extent of the outage and the projected length of the outage. Ensure staff identifies the exception outlets on Normal Power and that only non-critical systems should be plugged into these outlets. | Identify Emergency procedure in the event of a complete loss of power (Emergency and Normal Power). If complete loss occurs, evacuation procedures will be initiated. Contact Facilities Management if red Emergency Outlets do not suffice |
| 3. Steam Distribution | Possible loss of supplemental heat | Facilities Management | Make arrangements for supplemental heat Train staff on use of supplemental heating units | Assess placement of supplemental heating units | Contact Facilities Management for deployment of supplemental heating units |
| 4. Heating, Ventilation & Air Conditioning (HVAC) | Loss of heat or cooling could impact operations to the point that patient care is impacted | Facilities Management | Acquire supplemental heating or cooling units Train staff on use of supplemental heating or cooling units | Number of supplemental heating units required Placement of Heating or cooling units | Contact Facilities Management for deployment of supplemental heating or cooling units |
| 5. Room or Hood Exhaust | Loss of Isolation rooms | Facilities Management | Assess number of patients requiring isolation Acquire portable isolation unit(s) Train staff on use of portable isolation units | Isolation required? If so, can a portable unit be utilized? | Deploy portable isolation units |
| 6. Water Delivery | Loss of Domestic Water would impact delivery of patient care | Facilities Management Head Nurse GI Nurse | a) Assess requirements for domestic water in the event of a disruption | a) quantity of domestic water required | a) Deploy back up domestic water supply |
| 7. Water Conditioning Or Drinkability | Unable to use water for drinking or patient needs. | Facility Engineering and Materiel Management | Obtain signs saying "Water Unsafe to Drink" for sinks, etc. Provide locations for bottled water | Assess patient needs and extent of problem Assess use of nonpotable water for sanitary needs | Report failure to command center with assessment Establish bottled water center(s) with control |
| 8. Waste Stream (Sanitary, Solid, Liquid, & Biohazard) | Large amounts of “red bag” waste generated – requiring disposal | Head Nurse GI Nurse Facilities Management | Assess alternate storage off site for waste handling Ensure adequate staff to transport waste | Assess vendor readiness for waste handling Determine storage area for waste | Contact alternate vendor for back up waste handling Ensure timely pick up of waste from clinical areas |
| 9. Critical Supplies | An interruption in critical supplies could hinder patient care | Head Nurse GI Nurse SPD | List of critical supplies required Identify space for storage of supplemental critical supplies Establish vendor contacts | Assess patient workload prior to Dec. 31st, 1999 Acquire supplies in close proximity to GI Nurse | Monitor supplemental quantities of critical supplies Contact alternate vendors for such supplies |
| 10. Communi- cations (Telephone, Radio, Intercom, Nurse Call; etc.) | Loss of phones will impede the departments ability to communicate with medical center staff and external contacts for patient care issues | Chief, MAS Facilities Management GI Nurse Head Nurse | Assess critical items requiring communications (lab values), Code Blue, etc.… Obtain radio communications Train staff on proper operation | Number of radios, and placement | Deploy radios as back-ups Place radios at identified critical areas (lab, operators, work pool) |
| 11. VISTA & Other Computer Applications | 1. Loss of access to patient records | IRMS, Information Security Officer | Reduce GI schedule for period following Dec 31st, 1999 For all emergency clinic procedures, obtain hard copy charts List of critical contacts (Lab, Nursing, Respiratory) Train GI personnel on “manual” procedures for obtaining automated information (lab values, charts, etc.) | List of critical automated information for clinic operation Patient load anticipated for Dec 31st through following week | Only emergency procedures for Dec 31st, 1999 (possibly week of 1/3/00) Print out and storage of hard copy charts |
| 12. Alarms (Fire, Code Blue, Security, Medical Gases, Nurse Call, Refrigeration; etc.) | Inability to call or hear fire alarm. Unable to call Code Blue. Cannot tell when medical gas supply is compromised. | Facility Engineering, Safety Office, Materiel Management, and Biomedical Engineering | Insure backup (2-way radio) is available. Orient and review fire watch procedures Set up frequent walk-thrus for alarm conditions Orient staff to act as "runners" | Assess situation for each system; insure alarms are checked for accuracy on alarm Assess backup levels of available gases in cylinders | Report status to command center with assessment Institute fire watch and alarm watch, with communications backup (if needed and available) |
| 13. Elevators & Other Vertical Transport | Minimal impact on operations. . | Head Nurse GI Nurse Facilities Management | Vertical Transport for emergency diagnostic procedures or evacuation only Train staff on vertical transport Obtain enough transport litters | If the elevators are not operational utilize manual vertical transport Ensure enough litters on hand for emergency evacuation | Deploy enough litters to handle evacuations |
| 14. Transport Systems (Robotic, Pneumatic Tube, Tracked Vehicle; etc.) | Unable to receive emergency medications. Unable to receive mail service. | Materiel Management (Mail Room) and Pharmacy | Orient staff to act as "runners" Plan for manual pickup and delivery of mail and similar items | Assess needs for mail and pharmacy items | Institute runner system for pharmacy items; administrative mail secondary |
| 15. Central Medical Gases (Oxygen, Medical Air, Vacuum) | With out an active AOV alarm GI Nurse staff would not identify an interruption in Medical Gas Interruption in supply would impact care | Facilities Management; GI Nurse; Head Nurse; Respiratory Care; SPD | Number of patients requiring use of Medical Gas Identify quantity of back up required for each gas (air,oxygen,vaccum) Identify ancillary equipment needs such as tank holders, regulators, portable suction, canisters, etc… | Number of patients requiring medical gas Monitor alarms/distribution of gases | Deploy supplemental Oxygen and air tanks, portable suction units Head Nurse GI Nurse will monitor gas delivery and report loss of gas to Facilities and Respiratory Therapy |
| 16. Automated biomedical equipment utilized by GI Nurse | 1. Loss of critical equipment such as ECG system, Endo-scopic Imaging Equipment, Radiographic Equipment, would incapacitate GI Nurse | GI Coordinator Biomedical Engineering | Reduce GI schedule for period following Dec 31st, 1999 Confer with Biomedical Engineering on emergency procedures with the use of identified critical equipment Weekend of Jan 1 , 2000 testing of proper operation Train staff on emergency procedures. Obtain backups as identified | Determine critical equipment requirements for GI Nurse Determine back-ups/emergency procedures | Deploy adequate back up or alternate source for critical clinic operation. |
| 17. Life Support Equipment/Systems | 1. Life Threatening situation (ie. Loss of Defibrillator, ventilator, etc.) | GI Coordinator Biomedical Engineering | ACLS training is current Confer with Biomedical Engineering on emergency procedures with the use of identified critical equipment Train staff | 1. Assess the situation for need of back-up critical support systems | List contacts for emergency procedures Contact Biomedical Engineering for delivery of identified back-up equipment |
| 18. |  |  |  |  |  |