## Options
Wind Integration Conference Call 11/27/07
Draft-For Discussion Purposes
COMPARISON OF WIND INTEGRATION RATE OPTIONS
For FY09:
Installed wind capacity = |  | 2661 | MW
Total annual cost = |  | 24938000 | $
Cost based on balancing capacity of 194 MW and charge of $10.71/kW-mo.
Option 1 - Installed wind capacity
Apply to installed capacity for each plant
Rate = annual cost/(12 * average annual installed capacity)
Rate = | 780.9721 | $/MW-mo
Option 2 - Wind energy produced
Apply to monthly energy produced by each plant
E = Total monthly generation by plant
ET = Total monthly generation for all wind plants
Charge = (1/12 annual cost to TS)*E/ET (Monthly)
Option 3 - Generator Ramp/Drop (based on Dragoon proposal)
Apply to monthly billing determinant (below)
GI = Mean of 10 largest generation increases for specified period
GD = Mean of 10 largest generation decreases for specified period
AS = Adjustment for relative costs of up and down regulation service (use 1)
G = Total billing determinant by plant
GT = Total billing determinant for all wind plants
For each wind generator
G = GI*(10/12) + GD*AS*(2/12)
Charge = (1/12 annual cost to TS)*G/GT (Monthly)
The change is generation is the difference between the current hour and the previous hour.
This uses hourly average energy from BPA’s billing meters.
Ramp Period
The mean of the 10 largest hour to hour increases each month for the hours 2000 to 0600
(8 pm to 6 am or HE21 to HE06) every day.
Drop Period
The mean of the 10 largest hour to hour decreases each month for the hours 0600 to 0800
(6 am to 8 am or HE 7 to HE8) every day.

## Comparison
Wind Integration Conference Call 11/27/07
Draft-For Discussion Purposes
COMPARISON OF WIND INTEGRATION RATE OPTIONS - Monthly charge
| Aug 2006 | $ per month | 31 days/mo | =G/GT
Generator | Capacity - MW | Option 1 - Capacity | Option 2 - Energy | Option 3 - Dragoon
Plant 1 | 50 | 39048.6033 | 30471.246 | 42606.5985
Plant 2 | 150 | 117145.8098 | 70777.1489 | 105487.8302
Plant 3 | 76 | 59353.877 | 99122.8802 | 41884.0861
Plant 4 | 90 | 70287.4859 | 84995.6799 | 92263.2282
Plant 5 | 25 | 19524.3016 | 19993.1227 | 23118.3347
Sum | 391 | 305360.0777 | 305360.0777 | 305360.0777
| Nov 2006 | $ per month | 30 days/mo
Generator | Capacity - MW | Option 1 - Capacity | Option 2 - Energy | Option 3 - Dragoon
Plant 1 | 50 | 39048.6033 | 38295.4073 | 39489.123
Plant 2 | 150 | 117145.8098 | 145831.3661 | 129134.8509
Plant 3 | 76 | 59353.877 | 29450.9233 | 54512.9413
Plant 4 | 90 | 70287.4859 | 68118.4472 | 63752.5771
Plant 5 | 25 | 19524.3016 | 23663.9339 | 18470.5854
Sum | 391 | 305360.0777 | 305360.0777 | 305360.0777
| Feb 2007 | $ per month | 28 days/mo
Generator | Capacity - MW | Option 1 - Capacity | Option 2 - Energy | Option 3 - Dragoon
Plant 1 | 50 | 39048.6033 | 33119.6124 | 35606.7483
Plant 2 | 150 | 117145.8098 | 142580.6465 | 134716.3594
Plant 3 | 76 | 59353.877 | 31164.8008 | 55593.4703
Plant 4 | 90 | 70287.4859 | 74327.7134 | 58753.6317
Plant 5 | 25 | 19524.3016 | 24167.3046 | 20689.8679
Sum | 391 | 305360.0777 | 305360.0777 | 305360.0777
| Apr 2007 | $ per month | 30 days/mo
Generator | Capacity - MW | Option 1 - Capacity | Option 2 - Energy | Option 3 - Dragoon
Plant 1 | 50 | 39048.6033 | 20512.6769 | 28931.8203
Plant 2 | 150 | 117145.8098 | 144284.5075 | 159739.3778
Plant 3 | 76 | 59353.877 | 53764.437 | 40768.3275
Plant 4 | 90 | 70287.4859 | 66991.5596 | 59021.0812
Plant 5 | 25 | 19524.3016 | 19806.8967 | 16899.4709
Sum | 391 | 305360.0777 | 305360.0777 | 305360.0777
Sum of the 4 months for each plant
Generator | Capacity - MW | Option 1 - Capacity | Option 2 - Energy | Option 3 - Dragoon
Plant 1 | 50 | 156194.4131 | 122398.9425 | 146634.2901
Plant 2 | 150 | 468583.2394 | 503473.669 | 529078.4183
Plant 3 | 76 | 237415.508 | 213503.0412 | 192758.8252
Plant 4 | 90 | 281149.9436 | 294433.4001 | 273790.5181
Plant 5 | 25 | 78097.2066 | 87631.2578 | 79178.2589
Sum | 391 | 1221440.3107 | 1221440.3107 | 1221440.3107

## Wind Data
Wind Integration Conference Call 11/27/07
Draft-For Discussion Purposes
Data in kW
Farm | Data | 2006-08-01 | 2006-09-01 | 2006-10-01 | 2006-11-01 | 2006-12-01 | 2007-01-01 | 2007-02-01 | 2007-03-01 | 2007-04-01 | Average
Plant 1 | - GI | 15190 | 11465 | 14310 | 16835 | 12380 | 13015 | 13160 | 16075 | 12710 | 13904.4444
| - GD | -6785 | -5260 | -3785 | -11295 | -3470 | -5560 | -5500 | -6530 | -5440 | -5958.3333
| - G | 13789.1667 | 10430.8333 | 12555.8333 | 15911.6667 | 10895 | 11772.5 | 11883.3333 | 14484.1667 | 11498.3333 | 12580.0926
| - AE | 7340 | 7650 | 9967 | 19965 | 9036 | 11952 | 11809 | 9590 | 8196 | 10611.6667
Plant 2 | - GI | 39390 | 32740 | 36890 | 58950 | 48120 | 43190 | 47670 | 73060 | 71180 | 50132.2222
| - GD | -7890 | -12830 | -8720 | -17450 | -17220 | -6340 | -31410 | -26160 | -25010 | -17003.3333
| - G | 34140 | 29421.6667 | 32195 | 52033.3333 | 42970 | 37048.3333 | 44960 | 65243.3333 | 63485 | 44610.7407
| - AE | 17049 | 21435 | 28594 | 76028 | 32943 | 37791 | 50838 | 54156 | 57650 | 41831.5556
Plant 3 | - GI | 13967 | 17287 | 20382 | 24025 | 17105 | 22307 | 21155 | 19320 | 17370 | 19213.1111
| - GD | -11497 | -9685 | -6797 | -11667 | -7125 | -6980 | -5547 | -13645 | -10365 | -9256.4444
| - G | 13555.3333 | 16020 | 18117.8333 | 21965.3333 | 15441.6667 | 19752.5 | 18553.6667 | 18374.1667 | 16202.5 | 17553.6667
| - AE | 23877 | 20221 | 17412 | 15354 | 7426 | 11296 | 11112 | 18048 | 21482 | 16247.5556
Plant 4 | - GI | 34070 | 25960 | 24370 | 28430 | 28920 | 22180 | 21270 | 40500 | 26120 | 27980
| - GD | -8810 | -3490 | -5640 | -11980 | -2050 | -10140 | -11300 | -15270 | -10140 | -8757.7778
| - G | 29860 | 22215 | 21248.3333 | 25688.3333 | 24441.6667 | 20173.3333 | 19608.3333 | 36295 | 23456.6667 | 24776.2963
| - AE | 20474 | 17983 | 21413 | 35513 | 13508 | 21426 | 26502 | 28290 | 26767 | 23541.7778
Plant 5 | - GI | 8605 | 6146 | 6752 | 8206 | 7063 | 8930 | 7608 | 11747 | 7481 | 8059.7778
| - GD | -1867 | -1448 | -1615 | -3625 | -1230 | -2742 | -3390 | -3705 | -2893 | -2501.6667
| - G | 7482 | 5363 | 5895.8333 | 7442.5 | 6090.8333 | 7898.6667 | 6905 | 10406.6667 | 6716.3333 | 7133.4259
| - AE | 4816 | 4519 | 5902 | 12337 | 5435 | 6710 | 8617 | 8832 | 7914 | 7231.3333
Sum | - AE | 73556 | 71808 | 83288 | 159197 | 68348 | 89175 | 108878 | 118916 | 122009 | 99463.8889
As a percent of nameplate
Farm/nameplate | Data | [9 empty] | Average
Plant 1 | - GI | 30.38% | 22.93% | 28.62% | 33.67% | 24.76% | 26.03% | 26.32% | 32.15% | 25.42% | 27.81%
50 | - GD | -13.57% | -10.52% | -7.57% | -22.59% | -6.94% | -11.12% | -11% | -13.06% | -10.88% | -11.92%
| - G | 27.58% | 20.86% | 25.11% | 31.82% | 21.79% | 23.54% | 23.77% | 28.97% | 23% | 25.16%
| - AE | 14.68% | 15.3% | 19.93% | 39.93% | 18.07% | 23.9% | 23.62% | 19.18% | 16.39% | 21.22%
Plant 2 | - GI | 26.26% | 21.83% | 24.59% | 39.3% | 32.08% | 28.79% | 31.78% | 48.71% | 47.45% | 33.42%
150 | - GD | -5.26% | -8.553% | -5.813% | -11.63% | -11.48% | -4.227% | -20.94% | -17.44% | -16.67% | -11.34%
| - G | 22.76% | 19.61% | 21.46% | 34.69% | 28.65% | 24.7% | 29.97% | 43.5% | 42.32% | 29.74%
| - AE | 11.37% | 14.29% | 19.06% | 50.69% | 21.96% | 25.19% | 33.89% | 36.1% | 38.43% | 27.89%
Plant 3 | - GI | 18.38% | 22.75% | 26.82% | 31.61% | 22.51% | 29.35% | 27.84% | 25.42% | 22.86% | 25.28%
76 | - GD | -15.13% | -12.74% | -8.943% | -15.35% | -9.375% | -9.184% | -7.299% | -17.95% | -13.64% | -12.18%
| - G | 17.84% | 21.08% | 23.84% | 28.9% | 20.32% | 25.99% | 24.41% | 24.18% | 21.32% | 23.1%
| - AE | 31.42% | 26.61% | 22.91% | 20.2% | 9.771% | 14.86% | 14.62% | 23.75% | 28.27% | 21.38%
Plant 4 | - GI | 37.86% | 28.84% | 27.08% | 31.59% | 32.13% | 24.64% | 23.63% | 45% | 29.02% | 31.09%
90 | - GD | -9.789% | -3.878% | -6.267% | -13.31% | -2.278% | -11.27% | -12.56% | -16.97% | -11.27% | -9.731%
| - G | 33.18% | 24.68% | 23.61% | 28.54% | 27.16% | 22.41% | 21.79% | 40.33% | 26.06% | 27.53%
| - AE | 22.75% | 19.98% | 23.79% | 39.46% | 15.01% | 23.81% | 29.45% | 31.43% | 29.74% | 26.16%
Plant 5 | - GI | 34.42% | 24.58% | 27.01% | 32.82% | 28.25% | 35.72% | 30.43% | 46.99% | 29.92% | 32.24%
25 | - GD | -7.468% | -5.792% | -6.46% | -14.5% | -4.92% | -10.97% | -13.56% | -14.82% | -11.57% | -10.01%
| - G | 29.93% | 21.45% | 23.58% | 29.77% | 24.36% | 31.59% | 27.62% | 41.63% | 26.87% | 28.53%
| - AE | 19.26% | 18.08% | 23.61% | 49.35% | 21.74% | 26.84% | 34.47% | 35.33% | 31.66% | 28.93%
GI - average of 10 largest generation increases (hour to hour change) for specified period
GD - average of 10 largest generation decreases (hour to hour change) for specified period
G - weighted average of GI and GD
AE - average energy

## Total GT
Wind Integration Conference Call 11/27/07
Draft-For Discussion Purposes
Calculation of the total GT billing determinant by month for FY09
This is to be used in the ratio of each plant's G divided by total monthly GT.
This assumes that the average G for the remainder of the 2661 of wind in FY09 is equal to the average of these plants.
So GT total for FY09 is the ratio 2661/391 for each month.
Total installed wind = |  | 391
Farm | Data | 2006-08-01 | 2006-09-01 | 2006-10-01 | 2006-11-01 | 2006-12-01 | 2007-01-01 | 2007-02-01 | 2007-03-01 | 2007-04-01
Plant 1 | - G | 13789.1667 | 10430.8333 | 12555.8333 | 15911.6667 | 10895 | 11772.5 | 11883.3333 | 14484.1667 | 11498.3333
Plant 2 | - G | 34140 | 29421.6667 | 32195 | 52033.3333 | 42970 | 37048.3333 | 44960 | 65243.3333 | 63485
Plant 3 | - G | 13555.3333 | 16020 | 18117.8333 | 21965.3333 | 15441.6667 | 19752.5 | 18553.6667 | 18374.1667 | 16202.5
Plant 4 | - G | 29860 | 22215 | 21248.3333 | 25688.3333 | 24441.6667 | 20173.3333 | 19608.3333 | 36295 | 23456.6667
Plant 5 | - G | 7482 | 5363 | 5895.8333 | 7442.5 | 6090.8333 | 7898.6667 | 6905 | 10406.6667 | 6716.3333
| Sum | 98826.5 | 83450.5 | 90012.8333 | 123041.1667 | 99839.1667 | 96645.3333 | 101910.3333 | 144803.3333 | 121358.8333
| GT = | 672576.257 | 567932.9425 | 612593.7327 | 837372.2366 | 679468.0882 | 657732.0512 | 693563.6752 | 985477.4169 | 825922.9041