November 21, 1997 October 1, 1996

Contract # TW-0928AQ-1486A

SPECIAL SPECIFICATION

SECTION 13943-S

HVAC CONTROLS AND ENERGY MANAGEMENT CONTROL SYSTEM

LIST OF ARTICLES TITLES

Page

PART 1- GENERAL

1.01	Description of Work	3

1.02	References	4

1.03	Submittals	5

1.04	Quality Assurance	6

1.05	Warranty	6

PART 2 - PRODUCTS

2.01	General	8

2.02	Modular Building Controller (MBC)	8

2.03	Enclosure	9

2.04	EMCS Environmental and Service Conditions	9

2.05	Sensor, Switch, And Control Device	10

2.06	Control Damper	10

2.07	Control Valve	11

2.08	Instrument Air Source	11

2.09	Instrument Air Piping	12

2.10	Wiring	12

2.11	Control Panel	13

2.12	Controllers	13

PART 3 - INSTALLATION

3.01	General	14

3.02	Modular Building Controller (MBC)	14

3.03	Installation	14

3.04	Sensor, Switch, And Control Device	14

3.05	Control Damper	15

3.06	Control Valve	16

3.07	Instrument Air Piping	16

3.08	Wiring	17

3.09	Control Panel	17

3.10	Labels	17

3.11	Programming	17

3.12	Field Quality Control	18

APPENDIX A - FACILITIES OPERATIONS EMCS STANDARDS

Sandia Graphic Files for Insight for PC	19

Sandia Point Identification Scheme	21

Logical Point Name Identification Key for Hardware

& Virtual Points in Sandia FIDs (RCUs, SCUs, MBCs, UCs)	22

Sandia LCTLR Point Descriptor	23

APPENDIX B

GENERAL PROGRAM LAYOUT	24

SPECIAL SPECIFICATION

SECTION 13943-S

HVAC CONTROLS AND ENERGY MANAGEMENT CONTROL SYSTEM

PART 1 - GENERAL

1.01	DESCRIPTION OF WORK

A.	Contractor shall furnish, install,adjust, calibrate, and demonstrate operability of all sensors, switches, relays, controllers, control dampers and valves, wiring, instrument air piping, and accessories indicated on the drawings and requiredcommission the HVAC systems and equipment interfacing with the  Sandia National Laboratories' Energy Management and Control System (EMCS)  as detailed in the contract documents. This shall include, but not be limited to, installation , adjustment , calibration, and demonstration of operability of all sensors, switches, relays, controllers, control dampers and valves, wiring, instrument air piping, and accessories indicated on the drawings and other contract documents.

B.	Contractor shall be responsible for the installation, programming, field testing, documentation, and startup of the equipment covered by this specification. procurement, installation, calibration, demonstration of  operability and commissioning of all equipment and necessary programming to produce fully functional  HVAC / EMCS systems.  Responsibility includes the following including but not limited to: equipment such as all sensors, switches, relays, controllers, control dampers, valves and any other equipment or accessories associated with the control of the specified HVAC / EMCS systems including wiring and instrument air systems. Contractor is responsible for programming of new EMCS equipment only.  Programming of existing EMCS shall be maintained by SNL.

C.	The EMCS is referred to as the Plant Control Center (PCC).  Existing remote control units, known as Field Interface Devices (FID), and located in individual buildings, provide local monitoring and control functions.  Each FID communicates with an existing PCC Host Computer in Building 887 or Building 858 for remote monitoring and control purposes.  New control units consist of , known as Modular Building Controllers (MBCs), VAV box controllers, air handler controllers, fume hood controllers, and other controllers, as indicated on the contract documents.  MBCs include an MBC cabinet, internal point modules, controller modules, power module(s), primary module with bus expansion, expansion module with bus expansion, VAV box controllers, air handler controllers, fume hood controllers, and other controllers as indicated in the contract documents. New control units must be provided with computer and software for programming and control of EMCS.

D.	All new FID cabinets and modular components of the new FID cabinets will be provided by Sandia National Laboratories (SNL).

E.	Related Sections

Division 1, Section 1300-S, “Descriptive Submittals”

Division 1, Section 1700-S, “Commissioning”

Division 1, Section “Contract Closeout”

Division 15, Section “General Material & Work Requirements Mechanical”

Division 15, Section “Piping - Systems”

Division 15, Section “Ductwork”

Division 15, Section “Mechanical Systems Demonstrations”

Division 16, Section “Electrical Work”

1.02	REFERENCES

A.	National Electrical Manufacturers Association (NEMA)

250	Enclosures for Electrical Equipment (1000 Volts Maximum)

ICS 1	General Standards for Industrial Control and Systems

ICS 1.1	Safety Guidelines for the Application, Installation and Maintenance of Solid State Control

ICS 6	Enclosures for Industrial Controls and Systems

B.	National Fire Protection Association (NFPA)

70	National Electrical Code

C.	Underwriters Laboratories Inc.

508	Industrial Control Equipment

D.	Code of Federal Regulations (CFR)

Title 10 Part 435	Mandatory Energy Conservation Standards for Federal Buildings

Title 29 Part 1910	Occupational Safety and Health Standards for General Industry

Title 29 Part 1926	Safety and Health Standards for Construction

1.03	SUBMITTALS

A.	In generalEquipment Submittals shall conform to SNL Specification 1300-S, “Descriptive Submittals.”  Equipment submittals shall be as follows:

1.	Contractor shall submit program listing for EMCS programming for all new FIDs being installed.  Program listing shall comply with “General Program Layout” in Appendix “B” of this specification.  Program(s) shall demonstrate conformity with the Sequence(s) of Operations indicated in the contract documents.

2.	Shop drawings shall include applicable schematic diagrams.  These drawings shall clearly indicate any deviations from the contract documents.

3.	Contractor shall submit EMCS graphics files including database of all field points controlled by EMCS.  There shall be separate graphics files for each system and subsystem controlled by EMCS.  Graphic files shall comply with “Facilities Operations EMCS Standards” in Appendix “A” of this specification.  Contractor shall compile database of all field points installed and connected under this specification.  Database of field points shall include all points indicated in the contract documents.  Nomenclature of all field points shall conform to “Sandia Point Identification Scheme”  and “Logical Point Identification Key” of “Facilities Operations EMCS Standards” in Appendix “A” of this specification.  Paper “hard” copies of sample graphics shall be provided to the contractor by the Sandia Delegated Representative (SDR) upon request.

4.	Submittal shall list equipment being provided, and shall clearly describe equipment/devices/components of each type, as well as all equipment features.  Submittal shall demonstrate compliance with Part 2 of this specification.

5.	Contractor shall submit the final documentation for the EMCS installation as described in Paragraph 3.11 of this specification, prior to substantial completion of the contract as defined in SNL Standard Specification “Project Closeout.”

B.	Record Document Submittals shall conform to SNL Standard Specification “Project Closeout.”  Record document submittals shall be as follows:

1.	Final Drawings:  EMCS installer shall furnish one set of reproducible drawings of black on white of minimum size 11 X 17 inch (280 X 425 mm). minimum size showing  The drawings shall show dimensions, details, wiring diagrams and interconnections, which shall reflect all work performed under this specification.,  Drawings shall reflect  “as built”  conditions.  Wiring on all subsystems shall be included on these drawings.  Drawings shall be of sufficiently high quality drafting and reproducibility as to permit microfilming or scanning.  Internal wiring diagrams shall be laid out such that terminal blocks for external connections have sufficient room, a minimum of one and one-half inch, for showing cables for external connections.

2.	Warranty:  Contractor shall submit a warranty per Paragraph 1.05 of this specification.

C.	Provide calibration data and procedures for all sensors, switches, and controllers as part of these submittals.

D.	Provide final approved graphics files in the form of paper “hard” copies and electronic files on IBM-formatted diskette for each system or sub-system.  Files shall reflect all controls and controlled devices, together with name, catalog number, set point, and action at each end of the throttling range.  Files shall indicate the EMCS equipment formatted in compliance with “Facilities Operations EMCS Standards” in Appendix “A” of this specification.  Files shall indicate all work “as-built,” per subparagraph 1.03(B)(1) above.

1.04	QUALITY ASSURANCE

A.	The EMCS manufacturer shall demonstrate a minimum of five years experience in the design and manufacture of Energy Management Control Systems technology of the type specified on the drawings and in this specification.  This provision applies only to equipment furnished by contractor as required by the contract documents.

B.	Contractor shall provide the services of  the an EMCS manufacturer’ provided service engineer to train SNL’s personnel in proper operation and maintenance of the EMCS system per Part 3 of SNL Standard Specification “Mechanical Systems Demonstration.”  Provide a minimum of two (2) normal eight-hour working days on-site instruction unless otherwise noted in the contract documents.

1.05	WARRANTY

Contractor shall warrant any If any defect in apparatus furnished by contractor under this specification and warrant compliance , or failure to comply with the requirements of the contract documents for a shall appear within the period of one (1) year from the date of acceptance by SNL.   the controls installed under this specification shall be immediately repaired.   Contractor shall, without delay and at his own expense, correct the defects or failure of compliance of items and services by repairing the defective parts furnished and installed under this specification, by supplying non-defective replacement parts, or by correcting a defective or deficient design by any other means recommended by the EMCS manufacturer and accepted by the SDR.  Contractor shall provide to SNL a letter warranting their work on the controls and EMCS for a period of one (1) year from date of acceptance of the controls and EMCS by SNL.  Warranty shall cover labor only on equipment furnished by SNL.

PART 2 - PRODUCTS

2.01	GENERAL

A.	The EMCS shall comply with UL 508.

B.	The EMCS and its several components shall comply with the latest applicable standards referenced in Paragraph 1.02 of this specification.

C.	All materials and components used shall be standard components, regularly manufactured for this type application and not custom designed especially for this project.

D.	All products shall be as specified in the contract documents or approved equals.

2.02	MODULAR BUILDING CONTROLLER (MBC)

A.	Modular Building Controller (MBC) shall be as indicated on the contract documents and as provided by SNL and as unless otherwise indicated by on contract documents

B.	Contractor shall review equipment indicated as SNL-furnished in the contract documents.  Contractor shall insure that all interfaces are of sufficient types and quantities to enable a complete and fully functional system.  Contractor shall notify SDR in writing of any deficiencies in the functionality of the EMCS found during this review.

C.	Software for EMCS shall be as indicated in the contract documents.

Provide Personal Computer (PC) for control and data storage of EMCS programming.  PC shall be configured according to SNL Standards for PCs.  These standards are as follows:

Case shall contain a minimum of three (3) external drive bays and two (2) internal drive bays.  Case shall contain power supply of sufficient capacity for all components specified below.

The motherboard/CPU shall consist of an Intel Pentium CPU, 133MHz min., with heat sink and extra cooling, Triton chip set, 256k L2 cache, 32 Mbytes RAM in two SIMMs (upgradeable to 128 Mbytes), PCI IDE hard disk controller, floppy disk controller, 64 bit S3 PCI local bus video graphics controller with 2 Mbytes of video RAM, and a minimum of two 16550 UART serial ports, one enhanced parallel port, and one mouse port.

A minimum of one IDE 1.2 Gbyte hard drive and one 1.44Mbyte floppy drive mounted in external bays.

One 3C590 PCI Combo Network Interface Card, or integrated 3COM OEM supplied chipset.

Furnish 102 key enhanced keyboard and port mouse.

Furnish flat screen monitor, 17” diagonal, 0.28 dot pitch or better.

Furnish and install Sandia standard software:

Microsoft NT 3.51 Workstation.  Installation - 60 Mbyte.  Virtual Memory - 60 Mbyte.

Sandia-furnished version of Netscape 3.0.

Sandia-furnished Landis & Gyr Insight base software.

8.	Creative Labs Sound Blaster 16, or Creative Labs supplied OEM chipset.

One IDE 4X CDROM (energy star compliant) mounted in external bay.  CDROM must be on Microsoft NT Hardware Compatibility List, connected to IDE port of sound card, and provided with sound cable.

Speakers.

Contractor shall provide all interfaces with SNL computer as indicated in the contract documents.

2.03	ENCLOSURE

Enclosures for EMCS equipment shall house all electrical and electronic components and remote control devices.  Enclosure shall be a wall-mounted NEMA Type 1 per NEMA 250 and ICS 6 which shall include ventilation louvers for the dissipation of heat.

2.04	EMCS Environmental and Service Conditions

All EMCS components to be installed indoors shall be designed to operate within the following environmental or service conditions:

A.	Ambient Service Temperature:  0oC to 40oC.

B.	Humidity:  Non-condensing  to 90%.

C.	Altitude:  5,500 feet (1.7 km).

2.05	SENSOR, SWITCH, AND CONTROL DEVICE

A.	Room, duct, and immersion sensors shall provide an output signal that varies continuously with the sensed media within a fixed range specified on the drawings.  Output shall be linear with negligible hysteresis.

B.	Sensor accuracy shall be as indicated on the drawings and, when part of a control loop, shall be sufficient to maintain the controlled variable within limits indicated on the drawings.

C.	Controllers shall have variable set point and adjustable proportional band unless indicated otherwise on the drawings.

D.	Pneumatic room thermostats shall be a two pipe non-bleed relay type with visible temperature scale and adjustable set point scale with a permanently affixed external adjustment suitable for occupant control of room temperature without the use of tools.

Pneumatic zone thermostats shall be similar to room thermostats except the adjustable set point scale shall be concealed with an internal means of set point adjustment.

Sensors, switches, and control devices to be installed outdoors shall be listed for the environmental conditions in which they are being installed.

2.06	CONTROL DAMPER

A.	Damper shall be low leakage type, Ruskin CD-50 series airfoil unless indicated otherwise on the drawings.

B.	Damper shall be a standard louver type of heavy duty construction with each leaf reinforced.  Damper shall be provided with non-ferrous self lubricating bearings and trunions.

C.	Damper shall be of aluminum unless indicated otherwise on the drawings.

D.	Damper frame, blades, shafts, linkage, bearings, and trunions shall be non-corrosive.

E.	Damper blade edge seals shall be replaceable and of vinyl, silicone rubber, neoprene, or other synthetic elastomer.

F.	Damper shall have a published leak rate not exceeding 5 scfm per square foot (91.5 m³/hr. per m²) at 1.5 inches W.C. (373.6 Pa) differential pressure unless indicated otherwise on the drawings.

G.	Modulating dampers shall have opposed acting blades, and two-position dampers shall have parallel acting blades unless indicated otherwise on the drawings.

H.	Each damper section shall have an individual motor, derated so there is 10 percent over-capacity available over published rating for dust and corrosion buildup and shall be additionally sized to operate against the static pressure of the systems.

2.07	CONTROL VALVE

A.	Control valves 2 inches (50.8 mm) or smaller shall be screwed pattern with bronze body unless indicated otherwise on the drawings.

B.	Control valves larger than 2 inches (50.8 mm) shall be flanged with cast iron body unless indicated otherwise on the drawings.

C.	Valve pressure-temperature ratings and materials of construction shall be suitable for the intended service.  Valves intended for steam service shall be rated for 350oF (176.7oC).

D.	All 2-way control valves shall be capable of tight shut-off against total system differential pressure.

E.	Modulating control valves shall be fitted with equal percentage or linear characteristic modulating plugs as the service requires.

F.	Valve sizing data, including capacity index, shall be indicated on the control submittal diagrams.

G.	Visible position indicators shall be provided on all automatic valves.

2.08	INSTRUMENT AIR SOURCE

A.	Furnish and install as indicated in the contract documents, a self-contained air compressor which will supply compressed air for the operation of the pneumatic controls.

B.	The compressor shall be a complete unit designed to compress air to 80 psi (551.6 kPa).

C.	Compressor and motor shall be adequately sized so that the free air delivery at the receiver cut-in pressure equals or exceeds all present and indicated future instrument air demands while operating not more than 33% of the time.

D.	Compressor shall be provided with controls including starter, control panel, gauges, and controllers for full automatic operation.

E.	The compressor shall be factory assembled with a suitable receiver, ASME Code constructed for pressure of 125 psi (861.8 kPa).  Receiver shall be National Board Certified and so stamped.  The certification papers shall be submitted.  Receiver shall be provided with a manual valve drain, automatic drain, and ASME safety relief valves.

F.	A suitable pressure reducing valve designed for 125 (861.8 kPa) psi to the controls operating pressure shall be provided for system supply.

G.	Compressor shall be provided with an OSHA approved belt guard.

H.	When specified in the contract documents, a properly sized, completely automatic refrigerative type air dryer shall be furnished and installed in the supply line to the system to assure dry control air.  Dryer shall be equal to Hankison Series 80.

I.	The FID main control air filter shall be for compressed air service with manual drain and metal guard, 1/4" (6.35 mm) NPT inlet and outlet; Quincy Model No. 8527.

2.09	INSTRUMENT AIR PIPING

A.	Instrument air piping shall be copper, plastic, or stainless steel.  Aluminum tubing may be used only if approved by the SDR prior to the start of any work.

B.	Copper tubing shall be hard drawn with sweated fittings or soft drawn-stretched and straightened.

C.	Plastic tubing shall be flame retardant polyethylene.  Plastic tube bundles shall be provided with a factory installed PVC vinyl jacket.  Plastic tubing installed in return air ceiling spaces shall be plenum-rated.

D.	All instrument air piping shall be 1/4" (6.35 mm) O.D. unless approved prior to the start of any work.

2.10	WIRING

A.	All wiring shall comply with the electrical sections of these specifications.

B.	Plant Control Center Wiring

1.	Field wiring for each analog sensor shall be two conductor # 18 AWG, twisted AWG, copper, 300 volt, thermoplastic.

2.	Field wiring for each digital input device shall be # 16 AWG type TFFN.   Conductors shall be  colored blue.

3.	Field wiring for each digital output device shall be # 14 AWG type THHN.  Conductors shall be colored black.

4.	All wiring shall be installed in electrical-metallic tubing (EMT) with watertight compression-type threadless fittings or rigid galvanized steel conduit (RGS) or intermediate metal conduit (IMC), or as otherwise indicated in the contract documents.

2.11	CONTROL PANEL

A.	Panels shall be totally enclosed, 16 gage (min.) steel, with hinged locking door and door stiffeners.

B.	Panels shall have electrical connections prewired to terminal strips using same numbers shown on the drawings.

C.	Each panel shall contain, flush mounted on the cover, all 3 1/2-inch (88.9 mm) dial thermometers and other devices as indicated in the contract documents.

2.12	CONTROLLERS

A.	All controller modules shall be capable of communicating directly with the MBCs using the EMCS standard Landis & Staefa proprietary P2 or LAN network Protocols.  Any controller device provided shall be fully compatible with the EMCS standard and of a type regularly manufactured for HVAC control use and not a custom designed device.  Capability to communicate with the EMCS standard shall be demonstrated by the use of the device type in typical and fully functional HVAC control installations for a minimum of two years.  The controller device shall be capable of connecting directly to the communication network cable without intervening interface converting devices and cables.

PART 3 - INSTALLATION

3.01	GENERAL

A.	Install all MBCs, sensors, switches, control devices, accessories, conduit and wire, and instrument air piping indicated on the drawings and required for a complete and operational temperature control system.

B.	Contractor shall examine areas and conditions under which the EMCS is to be installed and notify the SDR in writing of those conditions detrimental to proper completion of the work.  Work shall not proceed until unsatisfactory conditions have been corrected in a manner acceptable to the SDR.

C.	Contractor shall provide indoor storage for the EMCS meeting service requirements listed in Paragraph 2.04 of this specification.

3.02	MODULAR BUILDING CONTROLLER (MBC)

MBCs shall be installed in dry interior areas of buildings and as indicated on drawings.  MBCs shall not be installed near heat generating equipment or devices.

3.03	INSTALLATION

A.	Construction work shall comply with the contract specifications, construction drawings, and the requirements of the referenced codes and standards of Paragraph 1.02 of this specification, particularly 29 CFR 1910, Subpart S and 1926, Subpart K, NFPA 70, and NEMA ICS 1.1.

B.	Installation of the EMCS and accessory items shall comply with the manufacturer’s written installation instructions and per SNL Standard Specification Section “Electrical Work.”

3.04	SENSOR, SWITCH, AND CONTROL DEVICE

A.	All sensor assemblies shall be readily accessible and adaptable to each type of application in such a manner as to allow for quick, easy replacement and servicing without special tools or skills.

B.	All sensors and switches installed outdoors shall be installed in NEMA 3R enclosures.

C.	Install sensors in locations which will provide a correct measurement of the sensed media.  Do not locate sensors in dead air spaces or positions obstructed by ducts, equipment, etc.  The location shall be within the vibration and velocity limits of the sensing element.  Use an extended surface element when required to properly sense the average temperature or pressure, etc., securely mounted and positioned to measure the best average temperature, etc.  Thermally isolate elements from brackets and supports.  Securely seal ducts where elements or connections penetrate ducts.

D.	Provide all sensors measuring temperatures in pipes with thermometer wells.  Where piping is smaller than the length of the well, install the well in the piping at elbows to affect proper flow across the entire area of the well.  Install wells either looking upstream or downstream.  Provide suitable thermal transmission material within the well to speed the response of temperature measurement.  Provide wells with sealing nuts to contain the thermal transmission material and allow for easy replacement.  Well shall not restrict flow area to less than 70 percent of the line-size-pipe normal flow area.

E.	All pressure sensors and switches, including differential pressure sensors and switches, installed on steam lines shall be protected by pigtail siphons installed between the sensor element and the steam line.

F.	Pressure sensors and switches, including differential pressure sensors and switches, installed on steam or liquid lines shall have an isolation valve installed between each sensor and its pressure source.

G.	Duct thermometers with a minimum 3-inch (76.2 mm) dial shall be installed upstream and downstream of each duct heat exchange device and adjacent to each duct mounted temperature sensor.  Range shall match application.

H.	Room thermostats and temperature sensors shall be wall mounted 5'-6" (1.7 m) above the floor.

I.	All thermostats or sensors located on exterior building walls shall be insulated from the wall surface on a 1-1/2 inch (38.1 mm) thick block of rigid insulation and shrouded by a cover that is closed on the top, sides, and front but open at the bottom for free air circulation.

J.	Mount all controllers in control panels so that all control adjustments can be made at a control panel.

3.05	CONTROL DAMPER

A.	Control dampers shall be installed per SNL Standard Specification “Ductwork”.

B.	Damper motors in plenums shall be mounted on damper frames.

C.	Motors shall be accessible for servicing.

D.	Motors located outside shall be mounted in a position to allow for condensation drainage.

E.	When two or more dampers are intended for inter-related operation, they shall be connected wherever possible through mechanical connections operating on easily movable swivel joints and shall not depend upon parallel operation of separate damper motors.

3.06	CONTROL VALVE

Control valves shall be installed per SNL Standard Specification “Piping - Systems”.

3.07	INSTRUMENT AIR PIPING

A.	Piping in the equipment rooms shall be installed exposed, securely attached to the structure or to the equipment and run parallel or at right angles to the structure.

B.	Piping on new construction to all equipment outside of the equipment rooms shall be concealed.

C.	Piping in old construction may be run exposed except where easy access permits concealment.

D.	All piping shall be securely supported by the structure or equipment using hangers of the clamp type.

E.	Piping shall be offset around all beams, girders, etc.

F.	Piping SHALL NOT be installed through the sheet metal ducts or in fresh air intakes.

G.	Piping installed outdoors shall be pitched toward the building, with suitable drip legs inside, for condensation drainage.

H.	Unsheathed plastic tubing shall be installed in an enclosed raceway system such as Wire-mold or EMT, except that final connections may be made with a maximum of 18" (460 mm) of exposed plastic tubing.

I.	Plastic tubing for enclosed control panel piping shall be installed parallel or at right angles to the panel configuration.

J.	All piping shall be provided with pressure gages at the final control element and at the controller.

K.	Air pressure gages, size 1-1/2" (38.1 mm) shall be installed on all connections to pneumatic controlled valves, damper motors, thermostats, control devices, etc., so that the operation of each device can be checked.  The range of each gage shall match the application.  Gages are not required where room thermostats are flush mounted with concealed connecting tubing.

L.	Do not install piping in same conduit with electrical wiring.

3.08	WIRING

A.	All wiring shall comply with the electrical sections of these specifications.

B.	Plant Control Center Wiring

1.	Wiring from sensors and control devices shall be to terminal strips within the FID, control panel, or Motor Control Center, as shown on the drawings.

2.	All wiring runs shall be continuous.  Splices will not be acceptable.

3.	Each wire shall be labeled at both ends per the drawings.

4.	Shielded cable shall be grounded at sensor only.

5.	All conduit shall be painted to match surroundings.  One-inch purple vinyl tape shall be installed on conduits within six inches of all J-boxes, sensors, and panels to identify PCC conduits.

6.	Wiring shall not be installed in the same conduit with instrument air piping.

3.09	CONTROL PANEL

Install control panels where indicated on drawings.  Enclosures shall be securely mounted to the floor, wall, or equipment with unistrut supports.

3.10	LABELS

A.	Each control device shall be provided with an engraved laminated phenolic resin label, black background with white letters.

B.	Nomenclature shall correspond to that indicated in the contract documents.

3.11	PROGRAMMING

Contractor shall install SDR approved programming in PC for EMCS per subparagraph 2.02(D) of this specification. Contractor shall install SDR approved programming in FIDs for EMCS.

3.12	Field QUALITY CONTROL

A.	Contractor shall provide the services of the EMCS manufacturer’s service engineer to test, checkout, and start up the EMCS.  The manufacturer’s service engineer may, at contractor’s option, concurrently perform the training functions required under Subparagraph 1.04 (B) of this specification, but is responsible for coordinating the training with the appropriate SNL Facilities Maintenance organization.  Contractor shall notify the SDR a minimum of two weeks prior to any scheduled test, checkout, and startup.

B.	Under no circumstances is contractor to energize any portion of the EMCS system without authorization from the EMCS manufacturer’s representative.

C.	Prior to start up, contractor shall make a visual inspection of the EMCS and take note of the following items:

1.	The presence of any moisture or debris inside the equipment.

2.	Any damage or dents to EMCS enclosure.

3.	Any damaged, disconnected, or loose components, conductors, control piping, devices, or terminal connectors.

Contractor shall correct any deficiencies found during this inspection prior to commencing the start up of the EMCS.

D.	Contractor shall demonstrate trouble free, stable operation of the EMCS and demonstrate system sequence of operation.  Sequence of operation shall comply with sequence noted elsewhere in the contract documents.  System demonstration shall comply with SNL Standard Specification Section “Mechanical Systems Demonstrations.”  Contractor shall provide written certification of this demonstration upon completion.

END OF SECTION

# Comments

Page: 5
 Suggest (The drawings shall show)

Page: 16
Check consistancy in use of MBC and FID