| 2 | Maintenance And Repair | C2, 1 |
| --- | --- | --- |
| 2.1 | General Information…….. ………………………… | C2, 1 |
| 2.1.1 | Annex Description ………………………………….. | C2, 1 |
| 2.1.2 | Background ………………………………………….. | C2, 1 |
| 2.1.3 | Definitions …………………………………………… | C2, 1 |
| 2.1.4 | Additional Contract Support ……………………….. | C2, 2 |
| 2.1.5 | SFUSS Descriptions ………………………………... | C2, 2 |
| 2.1.5a | Structures …………………………………………… | C2, 2 |
| 2.1.5b | Facilities …………………………………………….. | C2, 2 |
| 2.1.5c | Utilities ………………………………………………. | C2, 2 |
| 2.1.6 | Location of Services ……………………………….. | C2, 2 |
| 2.1.7 | Restrictions, Limitations, and Special Conditions… | C2, 2 |
| 2.2 | Scheduled Maintenance (SM) | C2, 3 |
| 2.2.1 | Implement the SM Plan …………………………….. | C2, 3 |
| 2.2.2 | Accomplish Scheduled Maintenance …………….. | C2, 3 |
| 2.2.3 | Equipment Inventories and Database Update…… | C2, 3 |
| 2.2.4 | Equipment Identification …………………………… | C2, 3 |
| 2.2.5 | Pressure Systems Support ………………………… | C2, 4 |
| 2.2.6 | Light/Lamp Replacement …………………………… | C2, 4 |
| 2.3 | Repair | C2, 5 |
| 2.3.1 | Repair Equipment and Systems in the SM Database | C2, 5 |
| 2.3.2 | Non Specified Equipment Emergency Response... | C2, 5 |
| 2.3.3 | Critical Spare Parts Management ………………… | C2, 6 |
| 2.4 | Maintenance Activation Program | C2, 6 |
| 2.5 | Warranty Program | C2, 7 |
| 2.6 | Availability And Reliability | C2, 8 |
| 2.7 | Reliability Centered Maintenance | C2, 9 |
| 2.8 | Personnel Requirements | C2, 9 |
| 2.8.1 | Provide Qualified Personnel ………………………. | C2, 9 |
| 2.8.2 | Provide Electrical Personnel ………………………. | C2, 9 |
| 2.8.3 | Provide Diesel Personnel ………………………….. | C2, 9 |
| 2.8.4 | Provide Refrigeration Personnel ………………….. | C2, 10 |
| 2.8.5 | Provide General Tester …………………………….. | C2, 10 |
| 2.8.6 | Provide Breaker Tester ……………………………... | C2, 10 |
| 2.8.7 | PT&I Personnel Requirements ……………………. | C2, 10 |
| 2.8.8 | Provide Journeyman Linemen or Equivalent Title .. | C2, 11 |
| 2.9 | Records, Reports, And Submittals | C2, 11 |
| 2.9.1 | User Equipment Maintenance Report ……………. | C2, 11 |
| 2.9.2 | Pressure Systems Certification Testing Report …. | C2, 11 |
| TABLE 2-1 | Work Classification | 2-1, 1 |
| TABLE 2-2 | Maintenance Scheduling Windows | 2-1, 2 |
| TABLE 2-3 | Building Systems -Ellington Field -Johnson Space Center -Sonny Carter Training Facility | 2-3, 1 2-3, 1 2-3, 13 2-3, 92 |

2	MAINTENANCE AND REPAIR

2.1	General Information

2.1.1	Annex Description

This Annex identifies the routine *Scheduled Maintenance (SM) and Repair (R) requirements for specified significant Structures, Facilities, Utilities, Systems and Subsystem components (SFUSS), Mobile Support Equipment (MSE), User Equipment (UE), and Installation - Accountable Government Property (IAGP)

2.1.2 	Background

The *JSC is a large and complex site and the Contractor is expected to use to full advantage the equipment and facilities provided by the Government to keep all identified equipment providing their intended functions, outputs, and availability.  The Contractor will be provided the NASA-JSC Scheduled Maintenance Database, which includes:

- The initial Annual Work Plan (AWP)

- All required scheduled maintenance task instructions

- Partial equipment inventory including buildings and systems with six categories of equipment.

- All mandated Computerized Maintenance Management System (CMMS) fields

- Levels of criticality for Repairs

The SM plan establishes the minimum quantity and frequency for each scheduled Preventive Maintenance (PM) task for the Buildings, Systems, Sub-systems and equipment in the **SM database.  System Descriptions, components, and required outputs are provided in Section J, Attachment N, Exhibit N-1, Table 1. In the event that inconsistencies exist between SFUSS descriptions, and their components, as generally set forth in Section J, Attachment N, Exhibit N-1, Table 1 and specific descriptions of such systems contained in the Technical Reference Library (TRL), the specific descriptions in the TRL shall control.

Equipment Categories within the SM Database are as follows:

- Center Operations User Equipment (UE/JA)

- Structures, Facilities, Utilities, Systems and Sub Systems (SFUSS)

- Installation - Accountable Government Property (IAGP)

- Mobile Support Equipment (MSE)

- User Equipment (UE)

- Non Specified Equipment (NSE)

2.1.3	Definitions

User Equipment (UE)- Those systems or equipment that are required for test setups or in conducting operations unique to a particular facility, and frequently changed or moved to accommodate the requirements of a particular test program.

Center Operations User Equipment (UE/JA)- Those pieces of user equipment that belong to the Center Operations Directorate.

Structures, Facilities, Utilities, Systems, and Subsystems (SFUSS) - the physical plant of *JSC; further defined in CLIN 2.1.5.

Installation - Accountable Government Property (IAGP) - Property in the possession of, or directly acquired by, the Government and subsequently made available to the Contractor for use in the performance of work related to this contract.

Mobile Support Equipment (MSE) - A group of Government owned mobile equipment that is maintained, repaired, and fueled by the COSS contractor and may be made available for use by the Government, other Government Contractors, or the COSS Contractor.  A portion of the MSE is engine driven and the remainder is not.  A detailed list of MSE is provided in Section J, Attachment N, Exhibit N-2.

Non Specified Equipment (NSE) - A group of non-collateral equipment that is not specified in the contract and will have maintenance and repair provided, if required, by Task Order.

Maintenance - Day-to-day, periodic, scheduled, or unscheduled work required to preserve a piece of equipment, a system, or a real property facility in a condition that it may be effectively used for its intended purpose and availability.

Repair - That facility work required to restore a facility of component thereof, including *collateral equipment, to a condition substantially equivalent to its originally intended and designed capacity, efficiency, or capability. It includes the substantially equivalent replacements of utility systems and *collateral equipment necessitated by incipient or actual breakdown.  Repair includes adjustment, overhaul, reprocessing, or replacement of constituent parts or material that have deteriorated by action of the elements or usage, have been damaged, regardless of the cause, or have not been corrected through maintenance.  Example:  Repair does include services such as tank cleanings, etc., due to unsatisfactory testing, inspections, or scheduled maintenance; however, Repair does not include upgrades identified as building deficiencies (e.g., safety or fire inspections, new laws, etc.)

2.1.4	Additional Contract Support

The *Scheduled Maintenance (SM) and Repair (R) programs shall include, but not be limited to: all labor, materials, equipment, tools and other Center Operations Support Services (COSS) such as transportation, rigging, supply, engineering, operations, and reporting necessary to accomplish maintenance and repair.  The programs also include, but are not limited to: planning, implementing, accomplishing, recording, and reporting on all facets of maintenance and repair.

2.1.5	SFUSS Descriptions

SFUSS includes, but is not limited to the general descriptions below:

2.1.5.a	Structures (S): A structure is a constructed unit established for a designated objective.  Structures that are part of or inside a facility are included with the facility.  For purposes of this Contract, the following are defined as examples of structures:

(1) Environmental - Vaults, containment berms.

(2) Civil - Fences, gates, memorial and Rocket Park displays, flagpoles, weather towers, antenna towers, refuse collection and compaction structures, fire training facility structures.

2.1.5.b	Facilities (F): A facility is an enclosed structure to protect personnel, material, or equipment from the elements and to provide associated work or storage space. A facility includes the utility systems inside the facility to a point of interface as defined in Section J, Attachment N, Exhibit N-1.  The facility is defined to extend to five feet from the facility on each utility system or as otherwise defined.

(1) Civil (C): Includes roll-up and automatic doors, domestic hot 	water, potable water, sanitary and storm sewer, natural gas, fire 	protection water, roofs, doors, windows, flooring (coatings and 	coverings), stairs and stairwells, interior walls, ceilings, and partitions, 	foundation, structural system, building shell, including Pre-cast Exposed 	Aggregate Faced  (PEAF) panels, external attachments such as 	walkway covers, overhangs, barge and loading docks.

(2) Electrical (E): Includes138kV transmission systems, 15kV 	distribution systems, emergency lighting system, emergency power 	backup systems, general area lighting, grounding, lightning 	protection, Energy Management and Control Systems, secondary 	distribution system, fire protection and security system, exterior 	lighting systems, traffic control, obstruction and warning lighting 	system, central telecommunication systems, Intercom systems, and 	radio tape monitoring systems.

(3)	Mechanical (M): Includes Heating Ventilation and Cooling 	(HVAC), compressed air, chilled water, steam/condensate return, 	heating hot water, exhaust, refrigeration systems, and support 	equipment.

(4)	Environmental (X): Includes various combinations of utility or facilities units, i.e., tanks and collection systems, vaults, containment berms and impoundments, groundwater treatment systems, and waste treatment systems. These facility units and systems are highly regulated by numerous Environmental Protection Agency (EPA) and State environmental laws and regulations and therefore shall be maintained to meet these regulatory requirements. For all environmental structures, facilities, utilities, and systems, the Contractor will conduct Preventive Maintenance tasks in accordance with JSC approved PM’s.

(5)  Other (O): includes elevators, cranes, and hoists.

2.1.5.c	Utilities (U): A utility is a system for collecting or distributing services between a common point and specific locations both above and below ground.  They are characterized by the assignment of site code of 998 in the System field in the SM Database.  The division between facility and utility occurs at five feet from the facility for piping systems or as defined in the respective definition.

Detailed definitions including components and associated output are provided in Section J, Attachment N, Exhibit N-1,Table 1.

2.1.6	Location of Services

Maintenance and Repair services are required at *JSC.  The Contractor shall be provided with a wide variety of facilities and work areas, see ** List of Contractor Facility Floor Plans and ** Drawings of Contractor Facility Floor Plans, from which to support these services

2.1.7	Restrictions, Limitations, and Special Conditions

All personnel performing maintenance and repair work within any *JSC facility shall sign in and out on the Facility Managers building work log.  Sign in/out is required for occupancy/evacuation purposes and shall be done for each separate activity even if performed on the same workday.

| 2.2 | Scheduled Maintenance |  |  |  |
| --- | --- | --- | --- | --- |
| 2.2.1 | Implement the SM Plan Ensure the SM database is accurately input into the CMMS | Load the **SM Database into the CMMS system. Conduct system verification and check out and ensure proper system operation. | 1 Database | All system modules operate correctly. |
| 2.2.2 | Accomplish Scheduled Maintenance | Accomplish all UE/JA, SFUSS, and IAGP maintenance tasks in the **SM Database. Tasks shall be performed within the windows specified in Table 2-2 for each applicable maintenance frequency. | **SM Database | All tasks accomplished on schedule and at industry standard quality or better. |
|  | Ensure performance of the PM tasks in the SM Database | Maintain HVAC equipment and systems free of mold, mildew, fungus, algae, and other biological growth to ensure indoor air quality meets current ASHRAE recommendations. Provide outage/operation support for maintenance work. |  |  |
|  |  | Maintain, update, report, and reconcile the **SM Database for changes to the PM task statements as directed under Maintenance Activation, CLIN 2.4 |  |  |
| 2.2.3 | Equipment Inventories & Database Update Verify/Validate an accurate CMMS Equipment Database | Conduct two comprehensive physical field inventories of all facility equipment at *JSC. One inventory within 90 days of contract start, including re-labeling and bar coding the equipment. Conduct a second inventory 42 months after contract start. (Year 1 and Year 4 of contract). There are approximately 12,600 items in the database. | 1 inventory in year 1 1 inventory in year 4 | All equipment accurately identified and accounted for. |
|  |  | Update the *SM Database and CMMS database as required to correct errors or anomalies identified during the inventory. |  | Updates are correct and made on time. |
|  |  | Identify configuration changes, errors, or deficiencies to the existing facility structures and utility inventories, and recommend changes and/or improvements to the CMMS Database. Upon Government approval, incorporate changes into the CMMS database. |  |  |
| 2.2.4 | Equipment Identification Maintain an accurate equipment identification program | Maintain an accurate CMMS Equipment database to: Ensure accurate Maintenance Identification (ID) Numbers Ensure accurate Equipment Numbers Facilitate Replacing missing Tags Accurately Identify new or replacement equipment. Ensure Capturing Database Information | 12,600 pieces of equipment | Timely and accurate data and identification. |
|  |  | Maintain a data base which tracks equipment numbers in the CMMS for all newly installed, relocated, and removed equipment per ** Equipment Number List. Distribute correct numbers to site customers within one day of request. |  | All equipment is tagged. |
|  |  | Accurately populate the equipment data fields within 14 days (Horsepower, capacities, etc.) for Facility Condition Assessment, equipment history, etc. as a part of Maintenance Activation and ensure that all equipment and database include matching maintenance ID tags. | Contractor determined | Accurate equipment data. |
|  |  | Replace tags found missing (as part of other duties) within two days of discovery. | Nothing additional | Tags correctly replaced on time. |
| 2.2.5 | Pressure Systems Support Ensure accurate inspection and certification of Pressure Systems | Provide required support to ensure that all SFUSS pressure vessels and pressurized systems are accurately inspected and certified as required by **JHB 1710B, Design, Inspection, Certification of Pressure Vessels and Pressurized Systems. For items in the system see **Pressure Systems Inventory. Note: Support includes but is not limited to: providing crafts to accompany the Pressure Systems Inspector and includes removing, bench testing and re-installing Relief Valves, removing and reinstalling tube bundles etc. and other disassemble/assembly work to facilitate inspection tasks. This support also includes Work Control Center support in tracking and other paperwork to ensure an audit trail. |  |  |
|  |  | a. Provide support for Class I Pressure Vessel Inspections: Year 1 – 535, Year 2 – 564, Year 3 – 535, Year 4 – 520, Year 5 - 535. | 520 to 564 inspections | Inspections accurate and on time. |
|  |  | b. Provide support for Class II Pressure Vessel Inspections: Year 1 – 8, Year 2 – 11, Year 3 – 22, Year 4 – 10, Year 5 - 9. | 8 to 22 inspections | Inspections accurate and on time. |
|  |  | c. Provide support for Class III Pressure Vessel Inspections: Year 1 – 50, Year 2 – 93, Year 3 – 95, Year 4 – 46, Year 5 - 59. | 46 to 95 inspections | Inspections accurate and on time. |
|  |  | d. Provide Relief Valve Certification and vessel/system proof testing support: Year 1 – 450, Year 2 – 359, Year 3 – 514, Year 4 – 295, Year 5 - 514. | 344 to 565 certifications | Certifications accurate and on time. |
|  |  | e. Provide Flex Hose Certification support: Year 1 – 24, Year 2 – 34, Year 3 – 46, Year 4 – 19, Year 5 - 29. | 19 to 46 certifications | Certifications accurate and on time. |
| 2.2.6 | Light/Lamp Replacement Incandescent and fluorescent lights and lamps are replaced when burned out or flickering. | Provide and replace burned out or flickering light bulbs/lamps with same type, wattage/voltage. Clean fixtures, globes, reflectors, covers, diffusers, and plastic side panels when lamps are replaced and clean any adjacent areas that become contaminated with foreign material, including dust, dirt, or cleaning product residue. Complete bulb/lamp replacement for those above 10 foot within 5 *workdays except where directed by the Maintenance & Repair *TMR. Place burned out bulbs and lamps into box labeled “Universal Waste.” Lamps shall be collected and recycled in accordance with Annex 9 requirements. | 20,000 fixtures at *JSC. | Lighting is replaced properly and on time. |
| 2.3 | Repair |  |  |  |
| 2.3.1 | Repair Equipment and Systems identified in the SM Database Ensure accurate repairs | Perform all repair work required for systems, equipment and components identified in the **SM database. NOTE: Response and Repair times are defined in Table 2-1. Obtain the services of a competent overhead door installer for recommendations to define the proper repairs to overhead or sliding doors (excluding personnel sliding doors) when critical components cannot be replaced on an exact one for one basis. This shall also apply to acquiring design recommendations if some engineering is required to complete the repair. Ensure that all modifications to overhead or sliding doors do not compromise the original safe installation and operation of the door. For all equipment in the ** SM Database: If repairs are anticipated to exceed 66% of the replacement cost of the equipment, notify the Maintenance and Repair *TMR for authorization to replace the equipment (also see H.5). For equipment not included in the **SM Database: Repairs for this equipment shall be accomplished by Task Order/ IDIQ as specified in Annex 13. Provide outage/operation support for repair work. | ** Workload History | Equipment operating except during repair period. Repair plan used where required. |
|  |  | Repair plans shall be submitted for work that will not be performed within the timeframe given in Table 2-1. The plan shall include at a minimum the name and work order number of the task, the justification for the delay and the scheduled completion date. |  | Repair plans submitted with adequate detail. |
|  |  | NOTE: Asbestos exists in some *JSC buildings, consequently, some Maintenance and Repair work will require OSHA Class I - III Asbestos Abatement. |  |  |
| 2.3.2 | Non Specified Equipment Emergency Response Correct Emergency Situations on Non Specified Equipment | Respond to, mitigate, and fix, non specified equipment requiring emergency repair. Includes cleanup actions resulting from an emergency situation, moving of equipment, furniture, etc. to preclude further damage to the property, and follow-up checks to ensure reliability of services (e.g. lights work properly after a kitchen fire, etc.) | 200 Emergency Calls | Respond per Table 2-1 |
|  |  | Individuals responding to an emergency shall be capable of mitigating the situation. When situations occur outside the Contractor's control, which prevent the work from being mitigated, approval to suspend emergency work shall be obtained from the Maintenance and Repair * TMR. Perform work up to an estimated cost of $ 500 *bare cost per occurrence. Individual Task Orders per Annex 13 will be issued for amounts exceeding that level. Authorization shall be obtained from the CO prior to exceeding the $ 500 cost estimate. |  | No work above the approval level without a Task Order or Verbal approval of the CO. |
|  |  | Once the Emergency has been mitigated, remaining work shall be reclassified to the appropriate classification and considered new work. Provide the Maintenance and Repair *TMR with the scope of work for mitigated or completed work within 24 hours of request. |  | Accurate data provided within the required time frame. |
| 2.3.3 | Critical Spare Parts Management Ensure Availability of Correct Spare Parts for Critical Equipment | Provide all necessary program analysis, field validation, technical research, analysis, failure rate determination, life cycle forecasting, and critical parts determination for critical equipment. The contractor shall recommend to the Government, the critical spares that need to be purchased for all new equipment or equipment that has changed in criticality of use. When equipment is removed from *JSC the Contractor shall recommend changes to the critical spares system. All approved critical spare parts will be procured, received, and warehoused according to Annex 10. Note: The current Critical Spares Catalog includes 3540 line items. | 365 Days | Critical Spare Parts Inventory is accurate. Critical spares are in inventory and available when needed. |
| 2.4 | Maintenance Activation Program Ensure a seamless transition from construction work to site Maintenance and Operations responsibility. | Develop and implement a Maintenance Activation (MA) program to ensure that all necessary changes to the **SM database are made. The changes shall be made whenever required due to the following: |  | Updates are correct and made on time. |
|  |  | Installation of new equipment as part of Repair, Service Orders, or work estimated to cost under $200,000. MA for IDIQ work estimated to cost greater than $200,000 shall be priced per IDIQ in Annex 6. Note: This can be either new capability equipment or replacement equipment. Note: New equipment installed by delivery order shall be added to the **SM Database during the quarterly equipment reconciliation. | 100 pieces of equipment |  |
|  |  | Changes identified through application of maintenance actions, manufacturer's maintenance change bulletins, configuration changes, etc. |  | Nothing additional |
|  |  | Changes identified through the application of the JSC Reliability Centered Maintenance analysis program. |  |  |
|  |  | Tasks in the program include but are not limited to the following: |  |  |
|  |  | Ensure correct Scheduled Maintenance Task Instructions are assigned/written, Government approved and added to the **SM database and the equipment is accurately input. Ensure that the task instructions maintain the manufacturer's warranty in full effect for its scheduled duration. Update **SM database within 14 days of receipt of approved changes. |  | Manufacturers warranties are not voided due to inappropriate maintenance. Updates are accurate and made within the specified timeframe. |
|  |  | Update the FCA database for new and replacement equipment. Update within 4 weeks of receipt of approved changes or receipt of a change order. |  |  |
|  |  | Monitor and verify work performed to ensure additions, deletions, and/or changes to equipment are identified and incorporated into the **SM database. |  |  |
|  |  | Continually track all Scheduled Maintenance task instruction additions (+) and deletions (-). |  |  |
|  |  | Provide a **Quarterly Reconciliation Report for the **SM Database to demonstrate accuracy. The report shall be in electronic form and submitted to the Maintenance and Repair Technical Management Representative (*TMR) within 10 days of the end of each quarter. The report shall contain as a minimum: (1) number of Original Database tasks deleted, (2) the value of Original Database tasks deleted, (3) number of Original Database tasks added, (4) the value of Original Database tasks added, (5) the total costs of Original Database tasks added and deleted, and (6) the net balance of tasks. | 4 Reports | Reports are accurate and submitted on time. |
|  |  | Maintain and continually update the Government provided **SM Database. Provide continual on-line access to the Government and assure that all updates and changes to the database are input by the 10th of each month. |  | The database is accurate and all updates are on time. |
|  |  | Provide outage/operations support for all work classes. This requirement is provided for and found in Annex 4 CLIN 4.1.4. |  |  |
|  |  | Take and record initial (baseline) data using the appropriate Predictive Testing tool (thermography, vibration, oil sample, etc) for equipment installed/replaced. Baseline documentation shall be completed within 15 days of BOD. |  | All new equipment has baseline documentation. |
|  |  | Ensure that the appropriate personnel are correctly trained on new equipment/systems installed by the COSS Contractor and that the appropriate personnel attend provided training for equipment, facilities, or systems provided/installed by other contractors. |  |  |
| 2.5 | Warranty Program Develop and maintain a warranty program. | Develop and maintain a warranty program for warranties received for the Government that includes, but is not limited to the following areas: all warranties for facilities, structures, utilities, construction, and equipment that have been transferred to the property accounts of the Government regardless of the source of the warranty. | Nothing additional. | Warranties accurately tracked and benefits enforced as needed. |
|  |  | a. Administer the warranty program. For construction projects, the normal warranty period is 1 year from the beneficial occupancy date (BOD). The warranty period for some items (typically landscape planting) will be less and others (termite protection, roofs, metal wall panels and certain equipment, etc.) will be longer. Warranty information will be provided on or near BOD and shall be maintained in the TRL for all contractor originated work. Data fields shall be established and updated in the CMMS to track facilities or equipment under warranty. | 300 warranties | Warranty data accurately and completely input into the CMMS. |
|  |  | b. Identification of warranty and warrantor notification. When an anomaly or discrepancy condition is identified on a newly installed item, the Contractor shall determine if a warranty is in effect. If so, the Contractor shall notify the warrantor and request corrective action. Notification may be by telephone, but shall be confirmed in writing, with a copy provided to the CO. If a warranty discrepancy creates an emergency or priority condition, the Contractor shall correct the emergency or priority condition without regard to warranty provisions. | Nothing additional. | Timely notification of Warrantor and CO on corrective warranty actions. |
|  |  | c. Response from the warrantor. When notified of a problem in accordance with the terms of a warranty, the warrantor should correct the problem promptly. However, if the warrantor fails to take corrective action within 14 days (or the construction contract response time, if less) or takes corrective action but fails to correct the discrepancy, the COSS Contractor shall confirm in writing any such action, and immediately provide a copy to the CO. When corrective actions require long lead times (due to parts and material), the COSS Contractor shall obtain an estimated completion date and shall follow-up based on that date in lieu of the 14 days specified above. | Nothing additional. | Written notification to CO of warrantor nonconformance and on time. |
|  |  | d. Actions if warrantor fails to correct discrepancy. If the warrantor fails to correct a warranted item problem within 28 days of initial contact, the Contractor shall make a final request. If the response to the final request is positive, the warrantor shall be allowed 7 additional days to take appropriate action before requesting CO assistance. If at any time, the warrantor declines responsibility under a warranty to the Government, the CO's assistance shall be requested immediately in writing. | Nothing additional. | Final written notification to warrantor on time. |
|  |  | e. Notification to CO of completed warranty work. Monitor warranty work and ensure satisfactory completion. Completed warranty work shall be reported to the CO in writing within 5 days of completion. | Nothing additional. | Accurate notification to CO on time. |
|  |  | f. Provide a monthly status report. This report shall include the most current status of all warranty actions (see items a-e above) performed during the month. Submit an electronic copy of the report to the Maintenance & Repair *TMR by the 5th day of the following month. Completed warranty actions shall be deleted after appearing on the second report. | 12 status reports. | Accurate report, complete, and on time. |
| 2.6 | Availability and Reliability Ensure Available and Reliability of equipment, systems, and components. | Track and report downtime as specified in the **JSC RCM Guideline as required to identify problem areas and ensure reliability of all systems, equipment, and components at JSC, EF, and SCTF. Modify the CMMS system to include two additional fields to track downtime (time and date stamps) and failure codes. Provide metrics reports as identified in AN-1-10 | Contractor Determined | Time/Date Stamps accurately recorded in a timely manner. All reports accurate and on time. |
| 2.7 | Reliability Centered Maintenance Develop and Implement a Reliability Centered Maintenance program | Develop and Implement a Reliability Centered Maintenance Program in compliance with the requirements in the **JSC RCM Guideline. Perform one (1) RCM Analyses per quarter for each year of the contract. Systems, equipment, or components shall be selected as specified in the RCM Guideline or as directed by the Government. b. Provide the training as required in the RCM Guideline in an appropriately phased manner to adequately support the required number of Analysis and to ensure that all applicable employees are trained by the end of the third contract year. | 4 RCM Analyses |  |
| 2.8 | Personnel Requirements |  |  |  |
| 2.8.1 | Provide Qualified Personnel Provide personnel who meet the following education or experience criteria. | See Annex 1 Equivalent criteria may be submitted through the Maintenance and Repair * TMR for approval. Personnel directly supervising individuals with maintenance and repair responsibilities shall successfully complete all education or experience required for the individuals they are supervising. | See below. | Current certification, or evidence of experience, is on hand for individuals performing duties defined above. |

| 2.8.2 | Provide Electrical Personnel Provide Journeyman Electricians, or equivalent title, to perform maintenance and repair and construction actions. | A journeyman shall have successfully completed a 4-year technical program. Technical training may include an accredited technical training program or a recognized, established apprenticeship program. Training may be substituted with progressive "hands-on" experience specifically in the power generator/distribution area on a year-for-year basis, with at least 2 years at an apprentice level. Specific experience shall include cable splicing; switchgear and line work; breakers, meters, transformers, and relays testing and calibration; and electrical generator work on power generator/distribution power systems. | Contractor determined. | Required for individuals working on power generator/distribution systems. Current certification, or evidence of experience, is on hand for individuals performing duties defined above. |
| --- | --- | --- | --- | --- |
| 2.8.3 | Provide Diesel Personnel Provide Journeyman Diesel Mechanics, or equivalent title, to perform maintenance and repair actions. | A Journeyman shall have successfully completed a 4-year technical program. Technical training may include an accredited technical training program or a recognized, established apprenticeship program. Training may be substituted with progressive "hands on" experience specifically in the diesel power generation area on a year-for-year basis, with at least 2 years at an apprentice level. | Contractor determined. | Required for individuals working on diesel generators and associated equipment. Current certification, or evidence of experience, is on hand for individuals performing duties defined above. |
| 2.8.4 | Provide Refrigeration Personnel Provide Journeyman Refrigeration Mechanics, or equivalent title, to perform maintenance and repair actions. | A Journeyman shall have successfully completed a 4-year technical program. Technical training may include an accredited technical training program or recognized, established apprenticeship program. Training may be substituted with progressive "hands on" experience specifically in the air conditioning and refrigeration area on a year-for-year basis, with at least 2 years at an apprentice level. Personnel shall meet the EPA requirements of 40 CFR 82.161. | Contractor determined. | Required for individuals working on direct expansion HVAC and refrigeration equipment. Current certification, or evidence of experience, is on hand for individuals performing duties defined above. |
| 2.8.5 | Provide General Tester Provide certified personnel to perform testing of all backflow prevention assemblies. | Recognized testers shall meet the Texas Natural Resources Conservation Commission (TNRCC) requirements for training and obtain the accredited tester classification for "General Tester" to test and repair backflow prevention assemblies on any domestic, commercial, industrial or irrigation system. NOTE: In accordance with the TNRCC, the test reports and records shall follow their format. The TNRCC states that the "Test and Maintenance report shall be retained for a minimum of 3 years. The public water supplier shall provide these records to the commission staff for inspection upon request." | Contractor determined. | Records of certification shall be made available for documentation of compliance. |
| 2.8.6 | Provide Breaker Tester Complete an accredited course covering breakers, relay and switchgear testing and maintenance. | Accredited courses shall meet or exceed the National Electrical Testing Association Standards. Certification is current for 1 year. Additional follow-up is required annually. | Nothing additional. | Required for individuals working on electrical breakers. Current certification, or evidence of training is on hand for individuals performing duties defined above. |
| 2.8.7 | PT&I Personnel Requirements | The following minimum standards shall be met by personnel performing Predictive Testing & Inspection work: A manager of the vibration program shall maintain a Vibration Level III American Society of Nondestructive Testing (ASNT) Certification. Vibration data collecting personnel shall maintain Vibration Level I Training and vibration analysts shall maintain Vibration Level II Training. | Contractor determined. | Records of certification shall be available for documentation of compliance. |
|  |  | A manager of the Thermography program shall maintain an American Society of Nondestructive Testing (ASNT) Level II Certification. Infrared Thermography scanning personnel shall maintain Thermography Analyst Level I Training, and Infrared Thermography Analysts shall maintain Thermography Analyst Level II Training. |  |  |
|  |  | Vibration and Thermography training requirements for Levels I and II are that the training program pursued shall be one that meets the guidelines set forth for that Technology and Level by the American Society of Nondestructive Testing (ASNT). An internal qualifications training program for the proper use of laser alignment equipment, air born ultrasonic scanner, ultrasonic thickness detector, battery monitoring systems, and collection and analysis of lubricants and insulating oil shall be developed by the Contractor as per the equipment manufacturer's recommendations. Similar qualifications and requirements standards shall be established as new technologies are implemented at JSC, EF, and SCTF. |  |  |
|  |  | A program shall be in place to ensure current qualifications are maintained and refresher courses pursued as needed in all predictive technology areas. |  |  |
| 2.8.8 | Provide Journeyman Linemen or Equivalent Title Provide Journeyman Linemen or equivalent title, to perform maintenance services on the electrical transmission/distribution system and the 15kV facility switches. | A Journeyman shall have successfully completed an apprenticeship-training program. Specific experience shall include cable splicing; switchgear and line work; breakers, meters, transformers, and relays testing and calibration on high voltage systems. | Contractor determined. | Be able to show compliance with training and knowledge requirements. Required for individuals working on 12 kV and higher voltage levels. |
| 2.9 | Records, Reports, and Submittals |  |  |  |
| 2.9.1 | User Equipment Maintenance Report Provide Monthly PM Report | Prepare and submit a report listing the preventive maintenance performed for each User in the PM program purchased by TO. Submit to the M & R (*TMR) by the 20th of each month. The report shall cite the DO, task instruction number, title, and completion date of each task, sorted by User organization. | 12 Reports | Reports are accurate and on time |
| 2.9.2 | Pressure Systems Certification Testing Report Provide Monthly Pressure System Certification Report | Prepare and submit a report listing the pressure systems testing performed during the month. Submit electronically and by hard copy to the M & R (*TMR) by the 10th of each month. The report shall cite the task instruction number, verbal description, location, type of test, status of all task orders received, task due date and completion date, list of backlogged tasks, reason for delay and new scheduled date, and significant events that occurred. | 12 Reports | Reports are accurate and on time |