SPECIAL SPECIFICATION

SECTION 15890

DUCTWORK SYSTEMS

Page

PART 1 - GENERAL

1.01  	Work Included	3

1.02  	Related Work	3

1.03  	Guarantee	3

1.04  	Contractor Coordination	3

1.05  	Standards And Codes	4

1.06  	Definitions	4

1.07  	Submittals	4

PART 2 - PRODUCTS

2.01  	Sheet Metal Ductwork-Rectangular Rigid Round	5

2.02  	Low Pressure Ductwork	5

2.03  	Medium Pressure Round/Oval Double-Wall Ductwork	8

2.04  	Seal Of Seams And Joints	13

2.05  	Pvc Ductwork	13

PART 3 - EXECUTION

3.01  	Installation1	4

3.02  	Low Pressure Ductwork	16

3.03  	Medium Pressure Ductwork	17

3.04 	Opening In Ductwork	18

3.05  	Flashing	18

3.06  	Duct Lining	18

3.07 	Installation - Pvc Ductwork	19

3.08  	Tests	19

3.09  	Adjusting And Cleaning	20

SPECIAL SPECIFICATION

SECTION 15890

DUCTWORK SYSTEMS

PART 1 - GENERAL

1.01	WORK INCLUDED

This section provides for furnishing and installing air ductwork for ventilating, exhaust, air handling unit distribution and VAV box distribution.

Ductwork involved will be double wall round/oval, single wall rigid round, single wall rectangular, flexible duct and below floor PVC ductwork.

1.02	RELATED WORK

A.	Insulation - Mechanical Systems:  Section 15250

B.	System Component Checkout and Balance:  Section 15901

1.03	GUARANTEE

Ductwork guarantee shall cover workmanship, noise, chatter, whistling or vibration. Ductwork shall be free from pulsation under all conditions of operation.

1.04	CONTRACTOR COORDINATION

Erect all ducts in the general locations shown on the drawing(s), but conform to all structural and finish conditions of the building.  Before fabricating any ductwork, Contractor shall check the physical conditions at the job site and make all necessary changes in cross sections, offsets and similar items, whether they are specifically indicated on drawings or not.

1.05	STANDARDS AND CODES

A.	Except as otherwise indicated, sheet metal ductwork material and installation shall comply with the latest edition of SMACNA Low Pressure Duct Construction Standards.  Medium pressure round/oval double wall sheet metal ductwork shall comply with the latest edition of SMACNA High Pressure Duct Construction Standards.  All air distribution devices (such as dampers) included in this specification shall comply with the latest applicable SMACNA manual.

B.	Construct ductwork and all air distribution devices to NFPA 90A, NFPA 90B and NFPA 96 standards.

1.06	DEFINITIONS

A.	Duct Size.  The duct sizes shown are inside clear dimension and do not include proper allowances for 1-inch acoustical lining, if required, and/or unless otherwise indicated.

B.	Low Pressure Systems.  Less than 3-inches w.g. to +3-inches w.g. positive static pressure and velocity less than 2500 fpm.

C.	Medium Pressure System.  3 inches through 6 inches w.g. positive static pressure and velocities greater than 2000 fpm. (10.2 m/sec).

1.07	SUBMITTALS

A.	Submit ductwork shop drawings and product data in accordance with Section 01300.

B.	Indicate duct fittings, particulars such as gages, sizes, weld and configuration prior to start of work for low, medium and high pressure and exhaust systems.

PART 2 - PRODUCTS

2.01	SHEET METAL DUCTWORK - RECTANGULAR/RIGID ROUND (SINGLE-WALL) (DOUBLE-WALL)

A.	Acceptable Manufacturers

1.	United McGill - Spiral round single and double-wall ductwork.

2.	Gowco - spiral round single and double-wall ductwork.

3.	Sheet Metal Products - spiral round sinble and double-wall ductwork.

4.	Thermaflex - insulated flexible duct.

5.	Contractor Shop Fabrication - single wall rectangular ductwork.

2.02	LOW PRESSURE DUCTWORK

A.	General.  Noncombustible or conforming to requirements for Class I air duct materials or UL 181.

B.	Steel Ducts.  ASTM A 525 or ASTM A 527, galvanized steel sheet, lock-forming quality, having zinc coating of 12.25 ounces per square foot for each side in conformance with ASTM A 90.

C.	Flexible Ducts.  Interlocking spiral of galvanized steel or aluminum construction, or fabric supported by helically wound spring steel wire or flat steel bands; rated to 6 inches w.g. positive and 1 inch w.g. negative for low pressure ducts, and 15 inches w.g. positive and 2 inches w.g. negative for medium high-pressure ducts.  Insulation shall not breed or promote fungi or bacteria, shall resist mold growth, shall not rot or sustain vermin.

D.	Insulated Flexible Ducts.  Flexible duct wrapped with flexible glass fiber insulation, enclosed by seamless aluminum pigmented plastic vapor barrier jacket; maximum 0.23 K value at 75 degrees F *0.034 ksi at 24 degrees C).

E.	Rectangular.  Provide rectangular low pressure ducts constructed of sheet metal in the following minimum gages:

Largest Dimension				U.S. Gage

inches

12" and less					No. 26

13" to 30"					No. 24

31" to 54"					No. 22

55" to 84"					No. 20

85" and above					No. 18

F.	Fabricate and support in accordance with SMACNA Low Pressure Duct Construction Standards and ASHRAE handbooks, except as indicated.  Provide duct material, gages, reinforcing and sealing for operating pressures indicated.

G.	Rigid, Single-Wall Round.  Furnish round, low pressure ducts which are spiral wound, such as manufactured by United McGill Company, or shop-fabricated round ducts with Pittsburgh lock longitudinal seams.  Use the following gages for shop-fabricated ducts:

Diameter - Round				U.S. Gage

inches

12" and less					No. 26

13" to 30"					No. 24

31" to 42"					No. 22

43" to 60"					No. 20

H.	Size round ducts installed in place of rectangular ducts in accordance with ASHRAE Table of Equivalent Rectangular and Round Ducts.  No variation of duct configuration or sizes permitted except by written permission.

I.	Low Pressure Insulated Flexible Duct.  Provide factory-fabricated flexible duct for connections between low pressure trunk ducts and supply air diffusers.  Furnish flexible duct with an airtight inner liner, insulation and outer jacket.  Construct the inner liner of coated steel helix and fabric substantially bonded together to prevent the duct from collapsing or kinking in short radius bends.  Provide fiberglass insulation at least 1 inch thick and 3/4-pound minimum density around the inner liner.  Sheath the entire assembly with heavy, outer vapor barrier jacket of reinforced aluminum foil kraft.  Maximum length of flexible duct is 6 feet and hold in place with strap or clamp.  Use a supply duct rated at a minimum positive working pressure of 6 inches of water.  Exhaust ducts must withstand a negative pressure of 1 inches of water.  Provide duct listed by UL at flame spread rate of not over 25 and smoke developed rate of not over 50, and complying with NFPA Standard 90A.

J.	Construct tees, bends and elbows with radius of not less than 1-1/2 times the width of duct on centerline.  Where not possible or where rectangular elbows are shown, provide double-wall, airfoil, galvanized sheet metal turning vanes. The turning vanes shall be fabricated in accordance with SMACNA HVAC Duct Construction Standards.

K.	For round duct, provide the elbows with a centerline radius of 1-1/2 times the duct diameter and furnish smooth elbows or 5-piece, 90-degree elbows and 3-piece, 45-degree elbows.

L.	Increase duct sizes gradually, not exceeding 15 degrees divergence wherever possible.  Divergence upstream of equipment shall not exceed 30 degrees; convergence downstream shall not exceed 45 degrees.

2.3	MEDIUM PRESSURE ROUND/OVAL DOUBLE-WALL

A.	Rigid Round (Double-Wall)

1.	Round duct will be constructed of a perforated inner liner, a 1-inch layer of fiberglass insulation (insulation shall not breed or promote fungi or bacteria, shall resist mold growth, shall not rot or sustain vermin), and an outer solid pressure shell.  Duct will be of spiral lockseam construction, provided in standard lengths of 10, 12, and 20 feet, or otherwise as specified.  It will be fabricated from galvanized steel meeting ASTM-A527 standards, and in accordance with the following table:

Inner Liner	  Outer Shell	Inner Liner	 Inner Liner

Diameter	 Minimum Gauge	  Gauge	Construction

(inches)	(2-10 inches wg)

3- 8	26	28	Standard Spiral

9-12	26	28	Ribbed Spiral

13-24	24	28	Ribbed Spiral

25-34	22	28	Ribbed Spiral

For 1-inch insulation, the outer pressure shell will be 2 inches larger than the inner liner (nominal) dimension.

2.	Perforated liner perforations will be 3/32 inch in diameter with an overall open area of 23 percent.  Insulated duct will have a maximum thermal conductivity (k) factor of 0.27 Btu per hour per square foot per degree Fahrenheit per inch thickness at 75°F mean ambient temperature.

3.	Round fittings will be constructed of a perforated inner liner, a 1-inch (unless otherwise specified) layer of fiberglass insulation, and an outer solid pressure shell.  Fittings will be constructed of galvanized steel meeting ASTM-A527 standards, and in accordance with the following table:

Inner Liner	  Outer Shell	Inner Liner

Diameter	 Minimum Gauge	  Gauge

(inches)	(2-10 inches wg)

3-12	24	24

13-24	22	24

25-34	20	24

a.	For 1-inch insulation, the outer pressure shell will be 2 inches larger than the inner liner (nominal) dimension.

b.	Unless otherwise specified, standing seam joints will be used wherever possible on all fittings.  All standing seam joints will be sealed with a UL-Classified zero flame spread and zero smoke developed cement specially formulated for bonding metal-to-metal joints.

c.	In lieu of standing seam construction, joints may be solid welded or spot welded and bonded.  All welded joints will be coated with a protective paint, inside and out, to prevent damage to the galvanized surface.  Spot welded fittings will have all joints sealed with a UL-Classified zero flame spread and zero smoke developed cement specially formulated for bonding metal-to-metal joints.

d.	Elbow outer shells will be of die-stamped, gored, or mitereed construction.  Elbow liners will be gored unless two-piece mitered construction is specified.

e.	Divided-flow fittings will be constructed with a radiused entrance to all branch taps and with no excess material projecting from the body into the branch tap entrance.

f.	Perforated liner perforations will be 3/32 inch in diameter with an overall open area of 23 percent.  Insulated fittings will have a maximum thermal conductivity (k) factor of 0.27 Btu per hour per square foot per degree Fahrenheit per inch thickness of 75°F mean ambient temperature.

4.	All double-wall duct and fittings will be furnished with both an inner liner coupling and an outer pressure shell coupling.  Outer shell connections can be by slip joint or flanged joint; however, flanged joints are recommended for outer shell diameters greater than 36 inches.  In either case, a slip coupling will be used to join inner liner sections at duct-to-duct joints.  Fitting liners will be extended 2 inches beyond the outer shell cutoff to provide an inner liner coupling at duct-to-fitting joints.  When flanged joints are used, angle rings will be Van Stoned to fittings and welded to duct.  Spiralmate connectors are available.

B.	Rigid Oval (Double-Wall)

1.	Flat oval duct will be constructed of a perforated inner liner, a 1-inch layer of fiberglass insulation (insulation shall not breed or promote fungi or bacteria, shall resist mold growth, shall not rot or sustain vermin), and an outer solid pressure shell.  Duct will be of spiral lockseam construction, provided in standard lengths of 6, 10, and 12 feet, or otherwise as specified.  It will be fabricated  from galvanized steel meeting ASTM-A527 standards, and with outer shell gauges in accordance with the following table.  (For 1-inch insulation, the outer shell major and minor axes will be 2 inches larger than the nominal inner liner dimensions).

Inner Liner			 Outer Shell

Major Axis Dimension		Minimum Gauge

(inches)

7-22				24

23-46				22

2.	Flat oval inner liners will be fabricated in accordance with the following table:

Inner Liner

Basic Round Diameter	Gauge	Construction

(inches)

3- 8	 28	Standard Spiral

9-42	 28	Ribbed Spiral

3.	Perforated liner perforations will be 3/32 inch in diameter with an overall open area of 23 percent.  Insulated duct will have a maximum thermal conductivity (k) factor of 0.27 Btu per hour per square foot per degree Fahrenheit per inch thickness at 75°F mean ambient temperature.

4.	Flat oval fittings will be constructed of a perforated inner liner, a 1-inch (unless otherwise specified) layer of fiberglass insulation, and an outer pressure solid shell.  Fittings will be fabricated from galvanized steel meeting ASTM-A527 standards, and with outer shell gauges in accordance with the following table.  (For 1-inch insulation, the outer shell major axis will be 2 inches larger than the nominal inner liner major axis).

Inner Liner		 Outer Shell

Major Axis Dimension		Minimum Gauge

(inches)

7-34			20

Round dimensions on flat oval fittings will be constructed in accordance with the following table:

Inner Liner Diameter		 Outer Shell

(inches)		Minimum Gauge

3-34			20

Flat oval inner liners will be fabricated in accordance with the following table:

Inner Liner

Basic Round Diameter		Gauge

(inches)

3-34		  24

a.	Unless otherwise specified, standing seam joints will be used wherever possible on all fittings.  All standing seam joints will be sealed with a UL-Classified zero flame spread and zero smoke developed cement specially formulated for bonding metal-to-metal joints.

b.	In lieu of standing seam construction, joints may be solid welded or spot welded and bonded.  All welded joints will be coated with a protective paint, inside and out, to prevent damage to the galvanized surface.  Spot welded fittings will have all joints sealed with a UL-Classified zero flame spread and zero smoke developed cement specially formulated for bonding metal-to-metal joints.

c.	Elbow will be of gored or mitered construction.  Flat oval mitered elbows will be solid welded.

d.	Divided-flow fittings will be constructed with a radiused entrance to all branch taps and with no excess material projecting from the body into the branch tap entrance.

e.	Perforated liner perforations will be 3/32 inch in diameter with an overall open area of 23 percent.  Insulated fittings will have a maximum thermal conductivity (k) factor of 0.27 Btu per hour per square foot per degree Fahrenheit per inch thickness of 75°F mean ambient temperature.

5.	All duct and fittings will be provided with both an inner liner coupling and an outer pressure shell coupling.  Outer shell connections can be by slip joint, FORC connection, or flanged joint; however, flanged joints are recommended for sizes with major axis dimensions greater than 42 inches.  In either case, a slip coupling will be used to join inner liner sections at duct-to-duct joints.  Fitting liners will be extended 2 inches beyond the outer shell cutoff to provide an inner liner coupling at duct-to-fitting joints.  When flanged joints are used, angle rings will be Van Stoned to fittings and welded to duct.

2.04	SEALS OF SEAMS AND JOINTS

The entire duct system shall be sealed in accordance with Table 1-2, Duct Sealing Requirements, in the latest edition of SMACNA HVAC Duct Construction Standards.

2.05	PVC DUCTWORK

A.	Acceptable Manufacturers

1.	PVC Plastic Company - ITS Division.

2.	Vanaire Ltd.

3.	Met-Pro Corp. - Duall Division.

B.	All ductwork shall be rigid, unplasticized polyvinyl chloride (PVC) with heat welded joints.  Ducts and accessories shall conform with the SMACNA Thermoplastic Duct Construction Manual.

C.	Materials Requirements

1.	Ductwork shall be extruded seamless.  Compounds utilized in the manufacture of these base components shall conform to the PVC Materials standard ASTM D 1784-69.

D.	Duct Construction - PVC

1.	Extruded material where used shall be manufactured from the basis compounds as specified above.  Extruded duct shall be acceptable in sizes 6" - 24".  The size of round duct shall be determined by the inside diameter.  The tolerance, including out of roundness should be plus or minus 3/16 inch for diameters up to 18 inches.

2.	Extruded Round Duct.  6" round through 18" round to have 3/16" wall thickness.  24" round to have 1/4" wall thickness.

3.	Round extruded duct shall be available in nominal 20 ft. lengths. Round duct fittings shall be mitered straight lengths of duct.  All fittings shall have belled ends to provide a bell and spigot joint connection.  The 90° fittings will have five (5) gore and the 45° fittings will be three (3) gore both with 1-1/2 times center line radius. All fittings to be designed to VA15D to assure consistent quality and interchangeability.

E.	Duct Connections

1.	Round duct joints and fittings to be welded with 5/32 dia. PVC rod.

F.	Dampers (Blast Gate)

1.	Furnish and install dampers as indicated on the drawing and additional dampers are to be installed at all locations where required for balancing or adjust in the system.

PART 3 - EXECUTION

3.01	INSTALLATION - SHEET METAL DUCTWORK

A.	Construction Standards.  Use construction methods which follow the requirements outlined in paragraph 1.4, as well as SMACNA Balancing and Adjusting publications, unless indicated otherwise in these specifications or accompanying drawings.

B.	Reinforcement.  Reinforce ducts having one side equal to 25 inches or more in accordance with recommended construction practice of SMACNA.

C.	Plenum Construction.  Construct single-wall and 2" (thick insulation double-wall) plenum chambers of not less than No. 20 U.S. gage meatal reinforced with galvanized structural angles.

D.	Cross Breaking or Beading.  Cross break or bead sheet metal for rigidity, except ducts which are 12 inches or less in the longest dimension.

E.	Wall Penetrations.  Where ducts pass through walls in exposed areas, install suitable escutcheons made of sheet metal angles as closers.  At all locations where ductwork passes through floors, provide watertight sleeves projecting 3 inches above finished floor and flush with bottom of floor slab.  Fabricate sleeves of 1/8-inch thick steel, galvanized after fabrication.  Anchor into adjacent floor slab as required.  Provide sleeves inside as well as outside chases.  Support ducts where passing through floors with steel structural angles of adequate bearing surface, galvanized after fabrication and resting on top of the sleeve.

F.	Interior Painting.  Paint flat black, the interior of metal ductwork exposed to view through grilles, registers, and other openings.  Do not install grilles, registers, or similar items until painting is complete.

G.	Ductwork Openings.  Provide openings in ductwork where required to accommodate thermometers and controllers.  Provide pilot tube openings where required for testing of systems, complete with metal can with spring device or screw to ensure against air leakage.  Where openings are provided in insulated ductwork, install insulation material inside a metal ring.

H.	Ductwork Location.  Locate ducts with sufficient space around equipment to allow normal operating and maintenance activities.

I.	Sealant.  The entire duct system shall be sealed.  Nonhardening, water resistant, fire resistive, compatible with mating materials; liquid used along or with tape, or heavy mastic.  Duct shall be thoroughly cleaned prior to application of sealant.  All transverse joints, longitudinal seams and duct wall penetrations shall be sealed.  All ductwork shall be sealed as per seal Class A irrespective of the duct pressure classifications.

J.	Hangar Rod.  Galvanized steel, threaded continuously.

3.02	LOW PRESSURE DUCTWORK

A.	Construction.  Construct rectangular ducts in accordance with the SMACNA Duct Manual.  Construct round ducts in accordance with Section III of the SMACNA HVAC Duct Construction Standards Manual.

B.	Controls.  For control devices concealed by ceilings, furring, or in other inaccessible locations, furnish extension rods and appropriate recessed-type Young regulators, mounted on the surface of the ceiling or the furring, unless specified, or shown otherwise.  For ducts which are not concealed, or ducts which are above lay-in ceiling but accessible, provide heavy-duty, quadrant-type, adjustable regulators having wing nuts for locking in position.  Saw-mark the ends of all operating rods for dampers and air control devices to indicate damper position.

C.	Obstruction.  Install streamline deflectors at any point where dividing a sheet metal duct around piping or where other such obstruction is permitted. Where such obstructions occur in insulated ducts, fill space inside streamliner and around obstructions with glass fiber insulation.

D.	Low Pressure Insulated Flexible Duct.  Do not exceed 6 feet in length with any flexible duct.  Make end connections with 3M 900 mastic and stainless steel screw band.  Support duct independently of lights, ceiling and piping.

E.	Low Pressure Duct Supports.

1.	Horizontal Ducts Up to 40 Inch.  Support horizontal ducts up to and including 40 inches in their greater dimension by means of No. 18 U.S. gage band iron hangers attached to the ducts by means of screws, rivets or clamps, and fastened to inserts with toggle bolts, beam clamps or other approved means.  Place supports on at least 8'-0" centers.  Use clamps to fasten hangers to reinforcing on sealed ducts.

2.	Horizontal Ducts Larger Than 40 Inch.  Support horizontal ducts larger than 40 inches in their greatest dimension by means of hanger rods bolted to angle iron trapeze hangers.  Use double nuts and lock washers on threaded rod supports.  Place supports on at least 8'-0" centers according to the following:

Angle Length		Angle		Rod Diameter

Feet		Inches		     Inch

4'-0"		1-1/2"x1-1/2"x1/8"		1/4"

6'-0"		1-1/2"x1-1/2"x1/8"	1/4"

8'-0"		2"x2"x1/8"	5/16"

10'-0"		3"x3"x1/8"	3/8"

3.	Vertical Ducts.  Support vertical ducts where they pass through the floor lines with 1-1/2" x 1-1/2" x 1/4" angles for ducts up to 60 inches. Above 60 inches, the angles must be increased in strength and sized on an individual basis considering space requirements.

3.03	MEDIUM PRESSURE DUCTWORK

A.	Rectangular.  Construct rectangular ducts as noted before.  Provide reinforcing method as shown without tie rods through 60-inch size.  For rods 61 inches and over, use tie rods to keep reinforcing angles to 2-inch minimum.  Use sealant (3M EC-800) or equal and 4-inch wide Glasfab or continuous welds at all of the longitudinal seams, and flanged (calk or gasket) transverse joints on rectangular ducts in shop and field fabrication to provide positive seal.

B.	Round.  Provide round, medium-pressure duct construction as noted before. Seal joints with 3M EC-800, lapped a minimum of 3 inches, secured with sheet-metal screws and covered with sealant, over which is applied a 4-inch wide Glasfab cloth.  Apply additional sealant until the cloth is completely embedded, or welded.  Make 90-degree branch take-offs with conical tees. Weld take-off fittings to fittings or to the main duct.  Clean and coat all welds with rust-inhibiting paint.  Stamp elbows as smooth-type, or 5- or 3-piece segmented or segmented standing seam type,l with either type having a centerline radius of 1-1/2 times the duct diameter.

C.	Medium pressure Insulated Flexible Duct.  Seal flexible duct connections with 3M 900 mastic and stainless steel clamp.  Support duct independently of lights, ceiling and piping.

D.	Medium Pressure Duct Supports.  Provide hangers and supports in accordance Low Pressure Duct.

3.04	OPENING IN DUCTWORK

Provide opening in ductwork where required to accommodate thermometers and controllers.  Provide pilot tube openings where required for testing of systems, complete with metal can with spring device or screw to ensure against air leakage. Where openings are provided in insulated ductwork, install insulation material inside a metal ring.

3.05	FLASHING

Where ducts pass through roofs or exterior walls, provide suitable flashing to prevent rain or air currents from entering the building.  Provide flashing not less than No. 26 gage stainless steel or 16-ounce (450 g) copper.

3.06	DUCT LINING (LOW PRESSURE - RECTANGULAR)

Install glass fiber acoustical lining in all rectangular (except exhaust) ductwork shown on drawings.  Provide 1-inch thick, 3-pound density, flexible lining coated on the air stream side to reduce attrition.  Secure to duct surfaces with Foster 85-22 adhesive and sheet metal fasteners on 12-inch centers.  Omit lining as necessary to permit satisfactory operation of air control devices.  Coat all exposed edges and leading edges of cross joints with adhesive.  Insulation shall not breed or promote fungi or bacteria, shall resist mold growth, shall not rot or sustain vermin.

3.07	INSTALLATION - PVC DUCTWORK

Follow manufacturer's written instructions and recommendations with the following minimum guidelines.

A.	Welding.  All welding to be done by the hot gas fusion welding method using PVC Filler Rod as manufactured for this purpose.  Welding shall be performed by workmen adequately trained in the art of PVC welding. Ductwork must be air tight.  Use three passes with 5/32" (4 mm) rod. Wherever possible there shall be one interior weld in addition to the exterior welds for added strength.

B.	Branches.  To enter main at no more than forty-five degrees (thirty degrees preferred) to direction of flow and wherever practical to enter on an enlarging taper section.  Branches should not enter opposite each other. Branches to be continuously welded to main.

3.08	TESTS

A.	Allowable Leakage.  Test ductwork for leaks before concealing.  Maximum allowable leakage is 5 percent of total flow.

B.	Equipment.  Provide equipment necessary for performing tests, including rotary blower, orifice section and U-tube gage board complete with cocks and rubber tubing.

C.	Risers and Branch.  Test duct riser or branch duct including flexible duct runouts in accordance with SMACNA manual.

D.	Mains.  Test mains after risers and branches are tied in and all equipment set.  Close runout connections and place fan in operation.  Provide pressure in mains above design pressure.  Visually inspect joints.  Repair leaks detected by sound or touch.  Release mains for completion after joints are tight.

3.09	ADJUSTING AND CLEANING

A.	Clean duct system and force air at high velocity through duct to remove accumulated dust.  To obtain sufficient air, clean half the system at a time. Protect equipment which may be harmed by excessive dirt with temporary filters, or bypass during cleaning.

END OF SECTION