COMMUNICATIONS SITE PLAN

GRIZZLY MOUNTAIN

COOS BAY DISTRICT OFFICE

Prepared by the United States Bureau of Land Management

Coos Bay District Office

State of Oregon

Approved by: ____Pat Ryan__________________________________    _12/01/2005____

Field Manager						Date

GRIZZLY MOUNTAIN COMMUNICATIONS SITE PLAN

I.	INTRODUCTION	3

A.	Terms and Definitions	3

B.	Purpose	4

C.	Site Description	5

D.	Area Served	5

E.	Access	5

F.	Site History and Development	5

G.	Goals and Objectives of Site Management Plan	6

II.	AUTHORITY AND DIRECTION	7

A.	Authority	7

B.	Relationship to Communications Site Lease and ROW Grant	7

III.	GENERAL RESPONSIBILITIES	7

A.	The BLM	7

B.	Facility Owners and Facility Managers 	8

C.	FCC and NTIA/IRAC 	9

IV.	AUTHORIZED USES AND USERS WITHIN A FACILITY	9

Use by Multiple Users	9

V.	FEES	10

VI.	General Operation and Maintenance Direction	10

A.	Unique Resource Considerations at this Communication Site	10

B.	Wiring and Grounding	11

C.	Communications Equipment	11

D.	Cables and Transmission Line (Wave Guides)	14

E.	Radiation	14

F.	Utilities-Availability of and Requirements for:	15

G.	Sanitary Facilities	16

H.	Security and Law Enforcement	16

I.	Site Maintenance	17

J.	Inspections	17

K.	Fire Prevention and Hazard Reduction Requirements	18

L.	Access Maintenance and Restrictions	19

VII.	CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION	19

A.	New Facility Owner Responsibilities	19

B.      Construction Methods and Resource Protection	21

C.	Construction Inspection	22

D.	New or Remodeled/Expanded Buildings	22

E.	New or Remodeled/Expanded Towers	23

VIII.	SITE ASSOCIATION/ADVISORY GROUP	24

IX.	APPENDICIES	24

A.	Site Map	24

B.	Authorized Facilities	24

C.	Site Photographs	24

D.	Inspection Checklist	24

E.	Association Constitution and By-Laws	24

INTRODUCTION

## Terms and Definitions

The terms used in this communications site management plan conform to the definitions listed in the April 22, 2005, Federal Register notice “Rights-of-Way, Principles and Procedures: Rights-of-Way Under the Federal Land Policy and Management Act and the Mineral Leasing Act”

and clarifications provided in Bureau of Land Management (BLM) Handbook 2860-1 and the United States Code of Federal Regulations (CFR) 43 2800.  In the event of a conflict, between the plan and these sources, the Federal Register notice and the BLM Handbook will govern.

The words “lease” and “lessee” as used in this plan refer to the relationship between the BLM and the communications use leaseholder, the lessee.  The words “customer” and “tenant” refer to the relationship between the lessee and the occupants in the lessee’s facilities.

LEASE – An authorization issued to a communication Facility Owner or Facility Manager, allowing for the use of Public Lands to construct and or operate a communications facility and unless specifically prohibited, to sublease to occupants in that facility.

LEASEHOLDER OR LESSEE – Facility Owner/Facility Manager

CUSTOMER – Entities that pay a facility owner, facility manager or tenant for communications services and are not re-selling or broadcasting communications services to others

TENANT – A communications user who rents space in a communications facility and operates communication equipment for the purpose of re-selling, or broadcasting communications services to others for profit.

COMMUNICATIONS SITE – An area of BLM-managed public land designated through the land and resource management planning process as being used or as suitable for communications uses.  A communications site may be limited to a single communications facility, but most often encompasses more than one.  Each site is identified by name; usually a local prominent landmark, such as Grizzly Mountain Communications Site.

FACILITY MANAGER – The holder of a BLM communications use authorization who leases space for other communication users.  A facility manager does not directly provide communications services to third parties.

FACILITY OWNER – Individuals, commercial entities, organizations, or agencies that own a communications facility on Federal land; own and operate their own communications equipment; and hold a communications use authorization.

NON-BROADCAST – This category includes Commercial Mobile Radio Service (CMRS), Facility Managers, Cellular Telephone, Private Mobile Radio Service (PMRS), Microwave, Local Exchange Network, and Passive Reflector.

BROADCAST – This category includes Television Broadcast, AM and FM Radio Broadcast, Cable Television, Broadcast Translator, Low Power Television, and Low Power FM Radio.

RIGHT-OF-WAY – The public lands authorized to be used or occupied pursuant to a right-of-way grant.

RIGHT-OF-WAY GRANT – An instrument issued pursuant to Title V of the Federal Land Policy and Management Act of October 21, 1976 (U.S.C. 1701 et seq.) or issued on or before October 21, 1976, pursuant to then existing statutory authority, authorizing the use of a right-of-way over, upon, under or through public lands for construction, operation, maintenance and termination of a project.

HOLDER – Any applicant who has received a right-of-way grant or temporary use permit.

ACRONYMS – ANSI, American National Standards Institute; BLM, Bureau of Land Management;  CFR, Code of Federal Regulations;  FCC, Federal Communications Commission;  FAA, Federal Aviation Administration;  NEPA, National Environmental Policy Act;  NTIA, National Telecommunication and Information Administration; IRAC, Interagency Radio Advisory Committee;   RFR, Radio Frequency Radiation;  ROW, Right-of-Way;   RMA, Ranally Metro Areas;  RMP, Resource Management Plan;

## Purpose

This plan will be used by BLM officials, administering communications uses at Grizzly Mountain, existing lessees, holders, and applicants desiring a lease, grant, or an amendment to an existing lease or grant.  The plan will be kept updated by amending pages or sections of the plan rather than issuing a revised edition of the plan.  When a revision is necessary, a review will be made by the User’s Association and then a letter approving the revised pages or section will be sent to each authorization holder to signed by the Coos Bay District Office to amend this plan.  The amendments will be consecutively numbered.

Overall management direction for the administration of communications sites is outlined in the U.S. Code of Federal Regulations (CFR’s) and the BLM Handbook and applicable BLM Instructional Memoranda.  Specific direction for site management planning on designated communications sites is contained in BLM Handbook 2860-1.  Primary regulations and policy pertaining to issuance of ROW authorizations by the BLM are found in Title 43, Code of Federal Regulations (CFR), Sections 2801- 2803 and BLM Handbook 2860-1

This site is in the Coos Bay District Resource Management Plan (RMP), which was approved in 1994.  The site is covered by General Objectives as described in Chapter 2-88 and as shown on Map 2-11.

No previous communications site plan has been approved for this site. This Site Management Plan incorporates current direction, applicable guidance, policy, and technical standards for better management of the Grizzly Mountain Communications Site.  This plan governs development and management of Grizzly Mountain and will be modified in the future as needs and conditions warrant.  Any future uses must be designed, installed, operated, and maintained to be compatible and not interfere with the senior uses.  This site-specific plan is administrative in nature and is Categorically Excluded from further review under the National Environmental Policy Act (NEPA) (516.DM2, Appendix 1,1.7).  Any additional development of the site will be addressed in a site-specific NEPA document.

## Site Description

The site is located on Grizzly Mountain east of Gold Beach on the southern Oregon coast and east of Highway 101.  The area is managed by the Myrtlewood Resource Area, Coos Bay District Office and the site is specifically located in portions of Section 4, T. 37 S.., R. 14 W., Willamette Meridian approximately 42º 23’ 49” North Latitude and 124º 21’ 54” West Longitude.  The elevation at the Grizzly Mountain Communications Site is approximately 2,323 feet above mean sea level.   A site map is provided as Appendix A.

## Area Served

This site does not serve a Ranally Metro Area, RMA.  The population zone served is less than 25,000 (Zone 9).  These zones may be adjusted in the future as population change.  This information will be used for fee determination.

## Access

Access to Grizzly Mountain is from Highway 101 at 3rd Street in Gold Beach then east on Grizzly Mountain County Road to the end of county maintenance, then through Crook Estates lands and across 5 private residential parcels.

The portion of access road that crosses the private residential parcels and lands owned by the Crook Estates do not have recorded rights of ingress or egress.  A separate road maintenance agreement between the private land owners and the Grizzly Mountain communications site users association is strongly encouraged..

## Site History and Development

The initial communications facilities on Grizzly Mountain was issued to Community TV Association for television translators, the Forest Service in 1960 for two-way radio and West Coast Telephone, now Verizon for a microwave facility at this site.  The Oregon Department of Forestry was authorized a grant for a fire protection lookout and two-way radio in 1962.  In 1991, when the lookout was no longer needed for fire detection, the US Coast Guard was authorized to occupy the old lookout as an equipment shelter and authorized to construct a separate tower.   Coos County Electric Coop was authorized to construct a facility at this site for two-way radio and also houses KGBR FM a low power FM radio station.

Curry County EMS was granted a ROW in 1980 for emergency radio repeaters, located with Oregon Dept of Forestry.  The Curry County Sheriff received their authorization in 1983 and the Oregon State Police in 1987.  These systems are located on separate towers, but in the same building as the Oregon Dept of Forestry.

In 1988, Gold Beach Gospel Echoes was authorized to occupy space in the lookout building.  This is a low power translator system. Ramcell of Oregon was authorized to install a facility for cellular coverage in 1994.

Space in the existing buildings and towers to serve this area is limited, but appears adequate for the current and future demand. The County and State plan to remove their old building and towers and replace them with a new larger facility which will accommodate all of their current and future needs on a single tower and building.  Any modifications to existing facilities or proposals for new facilities must be approved by the Coos Bay District Office according to the appropriate NEPA process and guidance described in this document.

## Goals and Objectives of Site Management Plan

1.	Manage the Grizzly Mountain Site as a low power site two-way radio, microwave and low power broadcast.  All uses must be designed, operated and maintained so as not to materially or electronically interfere with the senior uses.

2.	Manage communication equipment on the Grizzly Mountain Site to maintain the RFR hazard to be within the Public Standard as defined by the FCC.

3.	Systematically develop the site to maximize the number of compatible uses while ensuring safety and protection of resources.  Development of new towers or buildings within each of the authorized owner’s facilities will be authorized only after their respective tower or building space area is filled to near capacity.

4.	Present a program for future growth, development and operation within the site.

5.	Help fulfill the public need for adequate communications sites.

6.	Protect the interests of leaseholders and site users by preserving a safe and electronically “clean” environment.

7.	Encourage the efficient development and use of space and facilities within the designated site, subject to the BLM’s goal to provide the best possible public service at a reasonable cost.

8.	Achieve visual quality objectives by requiring design standards that are unobtrusive and utilizing earth tone colors and non-reflective surface material and stringent site maintenance requirements.

9.	Describe the BLM’s policy for authorizing road use and maintenance.

10. Developed new facilities only after the appropriate site-specific NEPA analysis and coordination with current leaseholders and users.  This future development must also be consistent with the Coos Bay District Office RMP and any future revisions to the plan.

11.	Encourage a Communications Site Users Association for road access, maintenance, and fuel break maintenance as well as on-site user coordination.

AUTHORITY AND DIRECTION

## Authority

BLM authority to authorize communications uses on Public Land (administered by the BLM) is granted by the Federal Land Policy and Management Act of 1976, 90 Stat. 2776 (43 U.S. C. 1761-1771) and is reflected in Title 43, Code of Federal Regulations (CFR), Sections 2801- 2803 and WO IB 98-23.

BLM authority for communications site management planning is contained in BLM Handbook 2801-1, Plan of Development.  Direction on, and policy for communication use authorizations is contained in BLM Manual (BLM Manual) section 2860.

Authority for the issuance of authorizations and/or licenses for the transmission and reception of electronic radiation for communication purposes is granted by Congress and administered by the Federal Communications Commission (FCC) and/or the National Telecommunication and Information Administration – Interagency Radio Advisory Committee (NTIA/IRAC).

## Relationship to Communications Site Lease and ROW Grant

This site plan will be incorporated into all leases and grants issued (now and/or in the future) for this communications site and must be used in conjunction with the granting authorization. PROVISIONS OF THE SITE PLAN ARE ENFORCED THROUGH THE GRANTING AUTHORIZATION  Each lessee or holder is expected to include the requirements of the authorization and the site plan into any documents, which describe the business relationship between the lessee or holder’s and their tenants and customers. The lessee or holder is responsible for enforcing those provisions.

GENERAL RESPONSIBILITIES

## The BLM retains the responsibility for:

Issuing and amending authorizing instruments to Facility Owners and Facility Managers, only for the areas actually occupied by the authorized improvements.  Granting occupancy and use of Public Lands rests exclusively with the BLM, Title 43 CFR Sections 2801- 2803.  The issuance of a FCC license (authorization), or frequency assignment, does not authorize occupancy of Public Lands.

- Approving any new/modified facility(ies) at the site.

- Approving amendments or assignments to leases and grants to qualified buyers of facilities on the site.

- Notifying existing authorization holders when any new/modification proposals are submitted and requesting comment in the appropriate NEPA and decision process.

## Facility Owners and Facility Managers (or their designated representatives) are responsible for:

- Complying with their authorization and all sections of this Site Management Plan.

- Ensuring that all new facilities, expansions, or improvements are consistent with the Coos Bay District Office Planning Documents; any environmental document(s)/decisions for the site; and, this Site Plan.

- Ensuring facilities/equipment not complying with Federal/State/local laws/regulations/ ordinances will be removed or modified within one year of the approval of this plan.  Any modification needs pre-approval by the BLM.

- Keeping all facilities within the established limits of their authorized area.

- Providing the BLM, with the name, address and phone number for a local contact person.  The Facility Owner and Facility Manager and the contact person may be the same individual.  The contact person will be available for emergencies and will have the authority to make decisions about construction issues, facility maintenance and all equipment within the facility.

- Adhering to the Facility Owner/Manager Lease/ROW as follows:

  - Facility Owners and Facility Managers with Communications Use Leases are authorized to rent building/tower space to tenants and/or customers without prior written approval from the BLM.

  - Tenants and/or customers may not construct their own equipment shelter (building, shelter or cabinet) or antenna support structure (tower or mast).  The facility owner must own all communication shelters and towers under their lease or grant. [If that is not possible, a separate SF-299 application, cost-recovery deposit, analysis, and authorization are required.  This will also result in the use being a tenant/customer of the original lease/holder in additional to being a separate facility for billing purposes.]

  - Tenants and/or customers using a facility covered by a Facility Lease/ROW will not have separate BLM Leases/ROWs to authorize the use except in situations where regulations or policy require them.

  - Facility Owners and Facility Managers are responsible for complying with the terms and conditions of the Facility Lease/ROW.  Facility Owner/Managers are also responsible for ensuring that their tenants and customers are in compliance with the terms and conditions of the Lease/ROW, and applicable FCC or NTIA/IRAC license terms and conditions.

  - The Facility Owner and Facility Manager may not place any unreasonable restrictions nor any restriction restraining competition or trade practices on tenants and/or customers, or potential tenants and/or customers.

- Ensuring that all communications equipment is properly installed, operated, and maintained.

- Ensuring that all communication equipment meets ANSI, FCC and BLM regulations, guidelines and standards concerning radiation limitations by:

  - Monitoring radiation levels at their facility and;

  - Immediately correcting any radiation levels that are, or could be a hazard to human health. (FCC 47CFR sections 1.1307(b), 1.1310 and 2.1093) and FCC OET Bulletin 65, August 1999.

- Providing a certified copy of their use and the category of use along with the current phone numbers and addresses of all tenants and customers as of September 30th each year.  This report is due by October 15th.

- Keeping the premises around their buildings free of trash and debris.

- Placing the Lease/ROW holder’s name, address, phone number, or BLM Lease/ROW number on the door of their communications site building.

- Correcting interference problems.

## FCC and NTIA/IRAC are responsible for:

Frequency Management.   The FCC and NTIA/IRAC are not normally responsible for the resolution of conflicts when the licensees or agencies are operating within the limits of the authorizations.

AUTHORIZED USES AND USERS WITHIN A FACILITY

## Use by Multiple Users

Use of all facilities and improvements by more than one user will be required except where the facility owner is a government agency.  Site applicants will take the lead in this area and design their proposals to accommodate multiple uses of facilities and improvements.  This includes multiple uses of buildings, towers, back-up generators, grounding systems, fuel containers, access ways and parking areas.

Due to the availability of building and tower space at the site, new facilities, or major modifications to existing facilities will generally not be approved until the optimum space is utilized even if other users are, or could be, competitors.

Facility Owners and Facility Managers are not required to lease facility space to others if they can prove to the authorized BLM officer that:

- Space is not available;

- The use is incompatible with the existing facilities;

- Additional space is needed by the facility owner/manager;

- Additional users would violate system security needs; or,

- Potential interference is not resolvable.

FEES

The BLM will charge Facility Owners and Facility Managers annual fees based on the Fee Schedule for Communications Uses on Public Lands as adjusted annually.  These fees will be fair market value for the use of Public Lands.  The population Zone 9 will be used for these calculations unless something else is specifically agreed to in writing by the authorizing officer or until populations change.

Fees that Facility Owners and Facility Managers may charge their tenants and “customers” are to be:

Reasonable (consistent with, and not in excess of, other fees for similar facilities) and commensurate with the uses and occupancy of the facilities and services provided to tenants and “customers”.

General Operation and Maintenance Direction

## Unique Resource Considerations at this Communication Site

SPECIAL STATUS SPECIES

The area has habitat for Howell’s manzanita, a Bureau Assessment plant species.  Bureau Assessment species are those which are not presently eligible for official federal or state status but are of concern in Oregon or Washington and may at a minimum, need protection or mitigation in BLM activities.  Currently there is one known population located at the Grizzly Mountain Communication Site.  The area has been posted with signs.  This population lies just below the power line right-of-way on the west side of the site and should be protected from disturbance.

Howell’s manzanita could easily be confused with a more common species, hairy manzanita, which occurs throughout the site.  The Howell’s manzanita is a much smaller shrub that tends to grow in very open areas on  the site.  It has more narrow leaves than hairy manzanita and awl-like bracts subtending the flowers. Howell’s manzanita is fire intolerant and may be eliminated by fire, as it does not have a burl which allows re-sprouting following fire events (Adams 1940, Wells 2000).

If Facility Owners, Facility Managers, or their tenants and customers have any questions on the location of the Howell’s manzanita site or have reason to believe that their activities could disturb the plants, they should notify the appropriate BLM officials before the disturbing activity takes place.  Every effort should be made to avoid or minimize disturbance to the small population that remains on this site.

THREATENED AND ENDANGERED SPECIES

The area to the north is identified as Occupied Marbled Murrelet habitat, a Federally Threatened bird species.  Any development at this site in the future will be evaluated through the NEPA and or RMP process.  Appropriate coordination standards will be amended to this plan.

## Wiring and Grounding

1.	All equipment is to be installed within existing buildings and on equipment racks that are grounded and shielded.  Grounding is to be installed in accordance with accepted standards.

2.	All electrical wiring and grounding must meet the “National Electrical Code” and applicable State codes.  All permanent wiring shall be installed in metallic conduit.  Surge protection shall be installed on all power distribution panels.

3.	Lightening protection “down” conductors installed upon communications towers shall be treated as “Transmission lines”.  Therefore, they shall have an insulating jacket.  Periodic bonding of the down conductor to the tower (Galvanized) steel shall be made with proper bonding connectors that are tin plated or made of brass.

4.	Each building is to have its own separate grounding system for all users in that structure.  Wherever practical, interconnection of individual grids and/or the simultaneous placement of a large sized copper ground wire with any new grounding systems that are buried on the site will be required.

5.	Site or facility grounding must be constructed of copper, with #2 AWG or larger wire or 2” or larger solid copper strap, connected to an adequate site/facility ground electrode system.  The site/facility ground electrode system shall be bonded to the power service entrance grounding electrode conductor.  Guy wires should also be grounded using manufacturers approved methods to preclude bi-metallic junction and corrosion.  All equipment on the site (buildings, towers, power units, transmitters, receivers, antennas, combiners, telephone systems, power cabinets, HVAC units, etc) must be connected to the site/facility ground by direct connection.  Electrical system ground wiring is required for electrical ground fault protection and circuit breaker coordination.  The grounding systems shall comply with applicable laws, codes and in accordance with standard engineering practice.  Below ground connections must use either an exothermic welding process (i.e. Cadweld, Thermoweld, etc.), copper wedge pressure devices (i.e. Ampact, Wrench-lock, etc.), or brazed copper connections in conjunction with a mechanical UL listed connector (to be used as a physical strength enhancement component).  Brazing by itself is not an acceptable method of bonding below earth grade (buried).

## Communications Equipment

Equipment Ownership

All equipment shall be labeled with:

- The owner’s name;

- Transmitter frequency(ies);

- A valid FCC, or IRAF, authorization;

- Transmitting power output(s); and

- A current 24-hour phone contact number.

Transmitting Equipment

All transmitters will have protective devices (shields, filters, isolation components), designed into or externally installed, to prevent interference to other users.  All transmitters shall be FCC type accepted or meet type acceptance criteria.

Re-radiation of intercepted signals from any unprotected transmitter and its associated antenna system will be prevented by the use of appropriate filters (wide band and narrow band broadcast transmitters).

The direct radiation of out-of-band emissions (i.e. noise or spurious harmonics) will be reduced to a level such that they may not be identified as a source of interference as defined in the FCC Rules and Regulations (e.g. Part 90.209(e)).  If site noise (electromagnetic noise) becomes an issue, noise threshold limits will be established, and amended into the Site Plan.

Direct radiation of out-of-bound emissions, (i.e. transmitter wide band noise, spurious emissions, harmonics, etc.) shall be reduced to a noninterference level by using bandpass, lowpass, and/or harmonic filtering.  Where duplexing is used, use of a notch type device should be avoided.  In situations where a notch type or a hybrid device is used, a bandpass filter must be used with the transmitter.

Band-reject filtering may be required in certain applications.

Re-radiation of signals from a transmitter and its associated antenna system shall be prevented by installing appropriate devices (i.e. ferrite isolators), with minimum return loss of 25 db.

All transmitters not in immediate use and not specifically designated as standby equipment shall be removed.  Loads connected to circulators are to be capable of dissipating the total power output of the transmitter.

Receiving Equipment

All receivers shall comply with all applicable parts of the FCC rules, including Parts 2 and 15.

All receivers shall have sufficient “front end” pre-selection to prevent receiver spurious response. The use of bandpass, band-reject cavity or crystal filters may be required to prevent receiver-produced intermodulation or adjacent-channel interference is recommended at the input of all receiving devices.

Where duplexing is used, use of a notch type device should be avoided.  In situations where a notch type or hybrid device is used, a bandpass filter must be used with the transmitter.

Tower

- Generally only one tower is authorized for each facility owner.  Facility Owners and Facility Managers may obtain permission to construct a second tower only after submitting evidence that demonstrates that their existing tower is completely filled and full use has been made of combining systems.

- All towers will be left unpainted, if they are dull, galvanized steel.  If paint is required, the BLM will approve only non-reflective colors from the Munsell Soil Color Chart, Standard Environmental Colors.

- Maximum tower height (including antennas) for this site is 199 feet.

- Anti-climb devices, removable steps, or other means to discourage unauthorized climbing, are highly recommended to reduce or avoid liability claims.

- All new towers will be self supporting.  No guy lines are permitted

- To avoid possible impacts to migratory birds or bats, follow the most current version of the U.S. Fish & Wildlife Service’s Interim Guidelines on the Siting, Construction, Operation and Decommissioning of Communication Towers (available at http://migratorybirds.fws.gov/issues/towers/comtow.html).

Antennas

            - The maximum antenna height (including tower) is 199 feet.

            - Microwave (dish) antennas (other than ground mounted satellite dishes) will be limited to a maximum of ten (10) feet in diameter.  The smallest diameter dishes are preferred if technically feasible.

            - All antennas must meet all OSHA safety standards.  If an antenna exceeds FCC public or occupations standards (see FCC OET Bulletin 65), it will be remedied within 24 hours after measures are taken or isolated (e.g., fencing, signing, relocation, lowering power levels are all possible remedies).  Ground measurements of RFR levels will be taken before mitigation measures are implemented.

            - Color(s) for dish antennas, or covers, must be pre-approved by the BLM.  Future white dish antennas and/or covers will not be approved.  Existing white dishes and covers must be repainted or replaced with dishes of approved colors, as repairs or replacement become necessary.

            - Antennas will be treated for low to non-reflectance.

Interference

The responsibility for correcting interference problems is a matter for resolution between the Lease/ROW holder of the facility(ies), the user causing the interference, and the affected party(ies).  First users on a site have seniority with respect to the resolution of interference complaints.  Senior holders have an obligation to maintain their equipment to industry standards, to operate their systems in accordance with the terms of both the FCC license and NTIA/IRAC frequency authorization, and to comply with the BLM authorization.

New users on a site must correct, at their expense, interference problems that they create.   They may be required to furnish an intermodulation study or other interference-related data and agree to accept financial responsibility for elimination or prevention of any interference caused by the facility before their application can be evaluated. They must cease operation of the suspect equipment until the problem is corrected.  If interference problems cannot be resolved or corrected within a reasonable time, the new use that is causing the interference may be terminated and the equipment removed.

All users shall cooperate with the User’s Group Association and the BLM in identification and correction of any interference.  The BLM does not have authority for correcting interference problems, but can act as a mediator to help all affected parties.  Interference problems must be coordinated with the FCC or NTIA/IRAC whichever is appropriate.

Interference with law enforcement and/or emergency communications must be corrected immediately.  The operation of equipment covered by this Site Plan shall not interfere with United States Government radio or electronic operations already in existence on public land within two (2) miles of the site to which this authorization refers.  The user causing this interference, shall, at its own expense, take all action necessary to prevent or eliminate such interferences.  If it does not eliminate such interference within ten (10) days after receipt of notice from the BLM to do so, this use will be terminated.

If electromagnetic noise becomes an issue, noise thresholds will be established and this Site Plan will be amended accordingly.

## Cables and Transmission Line (Wave Guides)

All new cabling will be jacketed and shielded and shall either be flexible or semi-rigid type.  Existing substandard cables will be upgraded as repairs or replacement become necessary.

Cables will be properly installed and will be strapped and fastened down.  Use of ports at building entrance points will be kept to a minimum by use of combiners.

When attaching cables onto a tower, conduits should be used and cable runs should be equally divided among all tower legs.

All transmission lines (wave guides) are to be supported in accordance with manufacturer’s specifications.

Double shielded braided or solid shielded cable will be used.  No RG-8 type cable is permitted.  No connector-type adapters will be used on transmission lines.  Only correct connectors that will mate to connected devices are to be used.

Conduits will be shared when they service common areas and will be buried where possible.

## Radiation

All communications uses must meet ANSI, FCC and BLM regulations guidelines and standards concerning radiation limitations.

Monitoring radiation levels at the site is the responsibility of all site users and will occur at required intervals to comply with FCC regulations and guidelines.  A copy of the monitoring report will be provided to the BLM within 30 days of its completion.

Onsite RFR measurements will be taken using appropriate equipment that can adequately measure both on-tower and on the ground levels before mitigation measures related to RFR are implemented.

Security fences with RFR notice signs are required around areas that exceed public use levels including anchor points outside the primary facility compound if necessary.  Raising higher power transmitting antenna on the tower or modifying the antenna type to half wavelength may be necessary to eliminate RFR hazards.  Reducing power may also be required if other alternatives are not feasible. All fencing location and design or new tower construction must be pre-approved by the BLM.

Warning signs will comply with ANSI C95.2 color, symbol, and content conventions.  Contact information including name and telephone number will also be included on warning signs.

Lowering power levels for on-tower access during maintenance will be coordinated between affected users.

Any identified RFR radiation problems that are, or could be, a human health hazard must be corrected within 24 hours after measurement tests have been completed or be removed from the site by the site user(s).  If the proposed corrective action involves any new ground disturbance, it must be pre-approved by the BLM.

## Utilities-Availability of and Requirements for:

Commercial Electrical Power

Commercial power is provided to the site under separate ROW grant to Pacificorp.

Telephone Service

There is no commercial telephone provided to the site.

If additional service is ever deemed necessary, site users will pay for the cost of:

- The necessary resource surveys and reports for service connections; and

- The cost of constructing service connections.

For visual reasons, overhead utility poles may not be authorized.

Fuel Tanks

All facility owners are responsible for providing fuel storage (propane and diesel) and emergency power for their tenants.  No tenants will be authorized to have separate fuel tanks and/or generators. Each facility owner will preferably consolidate fuel storage into a tank large enough in size to accommodate all tenants.  At a minimum, tanks will be grouped together in a consolidated area adjacent to their facilities.  All fuel, storage tanks (e.g. LPG, propane and diesel) must meet current fire department, Federal, State and County safety and hazardous materials requirements, including NFPA hazard placarding. Propane is the preferred fuel for future generators.

- All tanks will be:

a.	Signed in red letters, “SMOKING OR OPEN FLAME PROHIBITED WITHIN 20 FEET”;

b.	In conformance with National Fire Protection Association (NFPA) and Oregon Uniform Fire Code (OUFC) requirements; and,

c.	Painted an approved color, or screened by an enclosure to blend in with the natural environment.  If an enclosure is used, it must be pre-approved and painted an approved color from the Munsell Soil Color Chart, Standard Environmental Colors.

2.	Diesel tanks will also be:

a.	Designed with Federal and State approved internal secondary containment or enclosed in BLM and fire department approved secondary containment vaults that are painted a BLM approved color from the Munsell Soil Color Chart, Standard Environmental Colors.

b.	Constructed with underground fuel lines.  Fuel line must be constructed of black, treated pipe and fittings, protected from surface damage, and must be clearly posted as fuel lines.

c.	A containment basin must be maintained below all diesel tanks which are not designed and approved to be self contained.

d.  Spill Prevention, Control and Countermeasure (SPCC) Plans shall be developed, approved and put into effect for any fuel system in excess of 660 U.S. gallons capacity per single tank, or 1320 U.S. gallons aggregate capacity per facility.  These plans shall meet the requirements of Title 40, CFR Part 112 and Part 300, Oregon Statute (ORS) Chapter 468, and Oregon Adminstrative Rule (OAR) 340, Divisions 47 and 108.

## Sanitary Facilities

1.	Plans for any sanitary facilities must be pre-approved by the BLM.  If it is determined by the BLM that the users need such facilities, they will be provided by the Lease/ROW holder in a manner and location satisfactory to the BLM and within the requirements of the County Health Department.

## Security and Law Enforcement

The County Sheriff’s Department is the key law enforcement agency for the area.  They are responsible for most civil and criminal matters.  The BLM will be responsible for enforcing matters related to uses of BLM lands (e.g. resource protection issues).

Patrolling and policing for security purposes is the holder’s responsibility.

Gates and key access must be approved in advance by the BLM and must be adequate for BLM, State, County, and local emergency services access needs.

## Site Maintenance

The objective of maintenance activities is to present a clean, neat, and orderly appearance at the site and have all of the authorized improvements safe for workers and the public.  All users will keep up the overall appearance of the site.

Miscellaneous debris remaining after any construction and/or equipment installation, removal or modification, is not only a hazard, but can cause interference or intermodulation problems.  In particular, all loose wire or metal objects are to be removed from the site.

The users of the Site will remove all graffiti within 10 working days of finding it.  If graffiti is on natural features (e.g. rocks), the graffiti will be removed in a method approved by the BLM Authorized Officer.

Holders will not be permitted to leave or dispose of trash, garbage or cut brush on BLM lands.  No outside trash or litter containers will be provided.  Site users (i.e. holders) will remove litter from the site as it is produced.

Policing of litter in common areas (i.e. areas between buildings and developed sites) is the shared responsibility of those holders bordering these areas.

During construction and/or maintenance, paintbrushes will not be cleaned off on the rocks around the site and excess materials (e.g. cement) will be removed from BLM land.

Peeling paint on buildings and/or towers will be re-painted within thirty (30) days of discovery by the Facility Owner or within 10 days of notification of the holder by the BLM.

## Inspections

Enforcement authority is vested in the BLM as the Communications Site Administrator for Grizzly Mountain via 43 CFR 2800.  The BLM may conduct an annual inspection of each primary user’s facility.  This inspection will verify:

  - Compliance with technical standards.

  - Structural integrity.

  - As-built plan accuracy.

  - Electromagnetic compatibility.

  - General site health, safety, and cleanliness.

The BLM shall provide written notice of the scheduled inspection date at least 30 days in advance.  Each primary user shall arrange to have personnel available at the site at the time of the inspection.

Any non-compliance found shall be forwarded to the BLM and a written copy of the report shall be forwarded to the violating party or organization within 30 working days following the inspection.  The report shall include:

  - A description of the violation.

  - Corrective action required.

  - Name, address, and organization of the responsible party.

  - Time allowed for completion of corrective measures.

  - Anticipation action in the event of noncompliance with remedial instructions.

  - Method, manner and time allowed for appeal.

## Fire Prevention and Hazard Reduction Requirements

All facility owners will be responsible for maintaining a firebreak around the outside perimeter of their facility.  The purpose of the fuel break is to protect facilities within the communication site.  Evaluating the condition of the fuel breaks will become part of any inspection by the Facility Owner/Manager or BLM.  Standards for the fuel break are as follows:

1.  All facilities will have a zone around structures cleared of all vegetation for a      distance of 30 feet.

2.	All facility owners/managers shall establish a zone of 100 feet beyond the area cleared of all vegetation.  Each facility owner will treat their portion of that zone to reduce ladder fuels, as specified by the BLM.  In addition, annually from May 1 to September 30, this zone will be treated as needed to keep the height of brush, grass, and dead material within 6 inches of the ground.

This fuel break will be completed during 2005 or 2006. Identified threatened, endangered, or sensitive plant species must remain within the minimum clearance areas. (Howell’s manzanita  plant populations are specifically identified and areas will be posted.)

Smoking is prohibited in flammable vegetation areas.

Roof structure shall be kept reasonably clear of leaves, twigs, and other debris at all times.

No explosives will be stored at this site.  Flammable materials shall be stored in conformance with the requirements of local and state fire regulations.  Flammables will be placed in closed containers and stored away from sources of ignition and combustible materials.  If flammables are stored within a building, the building will be locked, properly signed and well ventilated.

Approved spark arresters will be required and maintained on all internal combustion engines.

At least one (1) U.L. rated 40 B: C dry chemical fire extinguisher is required inside each building.  Prior to each June, fire extinguisher(s) shall be inspected by holders and refilled, if necessary.

Any fire will be immediately reported to “911”, the nearest BLM office and/or County Sheriff.

BLM Officers will make periodic fire prevention inspections.  They will call to the holder’s attention to any lack of compliance with the above regulations, plus any other existing hazards.  Compliance with these inspections is required within the time limits specified in the inspection report.

## Access Maintenance and Restrictions

Roads

The access road from Highway 101 to the Crook Estates land is maintained by the County.  The BLM roads and portions which cross the private lands are generally well maintained and drained surface roads until it becomes a local road for the last mile to the site.   A road maintenance agreement between the private landowners and the Communications Site Users Association is strongly encouraged in order to negotiate   road maintenance fees across the private lands.

One of the primary functions of the association will be to negotiate road maintenance fees with the private landowners for that portion of access road which begins at the end of county maintenance and terminates at the public land boundary. The association will be issued a ROW grant for the access road leading to communication site (federal lands only). This gives the association control of the federal portion of the access road. The association could then construct a BLM approved gate and issue keys to all participating members only.

Interior Site Driveways/ Parking Areas

Roads within the communications site will be maintained by the site users.  Interior roads will be planned and approved during establishment of new facilities.  Interior roads will be maintained in a manner to allow only one entrance to the site.  Off-road vehicle use in and around the site is discouraged.

Road Closures

Roads on public land are subject to periodic closures to entry during periods of extreme fire danger, inclement weather, or wet conditions.  Authorized site users may use the site during these general closures, if advance approval is obtained from the BLM.

CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION

## New Facility Owner Responsibilities

## In addition to the responsibilities listed in Section III, New Facility Owners and Facility Managers are responsible for:

1.	Submitting a complete application to the Coos Bay District Office prior to any new construction or modifications to existing improvements (ATTN: “Realty Specialist”).  The application must include:

- The appropriate cost recovery and application fees.

b.	A copy of the approved Site Plan Base Map showing all of the proposed (new) facilities including structures, towers, and auxiliary equipment;

c.	Completed drawings/plans prepared by a registered engineer and approved by the BLM;

d.	Identification of any microwave beam paths, a plot of their azimuth(s), and their proposed elevation(s) on the tower;

e.	Documentation that shows that proposed facilities will not be obstructing, or interfering with, any existing fixed point to point antennas, omni directional broadcast antennas, or microwave beam paths in the directions of primary population targets.  Proposed beam path needs must be shown on Site Plan Base Map; and,

f.	Any needed recommendations, changes or modifications to their original proposal, based on any required resource surveys and/or reports.

2.	Demonstrating that their proposals will not cause undue interference with any existing uses before the BLM can approve new facilities.  In addition, it is the applicant’s responsibility to show that any new facilities will make the most efficient use of the limited amount of space at the site.

3.	Showing their proposals will provide for future users without additional construction.

4.	Providing engineering and geotechnical investigations for development of specific foundation designs and grading plans.

5.	Providing an Erosion Control Plan prior to construction activities.  At a minimum, the Erosion Control Plan must include: sediment control, stipulations that cut/fill slopes will be graded and contoured to prevent erosion and/or excessive runoff, and recommendations for temporary erosion control measures, (e.g. netting, silt fences, swales, and/or sediment collection areas).

6.	Coordinating with other Federal (e.g., FCC and FAA), State and County agencies and obtain all required approvals and/or permits.

7.	Providing 30-day notice to all facility owners/managers at the site, as well as the BLM, of all new frequencies proposed for the site.  A completed BLM technical data sheet or equivalent must be sent with the 30-day notice to allow for comment of potential interference.  This would be for new frequencies for themselves and their tenants.

8.	Insuring that all written approvals have been obtained from the BLM prior to construction.  In addition:

a.   Directional broadcast antennas (e.g. translators) will only be protected within the arch between their licensed 3 dB points.

b.   New and/or modified facilities will not obstruct existing fixed point-to-point antennas or omni-directional broadcast antennas in directions of primary population targets.

## Construction Methods and Resource Protection

Plans submitted by an applicant for any new construction or modifications shall specify provisions for soil rehabilitation measures including, but not limited to, soil replacement and stabilization and for proper handling of runoff from buildings, parking area, access roads, and undeveloped common areas.

The following methods and resource protection measures will be required to minimize impacts during construction:

1.	Avoid and protect sensitive resource areas, as identified by the BLM.

2.	Compliance with the Erosion Control Plan.

3.	During construction and/or maintenance, paintbrushes will not be cleaned off on rocks around site and no marks of any kind (including survey) marks will be permitted on rocks.

4.	Minimize ground disturbance and vegetation removal as much as possible during construction activities.  All ground-disturbing activities require BLM pre-approval.

5.	Any extensive cut and fill slopes will be re-vegetated with native vegetation species pre-approved by BLM as soon as possible after construction.  If necessary, reseeding will be required until vegetation is successfully established as determined by the BLM.

6.	 No grading material will be cast off during construction/reconstruction activities. Excess soil will be end hauled or can be used for fill material on road and/or building/tower pads.

7.	Temporary, on-site storage of construction materials will require pre-approval by the BLM.

8.	Construction materials and supplies, except for hazardous materials (see number 10. below) may be left unattended at the construction site at the end of each workday, but at the owner’s risk.

9.	Hazardous materials, including, but not limited to all fuels, oils, and lubricants are not to be left unattended at the site at any time.  During construction, these materials are to be removed from the site at the end of each workday, or temporarily stored inside a locked and signed building until the following workday.  	A modified Spill Prevention, Control and Countermeasure (SPCC) Plan for petroleum and hazardous materials is required and must be approved by BLM.  Such spill plan is required under Oregon Statute (ORS) Chapter 468, and Oregon Administrative Rule (OAR) No. 340, Divisions 47 and 108..

10.	All surplus construction materials and/or waste debris must be removed from the site no later than thirty (30) days after construction has been completed.

11. Any earth moving or heavy equipment (e.g. dozers, graders, cranes, backhoes, etc.) leaving the designated roadway and/or approved parking area(s) to perform authorized activities at the site, will be washed off prior to being brought onto public lands to prevent the introduction and spread of noxious weeds into the area.  If noxious weeds are present, the Facility Owner/Manager shall remove and control the weeds.  Use of pesticides/herbicides shall comply with applicable Federal and state laws.  Pesticides/herbicides shall be used only in accordance with their registered uses and within limitations imposed by the Secretary of the Interior.  Prior to the use of pesticides/herbicides, the Facility Owner/Manager shall obtain written approval from the authorized officer.

## Construction Inspection

1.	All new construction, reconstruction, or major modification shall conform to the established technical standards and accepted engineering practices (i.e., the Uniform Building Code).

2.	Any construction inspections required by other applicable agencies are the responsibility of the lessee/holder.  Copies of completed inspections are to be provided to the Field Office Manager, either as they occur or as part of the final as-built plan.  Inspection information shall become a permanent part of the proponent’s Lease/ROW case file.

3.	The Lessee/Holder agrees that corrective work detailed in BLM, or other agency required compliance inspections, would be completed by the scheduled completion date.  If the Lessee/Holder disagrees or has questions about specific items, the Lessee/Holder must contact the BLM in order that the disagreement or item may be resolved.

4.	A final set of as-built plans will be submitted to the Field Office Manager within 90 days of acceptance of structure (if contracted) or of completion date.

## New or Remodeled/Expanded Buildings

- Any new buildings must be designed to accommodate multiple users along with fitting into the physical environment as defined in a site-specific environmental analysis developed at the time of the proposal.

- Buildings are required to be one-story.  The roof must be metal or covered with metal to be fire resistant.  Roofs can be equipped with antenna support structures, such as poles and railings that can extend up to 25-feet above ground level.

- Facility Owners and Facility Managers are encouraged to construct the interior of their buildings in a modular fashion, so that they can:

a.	Sublease sections to others;

b.	Provide tenants and customers with internal separation and security;

c.	Reduce physical interference; and

d.	Increase management effectiveness.

- The following materials are approved for construction of new facilities (i.e. buildings)

#### a.	Floors – Concrete slab with drainage.

b.	Walls – Concrete block metal or pre-fabricated concrete.

c.	Roof – Metal, or concrete, if painted to eliminate shiny surfaces, or other fireproof material as approved by the BLM.  Proposals for wooden roofs will not be approved.

d.	Partitions – If it is felt partitions are necessary in buildings, ensure they are constructed with fire resistant material (e.g., concrete block, reinforced concrete, or properly grounded fencing.

e.	Color – Proposed color for use on all exterior building surfaces must be pre-approved by the BLM. The goal of the color selection for the facilities is to make the building as inconspicuous as possible and make buildings located on the skyline look inconspicuous when viewed from a distance.  The intent is to reduce or eliminate glare from reflective and/or illuminated surfaces such as windowpanes, sheeting and reflective paints.  Non-reflective, BLM approved colors will be used on equipment buildings.

- Building entry lights must:

a.	Only light the immediate area in the vicinity of the door;

b.	Be motion activated and have a limited time duration (e.g., 3-5 minutes); and

c.	Have a shielded beam that is pointed at the building door.

Requests for all-night (i.e. “dusk-to-dawn”) lighting, or entry lighting that would be visible from outside of the site will not be approved.

## New or Remodeled/Expanded Towers

- All new construction, reconstruction, and modifications to towers will be pre-approved by the BLM prior to implementation.

- It is the applicant/holder’s responsibility to assure that a new, or modified, structure will not unduly interfere electronically or physically with any existing equipment at the site.  Towers must be spaced, so as to prevent ground level radiation and/or interference problems.  This must be clearly demonstrated in writing to the BLM prior to issuance of a Lease/ROW or amendment.

- All new towers will comply with current structural and safety specifications and design standards, including safety-climbing devices.  Towers should be as narrow and “open” as safety and structural integrity allow.  New towers will be designed using maximum wind, snow, and/or tower loading anticipated for the site.

- To avoid possible impacts to birds or bats, follow the most current version of the U.S. Fish & Wildlife Service’s Interim Guidelines on the Siting, Construction, Operation and Decommissioning of Communication Towers (available at http://migratorybirds.fws.gov/issues/towers/comtow.html).

SITE ASSOCIATION/ADVISORY GROUP

A Site Users’ Association is encouraged to collectively work with the Crooks Timber Land Association for appropriate shares in maintenance of the access road across the private lands and for the long term maintenance of the fuel break, once completed by the BLM.  In addition to access, the goal of the Site User’s Association will be to maximize the effective use of the site.  The objective of a sanctioned association will be to represent all site users as a group when dealing with the Coos Bay BLM Field Office on matters relating to the site administration.  The association will be able to work in cooperation with the BLM to identify problems or opportunities and make recommendations to the BLM for any changes in management strategies at the site.  The association could also provide input to the BLM regarding the future addition of equipment and facilities at the site.  While the advice and recommendations of the association would not be binding on the BLM, the BLM could use the input for administration of the site.  The BLM would be a member of such a group and would help jointly develop the charter (i.e., the ground rules).

APPENDICIES

## Site Map

## Authorized Facilities

## Site Photographs

## Inspection Checklist

## Association Constitution and By-Laws

APPENDIX A

SITE MAP

(See associated AutoCAD Map on this website)

APPENDIX B

LESEE FACILITY TABLE

(See associated User’s Table on this Website)

|  | Auth # | Use | Building | Tower | Access/Parking | Other |
| --- | --- | --- | --- | --- | --- | --- |
| Facility # 1 Community TV Assoc | OROR 51932 | BT | 2 - 8’x 8’ metal | 40’ guyed 20’ guyed antenna masts | Access and parking. |  |
| Facility #2 Verizon | OROR 0005691 | MIC | 18’ x 22’ metal | 100’ lattice | Access and parking. | Diesel tank and generator 50’x 60’ fence |
| Facility #3 USFS | OROR 12748 | PMRS | 6’x 8’ metal | 80’ guyed | Access and parking. |  |
| Facility #4 Ramcell of Oregon | OROR 050732 | CEL | 8’x 12’ aggregate 8’x 10’ metal | 110’ lattice | Access and parking | Shared fence with Coos Curry Elec Coop |
| Facility #5 Coos Curry Elec Coop | OROR xxxxxx | PMRS | 8’x 10’ metal | 40’ guyed 3 – 30’ poles | Access and parking. | Shared fence with Ramcell |
| Facility #6 OR Dept of Forestry | OROR 46990 | PMRS | 10’x 12’ block w/ 6’x 8’ wood | 40’ guyed | Access and parking |  |
| Facility #7 OR State Police | OROR 43209 | PMRS | (w/ OR Dept of Forestry) | 50’ guyed | Access and parking |  |
| Facility #8 US Coast Guard | OROR 47000 | PMRS | 20’x 20’ lookout owned by ODF/CFPA | 60’ lattice | Access and parking | 300 gal propane 10Kw generator Fence |

APPENDIX C

SITE PHOTOGRAPHS

(See associated Facility Photos on this Website)

APPENDIX D

INSPECTION CHECKLIST

“Grizzly Mountain Annual Technical Inspection”

Date Inspected: _____________________________   	Time Inspection: ________________________________

Permit Holder: ______________________________  	Authorization # _________________________________

Site Technician : ____________________________   	 Phone # _______________________________________

Number of Transmitters ______________________   	 License Posted _________________________________

Please mark the following Items as Acceptable (A) or Unacceptable (U).

Electrical Wiring ------------------- (A)     (U)        	Grounding --------------------- (A)     (U)

Equipment Installation ------------ (A)     (U)	Housekeeping ----------------- (A)     (U)

Building Repair -------------------- (A)     (U)	Tower Repair ------------------ (A)     (U)

Please mark the following Items as Yes (Y) or NO (N) or (NA)

Isolators ---------------------------- (Y)     (N)     (NA)	Circulators --------------------- (Y)     (N)     (NA)

Cavities ----------------------------- (Y)     (N)     (NA)	Terminators -------------------- (Y)     (N)     (NA)

Filters ------------------------------- (Y)     (N)     (NA)	Lightning Protection ---------- (Y)     (N)     (NA)

Comments: __________________________________________________________________________________

____________________________________________________________________________________________

Recommended Corrective Action:  ________________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

Required Corrective Action To Be Taken:  __________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

Committee Representatives:  _____________________________________________________________________

Bureau of Land Management Representatives: _______________________________________________________

Please make the required corrective action within the next 120 days.

Please make a written report of corrective action taken and submit to the BLM in Coos Bay.  If  you should have any questions, please call the BLM office.

APPENDIX E, CONSTITUTION AND BYLAWS

GRIZZLY MOUNTAIN COMMUNICATIONS SITE

USERS ASSOCIATION

CONSTITUTION

ARTICLE I

This organization shall be called the Grizzly Mountain Communications Site Users' Association, hereinafter referred to as "the Association".

ARTICLE II

This Association is formed for the purposes of establishing a not-for-profit site management and advisory association, which is being organized to promote and encourage a spirit of fairness, one unto the other, and to cooperate for the mutual benefit of each member; to stimulate and encourage cooperative protection from interferences to existing radio facilities, protection of property, develop the site for maximum compatibility commensurate with adequate functioning of existing facilities, and to equitably allocate site maintenance costs among users.

ARTICLE III

This Association shall encompass all communications facilities on the Grizzly Mountain Communications site, as defined by the Bureau of Land Management.

ARTICLE IV

The membership of the Association shall comprise all Bureau of Land Management Right-of-Way holders, tenants, and customers as defined in 43CFR Part 2800 et al, dated November 13, 1995.

ARTICLE V

Each member (i.e. Right-of-Way holder, tenant, or customer) is entitled to one vote per user organization.  Associate members are individuals or representatives of concerned organizations or other persons that the Board of Directors may deem desirable to the Association.  Associate members are non-voting members.

ARTICLE VI

Amendments to the Constitution may be made only at the annual meeting by a two-thirds majority vote of the members in good standing and present at said meeting.  Voting by written, signed proxy on amendments shall be permitted.

ARTICLE VII

The Association shall be represented by a Board of Directors and its elected officers as set forth in the bylaws.

ARTICLE VIII

The following named persons shall serve as charter officers and directors until their successors are duly elected and qualified, to wit:

Director and Chairman:

Director and Vice-Chairman:

Director and Secretary:

Director and Treasurer:

Director and Trustee:

GRIZZLY MOUNTAIN COMMUNICATIONS SITE

USERS ASSOCIATION

BYLAWS

Article I. - Name

The name of the association shall be the GRIZZLY MOUNTAIN COMMUNICATIONS SITE USERS' ASSOCIATION, hereinafter referred to as the Association.

Article II. - Objectives, Purposes, and Powers

The purpose of the Association shall be to act in an advisory capacity only in assisting the United States Department of the Interior, Bureau of Land Management, hereinafter referred to as BLM, and the members of the Association in the long-term management of the Grizzly Mountain Communications Site, situated on public lands administered by BLM.

The Association shall act in conformance with applicable law, the rules and regulations of the BLM, as authorized by these Bylaws, and for the following purposes:

To recommend technical and operational standards for electronic installations, equipment, and operations at the Site to the members and the BLM.

To assist and advise the members and the BLM in conflict resolution and compliance with technical standards.

To review and recommend actions on new applications to the BLM.

To assist the BLM with annual site and facility inspections and to make the inspection reports available to the members.

To recommend maintenance, repairs, and improvements to the Site and access road to the members and the BLM.

To eventually create and maintain a centralized technical data base to assist in resolving interference disputes between members, and for the analysis of all applicants seeking BLM approval for new special use permits or amendments to existing permits.

To equitably collect monies as provided for in these Bylaws, and to expend these funds for the purpose of maintenance, repair, and improvements to the Site, access road, and other incidental expenses associated with the operation of the Association.

To establish and maintain a long term site plan.

Article III. - Prohibited Activities and Indemnification

Members of the Association are prohibited from participation in activities which might, or actually do result in civil claims or criminal penalties against any other member or members not directly participating in such activities.  Any such activities undertaken or authorized by any member or members shall be under the sole authority and responsibility of said member or members, who shall indemnify and hold harmless each and every other member of the Association against any and all such claims from whatever source derived.

Only the Board of Directors shall be permitted to enter into any contract or agreement with any person, firm, or corporation on behalf of the Association for any product or service, or to otherwise encumber or obligate the Association.

Article IV. - Duties of the Members

It shall be the duty of each member to cooperate with the other members, the Association, and the BLM in the efficient administration and operation of the Site; to cooperate with other members in the resolution of conflicts; to advise and assist other members whenever possible to resolve problems; to abide by the technical standards adopted by the Association; to maintain their installations in accordance with the requirements of the Association and the BLM; to support the efforts of the Association, to improve the site by prompt payment of membership fees and assessments, and to promptly correct any problems pointed out by the Association or the BLM.

Article V. - Duties of the Association - Internal Disputes

The duty of the Association in disputes between members is to fairly and reasonably arbitrate such disputes without the intervention of the overseeing Federal agencies whenever possible, and to provide, through the participation of its members and their available expertise and technical knowledge, recommendations for reasonable, cost-effective and technologically feasible solutions to conflicts and disputes between members, and to advise the members in performing whatever repairs, improvements, and modifications are reasonably necessary to resolve the problem.

In the event that the dispute cannot be successfully resolved within the Association, the duty of the Association is to provide the overseeing Federal agencies with accurate, complete, and unbiased evidence and information, and to act as a neutral advisory authority in any such dispute.

Article VI. - Duties of the Association - External Matters - Representation

In matters of complaints or actions by non-members regarding the Site generally, the Association shall act as the collective representative of the members in representing the common interests of all members.  This shall not preclude individual members from representing their own interests in any such action.

In all complaints or actions where non-members are involved, the association shall act in the best interests of the Association and its members.

Article VII. - Powers of Enforcement

The Association may recommend the revocation of any Right-of-Way, Lease, or permit, held by any member.

The Association shall have the power to revoke the membership of a member only as provided by these Bylaws.

Article VIII. - Board of Directors

The business and affairs of the Association shall be managed by a Board of Directors.  The Directors shall have full power and authority between annual meetings to perform all functions and do all acts which the Association might do or perform in accordance with these Bylaws.  The Board shall submit an annual budget for inclusion in the notice of the annual meeting which outlines proposed capital expenditures and operating costs of the Association for the upcoming year.  The Directors may refer certain business items for a vote by the entire Association before making a final decision.

There shall be five Directors or such larger number as shall be fixed by amendment of the Bylaws, but no decrease in the number of Directors shall shorten the term of any incumbent Director.

Article IX. - Election of Board Members

Members of the Board of Directors shall be elected by secret ballot of the members-in-good-standing of the Association held at the annual meeting, and shall be installed at that annual meeting and shall hold office until the next annual meeting after their election or thereafter until their successors shall have been elected and installed.  The Board shall be comprised of Association members representing a cross-section of Association membership.

Article X. - Vacancies - Directors

Any Director may resign at any time by giving written notice to the Officers of the Association.  Such resignation shall take effect at the time specified therein; and unless otherwise specified therein, the acceptance of such resignation shall not be necessary to make it effective.

Any vacancy occurring in the Board of Directors may be filled by the affirmative vote of a majority of the remaining Directors, though less than a quorum.  A Director elected to fill a vacancy shall be elected for the unexpired term of the Director's predecessor in office.

Any directorship to be filled by reason of an increase in the number of Directors shall be filled by election at an annual meeting or at a special meeting of the members called for that purpose.

Article XI. - Regular Meetings of the Board of Directors

Regular meetings of the Board of Directors shall be held without other notice than these Bylaws immediately after and at the same place as the annual meeting of the members.

Article XII. - Special Meetings of the Board of Directors

Special meetings of the Board of Directors or the Association may be called by or at the request of the Chairman of the Board or any two Directors.  The Board of Directors may fix any place within Oregon as the place for holding any such meeting.  Notice of any special meeting shall be given at least five (5) days previously thereto by written notice delivered personally, by facsimile, or Certified Return Receipt Mail, to the last known address of each Director and the District Office Manager of the BLM, Coos Bay District Office.

Neither the business to be transacted at, and the purpose of any regular or special meeting of the Board of Directors shall be specified in the notice.

Article XIII. - Telephone Conference Meetings

Any action which may be taken by the Directors at a special meeting may be performed by way of a telephone conference meeting as provided herein.

Telephone conference meetings may only be held upon the unanimous consent and participation of all Directors.

Upon the request of the Chairman of the Board or any two Directors, the Secretary may initiate a telephone conference call which shall include the Secretary and all Directors.

All such telephone conference meetings shall be recorded on audio tape and retained with the Association records by the Secretary.

During any telephone conference meeting, any Director or the Secretary may object to the continuation of the telephone conference meeting, and upon such objection, the meeting shall be immediately adjourned.  Any decision made or vote taken during that meeting shall be null and void.

The Secretary shall prepare written documentation of any decisions made or vote taken and shall forthwith submit such documentation by the United States mail or facsimile to each of the Directors.

Article XIV. - Quorum

A majority of the number of Directors fixed by these Bylaws shall constitute a quorum for the transaction of business at any meeting of the Board of Directors other than a telephone conference meeting, but if less than such majority is present at such meeting, a majority of the Directors present may adjourn the meeting without further notice.

The act of the majority of the Directors present at a meeting at which a quorum is present shall be the act of the Board of Directors.

For Association meetings, a quorum shall be two-thirds of all members in good standing.

Article XV. - Informal Action by Directors

Any action required or permitted to be taken at a meeting of the Directors may be taken without a meeting if a consent in writing, setting forth the action so taken, shall have the same force and effect as a unanimous vote of the Directors.

Article XVI. - Officers

The officers of the Association shall consist of a Chairman, Vice-Chairman, Secretary, Treasurer, Trustee, and such other officers as the Board may consider necessary.  The office of Secretary and Treasurer may be combined into one office if the board decides that the office is manageable by one person.

The Board of Directors may appoint such assistant officers, committees and agents as they may consider necessary, who shall be chosen in such manner and hold their offices for such terms and have such authority and duties as from time to time may be determined by the Board of Directors.

Article XVII. - Election of Officers

The voting members of the Association, from their numbers, shall elect the Officers of the Board of directors at the annual meeting, and the Officers shall serve until the next annual meeting after being installed as Officers.

Article XVIII. - Removal of Officers

Any officer or agent of the Association may be removed by the Board of Directors whenever in its judgement the best interests of the Association will be served thereby.

Article XIX. - Vacancies - Officers

A vacancy in any office, however occurring, may be filled by the Board of Directors.

Article XX. - Officers - Duties

The duties of the Chairman shall be:

1. Arrange for and preside at the annual and special meetings of the Association.

2. Represent the Association in public meetings and meetings with the Bureau of Land Management.

3. Supervise the work of the Secretary and Treasurer to assure coordination of efforts and on-time completions.

4. Approve and sign all Association expenditures.

The duties of the vice-Chairman shall be:

1. Assume any or all of the Chairman's duties, given appropriate notice, if the Chairman is unable to fulfill them.

2. Monitor site inspections to assure fair and impartial results.

3. Coordinate and direct committee work.

The duties of the Secretary shall be:

1. Prepare outgoing Association correspondence and present to President for approval, then make distribution to affected members.

2. Disseminate incoming correspondence to Chairperson and other affected users at annual and special meetings, or sooner if the urgency of the matter dictates.

3. Record minutes at annual and special meeting, and keep members appraised of meeting or planned activities affecting the Association, including annual, special, and public meetings.

4. Maintain all files, records, and mailing addresses, keeping them current and accurate.  All Association documents shall be open for inspection by any member in good standing.

5. Reproduce minutes of annual or special meetings and distribute to all officers within sixty (60) days following such meetings.  Distribute to remaining members at the next special or annual meeting.

The duties of the Treasurer shall be:

1. Maintain all accounts, keeping them current and accurate.  All Association documents shall be open for inspection by any member in good standing.

2. After the amount of the assessment has been determined at the annual meeting, the Treasurer prepares the individual assessment documents and mails to all users within 60 days following the meeting.  The assessments shall bear the breakdown of the total monies requested, with proper return mailing address, the Treasurer's signature and a request for remittance within forty-five days from mailing-date.  He (She) initiates follow-up correspondence if payment is not received by the due date.  Handles special assessments as the urgency of the circumstances dictates.

3. The Association is responsible for its own financial obligations, whether for major road repairs or minor costs of doing business, such as the purchase of administrative items and postage for mailings.  In this connection, the Treasurer prepares and signs all checks and payments and presents to the President for approval and signature.  Records all transaction, including date, amount received or disbursed, from or to whom, and for what purpose.

The duties of the Trustee shall be:

1. Attend or be represented at all meetings of the Directors and the Association.

2. Serve as Secretary for the Technical Committee.

3. Assist the Vice-chairman on committee work as needed.

Article XXI. - Bonds

Any Director, officer, or member authorized to receive or disburse, or authorize the receipt or disbursal of money for or on behalf of the Association may be required to give the association such bond for the proper discharge of their duties as the Association may direct.  The Association shall bear the cost of any such bond.

Article XXII. - Compensation

The Board of Directors shall receive no salary for services rendered in their respective positions, but the Secretary-Treasurer and any other officers or agents of the Association shall be allowed for expenses incurred and for whatever compensation the members of the Association may authorize.

Article XXIII. - Meetings

The annual meeting of the Association shall be held on such date and at such place as shall be determined by the Board of Directors.  The Secretary shall send notification of the time and place of the annual meeting, a proposed agenda, minutes of the previous annual meeting, a copy of the latest financial report and a proposed budget for the upcoming year to the last known address of each member and the BLM Representative by United States Mail, not less than thirty (30) days prior to the date of such meeting.

Special meetings of the Association shall be held at such times and places as shall be determined by the Board of Directors as necessary to conduct the business of the Association.  The  Secretary shall send notification of the time and place of such special meetings to the last known address of each member and the BLM Representative not less than fourteen (14) days prior to the date of such meeting.  Notices of such special meetings shall state the purpose for which called.  No business shall be transacted at a special meeting except as stated in the notice thereof.

Parliamentary procedure for all meetings shall follow Roberts Rules of Order.

Article XXIV. - Membership

Membership in the Association shall be open to those entities holding a valid Right-of-Way Grant issued by the United States Government, and their tenants and customer users, as defined in 43CFR Part 2800 et al.

Membership may be terminated upon expiration of tenancy or Right-of-Way Grant issued by the United States Government only if the member fails to renew such Right-of-Way or the tenant/customer rental agreement within ninety days of expiration, or if the member indicates a desire to abandon the use of the Site.  Unless another agreement has been made with the Board of Directors, the membership of associated tenants and customers shall also terminate when the principal Right-of-Way Grant terminates.

Membership may be terminated for failure of a member to abide by the Bylaws, rules, and regulations of the Association.

Article XXV. - Membership fees

The annual fee for membership in the Association shall be $25.00 (Twenty-five Dollars), and shall be payable on the first day of January.  There shall be a sixty day grace period for payment of membership fees beginning upon the first day of the calendar year, which runs January-December.  Members who have not paid the annual membership fee as of the sixty-first day shall not be in good standing from that time forward, until such fee shall be received by the Treasurer or their membership is revoked.  Members more than ninety days in arrears shall have their membership revoked.  For new members, the $25.00 fee shall be due upon grant of BLM Right-of-Way.

Article XXVI. - Voting

Each member in good standing shall be entitled to one vote on issues brought before the Association by the Board of Directors.  Voting by signed proxy shall be permitted in connection with any business of the Association.  A majority vote of members present and proxies cast shall carry.

Members not in good standing shall not be entitled to vote or to be elected to office.  A member shall not be in good standing unless that member has complied with all the requirements adopted by or on behalf of the Association under the Bylaws, except that no member may be denied a vote by reason of any unresolved dispute or conflict pending final decision or adjudication by the overseeing Federal agency or court of law at the time the vote is taken.

Article XXVII. - Amendments

Amendments to the Bylaws may be made only at the annual meeting by a two-thirds majority vote of the members in good standing and present at said meeting.  Voting by written, signed proxy on amendments shall be permitted.

Article XXVIII. - Assessments

For the purpose of providing funds to accomplish the objectives of the Association, assessments may be levied upon the members of the Association as provided herein.

The maximum assessment per member per year shall be $500.00 (Five Hundred Dollars), and shall be based on the annual budget as approved by the members at the annual meeting or any special meetings.

All assessments levied against Governmental agencies shall be subject to such agencies' normal authorization and appropriation processes.

Non-profit and volunteer organizations which act for the public good may be exempted from any part of or all assessments as authorized by the Board of Directors.  Exemptions from assessments shall be established by the Board at the annual meeting and shall continue from year to year, and need not be renewed at each annual meeting.  The Board shall be authorized to decrease such assessments to such members, or to waive such assessments entirely, and shall review each such exemption on a case-by-case basis.

Article XXIX. - Waivers of Notice

Whenever notice is required by law or these Bylaws, a waiver thereof in writing, signed by the person entitled to said notice, or the appearance of that person at such meeting in person or by proxy, shall be equivalent to such notice.

Article XXX. - Dissolution and Disposition of Assets

This Association may be dissolved upon a two-thirds majority vote of the members-in-good-standing at the time such vote is taken.  Upon dissolution of the Association, and after the payment of all just debts and obligations of the Association, all remaining assets, personal and real property shall become the property of the BLM, to be used for the improvement and administration of the site.  All documents and records of the Association shall be given to the BLM Representative for whatever disposition said BLM Representative shall deem appropriate.

Article XXXI. - Technical Standards Committee

The Board shall appoint a Technical Standards Committee which shall be responsible for developing and maintaining a set of rules, regulations, and technical standards for member operations at the Site.

Those rules, regulations, and technical standards adopted by the Technical Standards Committee and approved by the members shall become and be made a part of these Bylaws.

Rules and Regulations

Authority for these Rules and Regulations devolves from the Coos Bay BLM concurrence with the Grizzly Mountain Communications Site Management Plan (GMCSMP). The obligations to comply with them are in-turn, conveyed to all electronic facility operators on Grizzly Mountain through the Association’s Constitution and Bylaws.

The purpose of these rules and Regulations is to standardize and set procedures to provide all current and future communication users a method to utilize the Grizzly Mountain Communications Site. The Rules and Regulations are intended to minimize physical damage and public liability as well as to maintain a reasonable level of aesthetic integrity. This will provide for improved electromagnetic compatibility of all users, while projecting an image consistent with BLM expectations.  There is also a requirement to comply with Curry County land development codes relating to Telecommunications Facilities.

1.	Site Maintenance

1.1.	Each site is required to be maintained by the holder of the BLM right-of-way in an acceptable manner.

1.2.	Litter or unused equipment shall not be allowed to remain in the vicinity of the site building at any time. All garbage shall be removed from the site immediately.

  - All equipment not in service shall be stored properly or removed from the site.

2.	Access Roads

2.1.	The ROW holders shall maintain the roads designated by the BLM as access roads.

2.2.	It shall be the responsibility of all BLM right-of-way holders to work cooperatively toward ensuring adequate access on these access roads.

2.2.1.	Minimize travel during inclement weather.

2.2.2.	Minimize the number of vehicles.

2.2.3.	Remove road hazards, or notify the GMCSUA and the BLM when noticed.

2.2.4.	Minimize obstructing the access road.

2.2.5.	Visitors to the site shall drive in a courteous manner on private property and on all access roads.

2.3.	The Annual inspection shall address the access road condition.

  - The Technical Committee shall recommend maintenance and routing for the access road to GMCS.

3.	Inspections

3.1.	There shall be Annual Grizzly Mountain inspections.

3.1.1.	Inspections shall be performed in September of each year.

3.1.2.	The Technical Committee shall perform the inspection with a representative from the BLM present.

3.1.3	All right-of-way holders and their tenants are welcome to attend.

3.1.4  All potential future Grizzly Mountain users are welcome as observers.

3.2.	Inspections shall include the following items:

3.2.1.	Access road condition and functionality

3.2.2.	Adherence to the overall Grizzly Mountain site development plan.

3.2.3.	General visual inspection of each right-of-way site.

3.2.4.	Detailed floor plan and description of antennas and power for each site.

3.2.5.	Documentation of RF exposure level at 3 feet straight out from each building’s personnel entrance, at each tower base, and at electric meter panel.

3.2.6.	Measurement and documentation of the electromagnetic noise floor at the prescribed frequencies as requested by the Technical Committee.

3.2.7.	All electromagnetic measurements shall be made with qualified and recently calibrated equipment. Three members off the Technical Committee shall accept each measurement as accurate.

3.3.	Reports

3.3.1.	The results of the inspections will be presented at the next Technical Committee meeting.

3.3.2.	The reports will include segments on findings, recommendations, long term resolutions and immediate issues.

3.3.3.	The Technical Committee shall derive and submit a summary and a separate detailed report to the Board of Directors. The reports shall be due to the Board within 30 working days of the completion of the inspection.

    - The Board of Directors shall take appropriate action upon receiving the report.

4.	Application Reviews

4.1.	New Applications

4.1.1.	Applicant for ROW’s shall complete the current BLM data sheet.

4.1.2.	Any new users shall draft an application letter addressed to GMCSUA for review.

4.1.3.	Applicant shall deliver the data sheet and letter to the BLM office and a

copy to the GMCSUA Board of Directors.

4.1.4.	Applicants shall deliver a written statement with regards to accepting the financial responsibility for the elimination or prevention of interference to any GMCSUA right-of-way holder (in good standing) created by their electromagnetic emissions.

4.1.5.	Applicants are encouraged to submit detailed information including but not limited to site plan, technical specifications, Intermodulation, etc.

4.2.	Technical Committee Review

4.2.1.	Applications shall be dated, assigned a log number, and filed upon reception

4.2.2.	All Technical Committee members shall be provided with a complete copy of the application.

4.2.3.	All Technical Committee members shall respond with regards to the application to the Technical Committee Chairman within twenty (20) business days from the date of 4.2.1.

4.2.4.	The committee shall review application and member responses at the next Technical Committee meeting.

4.2.4.1. The committee shall reach an agreement to recommend acceptance of the application as is with no conditions, or

4.2.4.2. The committee shall present the applicant with information regarding recommendations for alterations to application, or

4.2.4.3. The committee shall reach an agreement to recommend acceptance of the application with specific conditions.

4.3.	Applicant actions

4.3.1.	Applicant shall have the right to contact the GMCSUA to inquire about an application or the process.

4.3.2.	Applicant shall have the right to respond to the actions of the Technical Committee in writing to the Board and the BLM.

4.3.3.	Applicant shall contact the BLM and GMCSUA if a decision is made to withdraw the application.

4.3.4. Applicant shall agree to become a GMCSUA member upon issuance of any BLM right-of-way for GMCS use.

4.4.	    Technical Committee reporting

4.4.1.	The Technical Committee Chairman shall provide a written report to the GMCSUA Board of Directors.

4.4.2.	Notification of findings shall be presented to the Applicant.

4.5.	Board of Directors action

4.5.1.	The Board shall act in a timely manner upon the Technical Committee recommendation, and forward the status of the application to the BLM and the Applicant.

4.6.	The Action of the BLM

4.6.1.	Notify the GMCSUA of all applications received

4.6.1.1. Forward all documentation of the application to the GMCSUA immediately.

4.6.1.2. Notify the applicant of the action

4.6.1.3. Notify the applicant of the GMCSUA and its address.

4.6.2.	The BLM shall review the GMCSUA recommendations

4.6.3.	The BLM shall accept or decline the GMCSUA recommendation

4.6.4.	Application acceptance

4.6.4.1. Amend existing right-of-way

4.6.4.2. Create new right-of-way, join GMCSUA.

4.6.4.3. Notify in writing and deliver documentation to applicant.

4.6.5.	Application declined

4.6.5.1. Notify in writing and deliver documentation to applicant.

5.	Grizzly Mountain site planning

5.1.	Long Term Plan

5.1.1.	This long-term site management plan was developed by the joint efforts of BLM, the GMCSUA Technical Committee and all GMCSUA members.

5.1.2.	This plan addresses issues regarding but not limited to:

5.1.2.1. Access roads

5.1.2.2. Individual right-of-way locations

5.1.2.3. Overall compatibility with users relevant to Federal, State, and  Local regulations.

5.1.2.4. Aesthetic presentation of the site (see GMCS Site Map, Appendix A):  New tower height for major towers shall not exceed 110' for the site.  No towers requiring new tower lighting will be authorized, however some existing lights may be relocated onto one of the new towers.  Work and “security” lights shall only be used when needed for night time work, and shall not generally be left on at night.  Any associated buildings will not exceed ten feet in height, and will be painted approved colors as specified by GMCSUA/BLM.

5.1.2.5. Co-locations and or migration of facilities to minimize redundant or excessive installations is encouraged.

5.1.2.6. Determining the capacity and overall loading of the complete site

5.2.	The Board of Directors and Technical Committee shall:

5.2.1.	Develop and maintain a site mapping of all facilities

5.2.2.	Develop and maintain a record of existing users and equipment service

5.2.2.1. Includes operating frequencies

5.2.2.2. Listing of antennas

5.2.2.3. Listing of electromagnetic equipment

5.2.2.4. Listing of RF protective devices

5.2.3.	Develop and keep current an Intermodulation Report and RF Study.

5.2.4.	Develop and keep current site inspection reports

5.2.5.	Develop and keep current As-Built documentation

    - Develop and keep a RF study of the site.

6.	 New Transmitter In Service notification

6.1. Applicant responsibility

6.1.1.	Notify the GMCSUA Technical Committee chairman

6.1.1.1. At least two weeks before proposed transmitter test period or commencement of transmitter.

6.1.1.2. Notify date of commencement.

6.1.1.3. Notification of any change of date of initiation.

6.1.2.	Notification requirements

6.1.2.1. Name and telephone of the applicant’s contact person

6.1.2.2. Transmitter location

6.1.2.3. Transmitter operating frequencies and power levels

6.1.2.4.  Proposed testing schedule

6.2.	Technical Committee responsibility

6.2.1.	Include information regarding Applicant in committee minutes and board minutes

6.2.2.	Mail notice to all ROW members

6.2.2.1. Include information provided by Applicant

6.2.2.2. Include current technical committee chairperson telephone number

6.2.3 Insure that Applicant is supplied with a copy of the Rules and                      Regulations

7.	Environmental safety with regards to non-ionizing radiation

7.1.	Warning measures

7.1.1.	Warning signs shall be installed and maintained by GMCSUA.

7.1.2.	Site specific signs shall be installed where needed by ROW holders.

7.1.2.1. Warning operation personnel and general public.

7.1.2.2. The radiation level of each site will determine the loitering time limit for each site as per applicable Federal Regulations.

7.1.2.3. Warning signs shall be posted on towers.

7.2.	Measurements

7.2.1.	The FCC licensee shall perform measurements.

7.2.2.	Documentation shall be recorded in the inspection reports.

7.3.	Standard

    - The radiation levels, warnings and measurements shall conform to the FCC guidelines based on the National Council on Radiation Protection and Measurements (NCRP) and current issue of OES-65.

8.	Electromagnetic Interference

8.1.	Rules

8.1.1.	All right-of-way holders shall comply with the Technical Standards to minimize interference potential

8.1.2.	The Association shall not recognize interference complaints from users who are not in good standing.

8.1.3.	New applicants may be required to furnish an Intermodulation study or other interference related document as requested by the Technical Committee.

8.1.4.	New applicants shall agree to accept financial responsibility for the elimination or prevention of any interference created by the applicant’s electromagnetic emissions before their application can be evaluated.

8.1.5.	The Technical Committee may request a field test for compatibility at the expense of the applicant.

8.2.	Actions upon occurrence of interference

8.2.1.	The right-of-way holder that is subject to the interference

8.2.1.1. Attempt to identify source and conditions of interference

8.2.1.2. Notify the source contact person of the interfering signal as soon as the interference is noticed and follow up with documentation.

8.2.1.3. Notify the Technical Committee chairperson.

8.2.2.	The notified interference source contact person

8.2.2.1. If this is a new transmitting source

8.2.2.1.1. Cease operation immediately

8.2.2.1.2. Review conditions with technical committee chairperson

8.2.2.1.3. Coordinate efforts for a solution with the right-of-way holder that is experiencing the interference

8.2.2.2. If the identified source transmitter has been in operation for a period of two months or longer

8.2.2.2.1. Review conditions with technical committee chairperson

8.2.2.2.2. Coordinate efforts for a solution with the right-of-way holder that is experiencing the interference

8.2.3.	Multiple source conditions

8.2.3.1. Apply the same procedure as above, using identified right-of-way holder that is involved.

8.3.	Resolution of interference

8.3.1.	Solution shall be identified and agreed upon by all parties involved.

8.3.2.	If financial considerations are not agreeable

8.3.2.1. The technical committee shall recommend a solution in writing  to the GMCSUA Board of Directors.

8.3.2.2. The GMCSUA Board will attempt to resolve the issue

8.3.2.3. The BLM or FCC shall resolve the issue if necessary

9.	Documentation to be kept on file by the Secretary:

9.1.	Site Mapping

9.2.	Individual right-of-way numbers and contact information (address and telephone)

9.3.	 Inspection Reports

9.3.1.	Access road

9.3.2.	Complete Grizzly Mountain Site

9.3.3.	Individual right-of-ways

9.4.	Long Term Development Plan

9.5.	As Built Documentation for each right-of-way

9.6.	Intermodulation report

TECHNICAL STANDARDS AND DEFINITIONS

TECHNICAL STANDARDS

Authority for these Standards devolves from the Coos Bay Bureau of Land Management (BLM) concurrence with the Grizzly Mountain Communications Site Plan..  The obligations to comply with them is in-turn, conveyed to all electronic facility operators on Grizzly Mountain through the Association’s Constitution and Bylaws.

The purpose of these Standards is to minimize RF interference, physical damage, and public liability as well as to maintain a reasonable level of aesthetic integrity.  This will provide for improved electromagnetic compatibility of all users, while projecting an image consistent with BLM expectations.  Curry County Land Development Codes also apply.

1.  Buildings

1.1.  New buildings and structures shall conform to the latest edition of the “Uniform Building Code.”  Existing buildings shall endeavor to comply with current standards or with recommendations of the GMCSUA Technical Committee.

1.2. Painting of structures shall comply with the Coos Bay BLM office standard.

1.3.  Structures shall be maintained and kept in good aesthetic appearance.

1.4.  All metallic materials shall be galvanized, stainless steel or plated.  Dissimilar metals shall not be placed in contact with each other in such a manner that a potential for a galvanic junction exists.

2.  Towers

2.1.  New towers shall comply with the current EIA/TIA - 222 standard.  Existing buildings shall endeavor to comply with current standards or with recommendations of the GMCSUA Technical Committee. The GMCSMP specifies limits on new tower heights of 150' for site one, 349' for site two, and 349' for site three.  The face of new towers shall not exceed three feet wide at site one or  five feet wide at sites two or three.   Smaller towers (less than 75' high and two feet wide) at other locations may be considered on a case by case basis.

2.2.  Towers shall meet the manufacturer’s recommended specifications for the Grizzly Mountain/Coos Bay geographical area, if available.

2.3.  All metallic materials shall be galvanized, stainless steel or plated.  Dissimilar metals shall not be placed in contact with each other in such a manner that a potential for a galvanic junction exists.

2.4.  Anti-climb measures on each tower are highly recommended.

2.5.  All guy wire installations shall be installed with respect to travel over the main access roads.  The installation shall not restrict the access of vehicles (of height up to 14 feet) to another site under any circumstance.

3.  Grounding

3.1.  Each right-of-way site shall employ and maintain an industry standard site-grounding system.

3.1.1.  All towers, buildings, and equipment shall be properly bonded to a common site ground.

3.1.2.  Site grounding must be constructed with #2 AWG or larger copper wire bonded to adequate copper electrode system and/or a maintained chemical grounding system.

3.1.3.  All buried joints must be welded.

3.1.4.  All tower guy wires will be grounded by the method recommended by the manufacturer, if known.

3.1.5.  Equipment grounding shall be of industry standard and must be bonded to the site ground system.

4.  Electrical Service

4.1.  All electrical facilities, equipment, and their installation shall conform to the “National Electrical Code”, and local laws.

4.2.  All permanent AC wiring shall be installed in metallic conduit.

4.3.  Back-up power plants shall conform to the “National Electrical Code”.

4.4.  All service loops shall be installed with respect to travel over the main access roads.  The installation shall not restrict the access of vehicles (of height up to 14 feet) to another site under any circumstance.  Power lines shall be buried wherever feasible.

5.  Electromagnetic Equipment

5.1 Transmitting Equipment

5.1.1.  All radiation of out-of-band emissions shall be reduced to a level that they shall not be identified as a source of interference, as defined in 47 CFR, Part 90.209.

5.1.2.  All transmitters shall incorporate protective devices to prevent direct interference to other users.  The implementation of bandpass and/or notch reject cavities/duplexers, and harmonic filters in recommended to keep spurious RF radiation levels to a minimum.

5.1.3.  All transmitters shall incorporate protective devices (i.e. ferrite isolators or circulators and/or bandpass filters) to prevent re-radiation of transmitter mixed signals.

5.1.4.  The emissions of all new transmitters shall not increase the level of the  “noise floor” of any site on Grizzly Mountain.

5.1.4.1.  This will be measured at the time of the test period for a new transmitter.

5.1.4.2.  The measurement shall be in compliance with the GMCSUA inspections test procedures.

5.1.4.3.  The measurement shall be initiated at the discretion of the Board of Directors, but always performed at sites adjacent to the location of a new transmitter that exceeds 800 watts effective radiated power.

5.1.4.4.  If the level exceeds the “noise floor” , then corrective measures shall be the responsibility of the new transmitter owner.

5.1.5.  All transmitters not approved within each right-of-way grant shall be removed from Grizzly Mountain immediately.

5.2 Receiving Equipment

5.2.1.  All receivers shall comply with all applicable parts of 47CFR, Parts 2 and 15.

5.2.2.  All receivers shall incorporate protective devices which will minimize receiver-produced intermodulation.

5.2.2.1.  All receivers shall have adequate preselection.

5.2.2.2.  All receivers (Part 94 point to point, exempt) shall incorporate bandpass cavity selectivity.

5.2.2.3.  All receiver preamplifiers shall have preselectors between the preamplifier and the associated receiving antenna.

5.2.3.   All receivers operating in conformance with 47 CFR, Part 90 shall incorporate CTCSS protection, if needed.

5.3.  Transmission Feed Line

5.3.1.  All antenna feed lines shall be of jacketed or high quality shielded construction.

5.3.2.  Feed lines shall be grounded in compliance with manufacturer’s recommendations, if available.

5.3.3  No unterminated feed lines shall be permitted.

5.3.3.1.  Unused feed lines shall be terminated in their proper impedance.

5.3.3.2.  Old feed lines that will not return to service, shall be removed from the Grizzly Mountain site.

5.4.  Antennas

5.4.1.  All antennas shall be installed in accordance to the right-of-way for each site.

5.4.2.  Antennas shall be installed in accordance with the manufacturer’s specifications.

5.4.3.  Antenna installations shall be designed and constructed to minimize interference.

5.4.3.1.  Physical location shall be designed and submitted in the application process outlined in the GMCSUA Bylaws.

5.4.3.2.  Installation shall conform to the manufacturer’s specifications.

5.4.3.3.  Vertical separation with respect to adjacent towers shall be reviewed in the application process.

5.4.4.  All antennas shall be terminated to the proper feed line.

5.4.5.  All unused antennas should be removed from the towers.

5.4.5.1.  A plan for use of unterminated antennas must be filed with the GMCSUA.

5.4.5.2.  The Technical Committee will make a recommendation to the Board regarding the unused antenna plan.

DEFINITIONS

Desensing - When ambient electromagnetic fields in the vicinity of a receiving antenna induce unwanted voltage on the receiver’s input sufficient to decrease the receiver’s sensitivity to the desired signals.

Noise Floor - The totality of electromagnetic field energy at a given location.  A high noise floor can desense receivers, and can cause neurological and physical health problems.  The FCC Office of Engineering and Technology (OET) published Bulletin 65.  All station engineers are advised to become familiar with these requirements.

RF Radiation - Radio Frequency electromagnetic fields emitted by radio transmitters.