Beam Loss Monitor System

Interface Control Document

Preface

The Beam Loss Monitor (BLM) System includes the distributed Ion Chamber monitors and the Neutron Detectors (NDs) concentrated in the Linac. Fast BLMs will be used in the HEBT, Ring and RTBT.

# Overall Description

The BLM System will be distributed throughout SNS  to measure the radiation produced by lost beam. It will provide data on the beam loss distribution, aide in minimizing those losses, and provide signals to the Machine Protection System (MPS) in the event of excessive loss.

Approximately 300 cylindrical argon-filled ion chambers will be used as the detectors, typically with several per Linac cavity, and one per magnet elsewhere. BLM signals will be conditioned in an analog front end (AFE) circuit. The signals will rise in a few µsecs (the electron component) and last up to 100 µsecs after the macro-pulse due to ion transit times.  These signals will be digitized and processed in a dedicated VME crate. Fast beam inhibit  and low-level, long-term loss warnings will be generated to provide machine protection. The fast loss data will have a bandwidth of 35 kHz. The low level, long term loss data will have much higher sensitivity but only be available over a 10 second average.

NDs will be used in the Linac area. A distribution of 30 photomultipliers will be used for this purpose. Signals from the PMTs will be conditioned with the same electronics as the ion chambers.

The FBLMs will require HV power supply control but the signals will be acquired by fast ADCs housed in the BCM PCI crates. The analog signal handling is not part of this ICD.

External timing is required to synchronize the data acquisition with the macro-pulse structure and provide time stamping.

# General Capabilities

- Detailed time history within the macro-pulse for each BLM.

- Total losses for each BLM each macro-pulse.

- Long-term history, both for wideband and low level losses for each BLM.

- Gain setting and readback for each BLM.

- Fast Loss output for the Machine Protect System.

- Long-term, low level beam loss alarm on exceeding 1 W/m.

- Remote/local system test

- Remote/local Bias Voltage setting.

- System Calibration.

## 1.	Detailed time history within the macro-pulse.

The time history within a macro-pulse is useful but transmitting data for all detectors at the macro-bunch rate would be excessive and unnecessary. Data will be packed and transmitted at a 6 Hz rate.

## 2.	Total losses for each BLM within the macro-pulse.

Data from each BLM will be acquired at 100 kSa/S. These will be summed at the front end (IOC) and stored for transmission to the console level at a rate once per second for all BLM channels at each IOC location. This data will be presented as a “waterfall” display showing detector location on the horizontal axis, Time on the vertical axis, and intensity of loss as color. A more conventional display of detector on the x-axis and amplitude on the y-axis may also be required for update at once or more per second.

## 3.	Long-term loss history for each BLM

A long term history of the slow, low level losses for each BLM will be kept at the console level for use in a “strip chart” or “water fall” like display. This data will be sent up from the IOCs as packets once every 10 seconds. The data will be acquired on each beam pulse but will be averaged over 10 seconds to provide the sensitivity required. Wideband loss data will also be stored at the console level. Total losses throughout the macro pulse shall be stored in a rolling memory for the prior 1000 pulses. Detailed losses within the macro pulse shall be stored for the most recent 100 pulses.

## 4.	Gain setting and readback for each BLM

Each BLM electronics channel will have the capability of 3 jumper selected gain states which   will be used to compensate for known high-radiation locations, such as at dumps , injection, extraction or the collimators or, low radiation locations in well shielded areas. A fourth jumper will be used to select whether the data sent to the ADC for the fast readback comes from the linear amplifier output or the integrator output. This is necessary since the sub microsecond pulse width in the RTBT would be too fast for the linear amplifier and 100 kilo-sampling ADC. A readback of this jumper is provided. In addition, the “Viewing Gain” can be changed (x1, x10) via the control system without effecting the loss level or MPS input data provided to the MPS. Setting this gain may be required on a pulse-to-pulse basis to allow for different mode cycles. Gain setting in the Ring during the macro-pulse is not required. Read back of the jumper-selectable gain and Viewing Gain states will be provided.

## 5.	Fast Loss Output for the Machine Protect System

Each BLM electronics channel will produce an output signal which will be processed to provide a signal to the Machine Protect System (MPS) to shut off the beam in the event the fast beam loss exceeds the programmable threshold level. This signal will represent the beam loss from each detector integrated over the macro pulse. The signal shall be provided within 10 μsec of the loss occurrence. Threshold level comparisons will be done in the MPS-I/F module located in the VME (IOC) crate, where the signal to the MPS hardware will be generated. The output of the MPS-I/F module will go directly to the MPS chassis.

## 6.	Long-term, low-level beam loss alarm on exceeding 1 W/m.

Beam losses should not exceed 1 W/m over the long term. The higher sensitivity will be achieved by limiting the signal bandwidth to 1 kHz to reduce noise, and providing additional gain. This data will be averaged in the IOC over 600 pulses and compared against a reference  representing 1 W/m. Since the signal levels will be very low, measurements of the signal baseline prior to the beam pulse will be required. Each BLM shall have an associated slow loss level reference. The IOC will send warnings as this level is approached and an alarm when it is exceeded. In addition, the long-term, low-level data will be presented as a water-fall display or a strip chart style display. This does not apply to the neutron detector channels.

## 7.	Remote/Local System Test

The BLM System can be tested by rapidly cycling the HV Bias Power Supplies Off and On again. The resulting transient capacitively couples between the high voltage electrode and  the signal electrode and passes through the BLM electronics. In this way all components of the system, including the bias an signal cables,  are checked.

## 8.	Local/Remote Bias Voltage Setting

The ion chambers exhibit a region of nearly constant signal versus bias voltage from several hundred Volts to 3000 V. During studies periods, it may be necessary at times to explore the linear region and so the ability to vary the HV bias Voltage is required. The NDs and FBLM PMTs will require carefull setting of the High Voltage to properly set their gain. Readback of the Voltage, current and polarity will also be needed. Each IOC crate  will contain 2 HV Bias Supplies ( 1 dual unit) , each powering alternate BLM detectors, as well as addition HVPS for the neutron detectors and FBLMs.

9.	System Calibration

Each BLM ion chamber will be calibrated in a controlled laboratory test setup using a certified radiation source. Data will be taken across the entire operating voltage range since the desired operating point may change with different operating conditions. Data will provided for each detector in hardcopy and electronic format. Following installation, tests of the electronics through the actual cabling will be performed using a measured 1 G-Ohm resistor and voltage source. These values shall be used in the electronics calibration database.

# System Configuration

## Distribution of BLMs

The distribution of loss monitors is shown in Table I.									Table I

|  | #FBLM | # BLMs | # NDs | Total AFE Ch |
| --- | --- | --- | --- | --- |
| •DTL_Diag:Cab401 |  | 12 | 15 | 27 |
| •CCL_Diag:Cab301 |  | 14 | 4 | 18 |
| •CCL_Diag:Cab302 |  | 14 | 4 | 18 |
| •SCL_Diag:HB13Cab01 |  | 42 | 3 | 45 |
| •SCL_Diag:HB1Cab02 |  | 44 | 4 | 48 |
| •HEBT_Diag:Cab07 | 3 | 34 |  | 34 |
| •Ring_Diag:Cab05 | 6 | 55 |  | 55 |
| •Ring_Diag:Cab06 | 6 | 52 |  | 52 |
| •RTBT_Diag:Cab04 | 3 | 28 |  | 28 |
| Totals | 18 | 295 | 30 | 325 |

Channels will be grouped according to common region. Typically racks will be located so that cable runs are not longer than 100 meters.

## Analog Front End Circuit Design

The BLM system must provide a measurement range of approximately 2.5 x 104 in order to cover the span from the high end fast loss (1% of beam at a single location) to the low-level loss threshold of 1 W/m. In addition a long-term measurement of low level beam loss extending 2 decades below the 1 W/m level must be made. Including 2-decades at the low end for resolution below the threshold, results in a 21-bit dynamic range.  The low level measurement will be made by providing a separate 1 kHz limited bandwidth signal to the 24-bit ADC and averaging the signal over 10 seconds. The 1 kHz low pass filter limits the noise but still enables measurement of the baseline prior to the beam pulse. This is necessary since the circuit must be DC coupled and amplifier offset, though small, is not negligible. An integrated output will also be provided, which will be used by the MPS-I/F to generate a beam inhibit signal if a reference threshold is exceeded. The integrated output will also be used for data logging for the RTBT signal.

## Packaging

The AFE’s will be housed in 6U high, 220 mm deep Eurocard (VME w/o the interface) modules  mounted horizontally in a separate chassis, with linear power supplies. Boards will hold 8 channels each. ADCs, DACs, Digital I/O, Timing, MPS-I/F and HV Bias Power Supplies modules will be housed in the IOC VME crates.

Cabling

Signals from the detectors will be carried on non-tribo-electric cable to reduce vibration induced noise. BNC connectors with non-PTFE insulators will be used. All signal runs must be continuous (no splices). Patch panel feedthroughs must be insulated from ground. The HV Bias will be connected to the BLMs using red jacketed RG-59 or equivalent. Connectors will be SHV type but with non-PTFE insulators. HV cables will run from the HV PS to the nearest BLM, skip the next BLM and pick up the following one. A separate HV cable from the second HV supply will run to alternate detectors to provide some fallback in case of  HV cable or power supply failure.

FIGURE 2. 32 channel BLM layout

The various signals to be interfaced to the Control System are shown in Table II.

TABLE II

| Signal | Quantity | Type | Range | Characteristic | IOC Rate |
| --- | --- | --- | --- | --- | --- |
| Wideband Loss | 1/BLM | ADC | 24-bits 0-±10 V | 100 kSa/s/ch | 6/sec |
| Low-level Loss | 1/BLM | ADC | 24-bits 0-±10 V | 100 kSa/s/ch | 600 pulses |
| Fast Loss Reference | 1/BLM | DAC | 16 Bits 0-10 V | > 60 Hz | 60 Hz |
| AFE Gain/Mode Readback | 6 bits/BLM | Dig Input | - | TTL | 60 Hz |
| AFE Gain CMD | 1 bit/BLM | Dig Output | - | TTL | 60 Hz |
| AFE Channel Select | 3 bits/AFE Channel | Dig Output | - | TTL | 60 Hz x 32 |
| AFE Module Select | 3 bits/AFE Module | Dig Output | - | TTL | 60 Hz x 32 |
| AFE Module Serial Number | 8 bits/AFE Module | Dig Input | - | TTL | 60 Hz x 32 |
| HV PS Inhibit CMD | 2/HVPS | Digital Output | - | TTL | 60 Hz |
| HV PS Over-current Status Readback | 2/HVPS | VME | - | VME | 60 Hz |
| HV PS Voltage CMD | 2/HVPS | VME | - | VME | 6 Hz |
| HV PS Voltage Readback | 2/HVPS | VME | - | VME | 6 Hz |
| HV PS Current Readback | 2/HVPS | VME | - | VME | 6 Hz |
| Start of Beam | 1/Location | Timing | 1 turn | TTL | 60 Hz |
| Sample Delay | 4/Location | Timing | 1 turn | TTL | 60 Hz |

Based on this table the total number of modules by type can be estimated. This is shown in Table III.

TABLE III

| # IOCs | 14 |
| --- | --- |
| # Util Mod | 14 |
| # Dig I/O | 14 |
| # IP Carrier Modules | 14 |
| # DAC IP Modules | 42 |
| # ADC | 23 |
| # AFE | 45 |
| # MPS/IF | 25 |
| # HV PS (BLM) | 14 |
| # HV PS (ND) | 16 |
| # HV PS (FBLM) | 10 |
| VME Bus Extenders* | 2 |
| # Exp CTLs Crates | 1 |

* A second IOC may be substituted for the Bus Extenders

Analog Data Acquisition

Analog data from the fast and slow loss outputs will be acquired using commercial 24-bit, 100 kSa/s/ch, VME ADC modules. Data will be taken for 1 msec prior to beam to provide baseline acquisition, and for 200 μsec after the beam to allow for ion collection for the fast loss, and 2 msec for the slow loss circuit signal decay.

Integrated loss data will be used as an input to the comparators which generate the signals sent to the MPS to shut off the beam. However, since the RTBT beam pulse is so short, the integrator signal will also be used for the ADC input for the fast data. A jumper will reconfigure those channels for this purpose with its status read back as the MODE. The comparators will have individually programmable references provided by the DACs. The outputs of the comparators in the MPS-I/F modules will be sent to the MPS using standard MPS interface circuitry. No provision has been made to digitize the integrator output except for the RTBT, as stated above. The same data is available by digitally integrating the fast loss data.

HV Power supply voltage and current will also be read back via the VME interface.  Data readback at once per second would be sufficient.

ND data will bethe same as for the BLMs except that the slow loss data will not be acquired. PMT gain for the NDs and FBLMs will be set from an LUT of HV bias vs gain for each detector.

Digital Data Flow

The gain and mode (integrator/linear) readback bits will be acquired by applying a 3 bit board select and a 3 bit channel select code to the digital data bus on each card in an AFE crate. The 5-bits corresponding to each channel will be read back along with one bit per channel of the 8 bits board serial number. Similarly, the Viewing Gain Command bit can be set when the appropriate channel and board code is applied. Since there are only a maximum of 4 boards per AFE crate, 2 AFE crates can be addressed by the 3-bit code from each IOC.

Front End Data Processing

- Data scaling.  Each BLM and ND channel will have gain and offset parameters for the AFE and ADC, and sensitivity of the BLM or ND detector, which must be applied to the data. The offsets should be stored in a separate array. Data must be scaled for presentation in either engineering (Volts) or physics (Rad) units.

- Detailed Time History.  Fast loss data from each BLM and ND channel will be sent to the console at a 6 Hz update rate. The array  will include the pre- and post- macropulse data. At the console, this data may be used to make a waterfall display with detector location along the X-axis, time on the Y-axis and intensity shown as color. The same data shall be available for display as a “scope trace”.

- Total loss per Macropulse. Each fast loss data channel shall have the data summed over the period of interest (macropulse plus 0.1 or 2  msec). The summed data shall be sent to the console at a 1 Hz rate. At the console, this data may be used to make a waterfall display with detector location along the X-axis, time on the Y-axis and intensity shown as color. The same data shall be available for display as a “scope trace”.

- Long Term History for Each BLM. A 1000 pulse FIFO history of the long term, low level losses for each BLM will be kept at the console level for use in a “strip chart” or “water fall” like display. This data will be sent up from the IOCs once per 10 seconds. The fast loss data for the most recent 100 pulses will also be stored at the console level. Total losses throughout the macro pulse shall be stored in a rolling memory for the prior 1000 pulses.

- Slow Loss Data. The slow loss data will be used to warn the operators that the 1 W/m loss level is being approached and will annunciate an alarm when the level is reached. Since the 1 W/m level applies to long term losses and uses data with a bandwidth of a few Hz, the warnings and alarm will be generated from an average of taken over a 1 minute period. This monitoring, warning and alarming shall be done at the console level. Additional processing will be required at the IOC level. The slow loss data will be acquired through 24-bit ADCs at a 100 kSa/s/ch rate. A baseline will be computed from data taken during 1 msec prior to beam and will be subtracted from the beam time data. Total loss during the 1 msec beam pulse and for 2 msec following will be accumulated  and averaged over a 10 sec period to determine if the slow losses exceed the 1 W/m threshold.

- Bias Voltage Setting and Readback. The high voltage bias for the BLMs shall be set at the console level. The power supply current shall be monitored and compared to a standard value at the IOC. A warning shall be generated if the current exceeds the reference value for a 1 second period. This time requirement is needed to allow for the current draw during turn on.

- System Test.  The BLM system can be tested by switching the HV bias supply on and monitoring the resulting transient. Since the voltage capacitively couples from the HV electrode to the signal electrode, the entire system is tested. A table shall be made of expected values for each channel and each gain in response to a defined voltage step. This shall serve as reference for future tests of the system and be stored in the IOC. The IOC shall, on command, perform the test by turning off the system and waiting for a (to be defined) period, then turning on the HV to the prescribed voltage. The outputs will be compared to the table and discrepancies will be sent to the console level.

# Text boxes

.
.
.
.
.
.
.
.
.

.
.
.
.
.
..
.
.
.

..........