DC POWER DISTRIBUTION

### OVERVIEW

The general configuration of the power distribution for the Near Detector front end electronics is shown in Fig. 1.  All cards and subcomponents in the system have this same general configuration.

Fig. 1.  General Power Distribution Scheme

For Near Detector Front End Electronics

### POWER HARNESSES

The power supplies for the MASTER and MINDER crates are commercial supplies made by Weiner, Model 6021.  The Timing crate power is provide by a commercial supply, a High Perfection Technology HS-250.  A wiring harness connects the power supply to the crate.  Fuses F1 and F2 are external to the power supply.  They are sized for the wire gauge of the harness, since the supplies can generally put out more power than the rating of the wires in the harness.  In some cases, multiple wires are used in the power harness for a given voltage.  When multiple wires are used, each wire is individually fused as shown.  In all cases, the number and size of return conductors equals the number and size of the source conductors.  The timing crate power supply harness is integral to the supply, but in-line fuses have been added where the lines exit the power supply casing.  Specific voltages, harness fusing, and cable gauges are shown for each crate in the following drawings and sketches.

PCB FUSING

Power is distributed on crate backplanes through the use of power planes.  The front end cards connect to the power plane through the use of DIN connectors.  The different cards have a different number of power pins for each voltage.  The pins for a given voltage are connected together at the input to the card, and then routed to a fuse, one fuse for each voltage.  Fuses F3 and F4 are sized based on the rating of the pins and the total number of pins used for each voltage.  The pins for the power returns come from a common plane on the cards.  Generally, the number of return pins equals or exceeds the sum of the power pins.  In the cases where there are separate digital and analog voltages, the analog voltages share a common set of return pins, while the digital voltage has a separate set.

Details for the specific front end cards are provided in the tables that follow.

| Power Distribution Parameters for the MASTER |
| --- |
| Power Supply |  | Power Harness |  | Backplane Connector |  | Card |
|  | Size |  | Wire | # Wires | # Wires |  | # Pins | Total | # Pins |  | Size |
| Voltage | F1/F2 |  | Gauge | Source | Return |  | Source | Ampacity | Return |  | F3/F4 |
| +5V | NONE |  | 00 | 1 | 1 |  | 6 | 9 A | 47 |  | 7 A |

Table 1.  Power Distribution Parameters for the MASTER

| Power Distribution Parameters for the MINDER |
| --- |
| Power Supply |  | Power Harness |  | Backplane Connector |  | Card |
|  | Size |  | Wire | # Wires | # Wires |  | # Pins | Total | # Pins |  | Size |
| Voltage | F1/F2 |  | Gauge | Source | Return |  | Source | Ampacity | Return |  | F3/F4 |
| +12 V | 25 A |  | 10 Ga. | 2 | 2 |  | 6 | 9.0 A | 20 (Analog) |  | 3 A |
| +5 V Ana | 25 A |  | 10 Ga. | 2 | 2 |  | 3 | 4.5 A | 20 (Analog) |  | 2 A |
| +3.3 V | 25 A |  | 10 Ga. | 2 | 2 |  | 6 | 9.0 A | 20 (Analog) |  | 4 A |
| -5 V | 25 A |  | 10 Ga. | 1 | 1 |  | 3 | 4.5 A | 20 (Analog) |  | 1 A |
| -12 V | 25 A |  | 10 Ga. | 1 | 1 |  | 3 | 4.5 A | 20 (Analog) |  | 0.25 A |
| +5 V Dig | 25 A |  | 10 Ga. | 2 | 2 |  | 3 | 4.5 A | 7 (Digital) |  | 2 A |

Table 2.  Power Distribution Parameters for the MINDER

| Power Distribution Parameters for the KEEPER |
| --- |
| Power Supply |  | Power Harness |  | Backplane Connector |  | Card |
|  | Size |  | Wire | # Wires | # Wires |  | # Pins | Total | # Pins |  | Size |
| Voltage | F1/F2 |  | Gauge | Source | Return |  | Source | Ampacity | Return |  | F3/F4 |
| +12 V | 25 A |  | 10 Ga. | 2 | 2 |  | 3 | 4.5 A | 20 (Analog) |  | 1 A |
| -5 V | 25 A |  | 10 Ga. | 1 | 1 |  | 3 | 4.5 A | 20 (Analog) |  | 1 A |
| -12 V | 25 A |  | 10 Ga. | 1 | 1 |  | 3 | 4.5 A | 20 (Analog) |  | 1 A |
| +5 V Dig | 25 A |  | 10 Ga. | 2 | 2 |  | 3 | 4.5 A | 7 (Digital) |  | 2 A |

Table 3.  Power Distribution Parameters for the KEEPER

| Power Distribution Parameters for the VTM |
| --- |
| Power Supply |  | Power Harness |  | Backplane Connector |  | Card |
|  | Size |  | Wire | # Wires | # Wires |  | # Pins | Total | # Pins |  | Size |
| Voltage | F1/F2 |  | Gauge | Source | Return |  | Source | Ampacity | Return |  | F3/F4 |
| +5V | NONE |  | 00 | 1 | 1 |  | 6 | 9 A | 47 (total) |  | 2.5 A |
| +12V | NONE |  | 6 Ga. | 1 | 1 |  | 1 | 1.5 A | 47 (total) |  | 1 A |
| -12V | NONE |  | 6 Ga. | 1 | 1 |  | 1 | 1.5 A | 47 (total) |  | 1 A |

Table 4.  Power Distribution Parameters for the VTM

| Power Distribution Parameters for the MTM |
| --- |
| Power Supply |  | Power Harness |  | Backplane Connector |  | Card |
|  | Size |  | Wire | # Wires | # Wires |  | # Pins | Total | # Pins |  | Size |
| Voltage | F1/F2 |  | Gauge | Source | Return |  | Source | Ampacity | Return |  | F3/F4 |
| +5V | 25A |  | 10 Ga. | 2 | 2 |  | 3 | 4.5 A | 9 |  | 2A |

Table 5.  Power Distribution Parameters for the MTM

# Text boxes

Figure 3: Timing VME Crate Power Harness Sketch

Figure 2: MASTER (Readout) Power Harness

Figure 1: MINDER (Front End) Power Harness