## Calculator
NOTE: Enter values in yellow blocks only. Others will be calculated for you.
Transformer Name:
Transformer Ratings Calculator
Impedance Lookup Table
Full-load rating, kVA: | 300 | kVA |  | kVA | 208V | 480V
SNL Standard Impedance, % | 4.7% | % |  | 45 | 2.9% | 2.6%
Line-to-line primary voltage: | 480 | volts |  | 75 | 2.9% | 2.6%
Line-to-line secondary voltage: | 208 | volts |  | 112.5 | 3% | 2.6%
Primary current, FLA: | 360.8545 | amps |  | 150 | 3% | 2.6%
Secondary current, FLA: | 832.7412 | amps |  | 300 | 4.7% | 2.6%
Primary fuse, max of 300% | 1082.5635 | amps |  | 500 | 4.7% | 4.3%
Primary fuse, min of 125% | 451.0681 | amps |  | 750 | 5.75% | 5.75%
Secondary breaker, 125% | 1040.9265 | amps |  | 1000 | 5.75% | 5.75%
Fault duty, primary | 7677.7554 | amps |  | 1500 | 5.75% | 5.75%
Fault duty, secondary | 17717.8971 | amps
Transformer Harmonics Calculator
| K-Factor |  | FHL-Factor | K-Factor is calculated on RLA, FHL-Factor on rated FLA
Fundamental current: | 100 | amps | 832.7412 | Use 100 amps for per-unit, otherwise use measured loads.
Third Harmonic current: |  | amps | 0
Fifth Harmonic current: |  | amps | 0 | Use 1/7th of RLA for VSD drives
Seventh Harmonic current: |  | amps | 0 | Use 1/7th of RLA for VSD drives
Ninth Harmonic current: |  | amps | 0
Eleventh Harmonic current: |  | amps | 0
Thirteenth Harmonic current: |  | amps | 0
Fifteenth Harmonic current: |  | amps | 0
Calculated RMS current, FLA: | 100 | amps | 832.7412
Calculated Harmonic Factors: | 1 |  | 1
Template dated 25Jan99 by HOE |  | Printed: | 2004-11-10