# Energy Efficiency, LEED, and Regulations

The differences between an empirical energy efficiency ranking, such as the Energy Star label for buildings, and compliance with energy standards and regulations is important to understand.  LEED Green Building Certification does document that a building design is “Green” in certain areas, but energy efficiency is based on apparent efficiency designed into a facility (which is inherently an expectation of efficiency but no guarantee) using energy compliance standards.  Compliance with ASHRAE Std 90.1-1999, which is used in LEED for EE points, or compliance with 10 CFR 435A will, unfortunately, not provide any guarantee of an energy efficient building.  This occurs for many reasons, including:

The regs and standards do not distinguish between certain system designs that will lead to excessive energy consumption and others that will lead to much lower consumption and resulting higher efficiency.  Why?  Partly out of ignorance and partly out of the need to follow a “standards-based process” that does not allow certain comparisons.  We have evidence continuing to mount on the detriment to EE caused by large fan systems and by many VAV designs, but we do not have enough evidence to produce solid statistics on the impact.  So, again unfortunately, we must rely on suggesting to building owners and designers that small fan systems (and probably no VAV) are critical to achieving higher efficiency.  We do have results from a preliminary analysis that indicates that, on average for the whole country, the EUI of a building will be 20-30 kBtu/sq-ft higher (on a source energy basis) if a building has a VAV system, but this number could change as the analysis is verified and refined.

The energy budget modeling process used as one option to comply with the standards and regs, and also used to gain LEED points, typically does not allow different types of HVAC systems to be compared against each other in many cases; so the standard VAV is not allowed to be compared against single-zone systems.  This will push designers strongly to only use VAV, since the simulation programs are modeling idealized, perfectly-functioning VAV systems.  The range of major malfunctions and inefficiencies present in many, if not most, VAV systems in the real world are not treated.

The important benefits of separating the “V” from “HVAC” to provide discrete heating / cooling system functions and ventilation / IAQ / exhaust / relief air system functions is also not recognized by the standards and regs.  One major benefit is the increase in quality of thermal control achieved through the potential of one occupant per thermal zone.

One major benefit of separating the V from HVAC is the ability to use small, local heating / cooling systems that only need to run when heating or cooling is required.  If the separate ventilation system provides continuous ventilation, the total volume of air to keep the space fresh and keep the perception of air movement is much less.  The simulation programs that need to be used to estimate the energy impacts of this approach are not readily able to handle the diversity of occupancy patterns that would impact energy use for the small, local system option.

The controls malfunctions that typically cause a large amount of inefficiency in buildings are not modeled in the compliance or LEED certification process, as the simulation programs assume that all controls work perfectly all the time.  A major means of attaining an Energy Star label is to have controls that actually work properly and efficiently, but the standards and regs do not deal directly with this issue (and indirectly only mention it in passing).

The malfunction of air economizers and the resulting energy penalties are assumed to be nonexistent by the standards and regs, since all systems function perfectly.  In the real world, if quality of maintenance is a problem, significant benefit is obtained from systems that cannot cause major energy penalties when they malfunction.  The standards and regs force use of economizers in many cases, although Std 90.1 has provided important exclusions based on climate.  Use of air economizers is unwise in many cases, and if the design separates the V from HVAC, the function of an economizer should be replaced by energy recovery equipment, which is a more technologically sure approach.

Truly high efficiency lighting designs will use quite a bit less energy than the standards and regs require, but designers are often uncomfortable trying to push the limits here.

Compliance with Std. 90.1 is no guarantee of energy efficiency, and indeed some of the requirements in 90.1 will detract from quality space and systems.  The same is true for 10 CFR 435A.  Compliance with 10 CFR 435A or Std. 90.1 can often lead to an Energy Star rating of 50 to 70.  A rating of 75 or higher is needed for an Energy Star label, so we might say the Standards may likely only give us mediocre to better-than-average energy performance.  This is not what is needed for energy efficiency.

Download this document from:  http://eber.ed.ornl.gov/commercialproducts/Design.htm

This document is not necessarily definitive, and comments are appreciated.

Email:  macdonaldjm@ornl.gov