Standard Measurement & Verification Plan

for

Chiller Replacement Projects

Conducted Under DOE’s Super ESPC Program

DRAFT IN PROGRESS

11/16/07

Federal Energy Management Program (FEMP)

Office of Energy Efficiency and Renewable Energy

U.S. Department of Energy

This document was developed for the U.S. Department of Energy’s Federal Energy Management Program by Nexant, Inc., and Lawrence Berkeley National Laboratory. This document WILL BE posted on FEMP’s web site at http://www1.eere.energy.gov/femp/financing/superespcs_mvresources.html.

Comments should be sent to lwebster@nexant.com

Contents

1.	Background	2

2.	How to use this Guide	2

2.1	User Notes	2

2.2	Risk and Responsibility Matrix	3

2.3	Instrumentation Requirements	4

2.4	M&V Plan Summary	4

3.	Chiller Re M&V Plan and Savings Calculation Methods	6

3.1	Overview of ECM, M&V Plan, and Savings Calculation for ECM	6

3.2	Energy and Water Baseline Development	7

3.3	Proposed Energy & Water Savings Calculations and Methodology	12

3.4	Operations and Maintenance and Other Cost Savings	14

3.5	Proposed Annual Savings For ECM	16

3.6	Post-Installation M&V Activities	17

3.7	Performance Period Verification Activities	18

# Background

This document provides a comprehensive framework for a measurement and verification (M&V) Plan for chiller projects performed via an energy performance contract. A working group of industry and private sector parties involved with DOE’s Super ESPC Program developed this document. It should serve the following purposes:

- Provide a foundation for an M&V plan for a common chiller replacement project utilizing a “best practice” approach, which considers risk allocation, engineering accuracy, and cost-effectiveness. This document provides a base document that must be customized for individual applications.

- Reduce development and review times on individual projects.

- Provide guidance to Agencies on what is essential for robust M&V plan for chiller projects.

- Provides an example of an M&V Plan for one of the most common measures that complies with the requirements set forth in the FEMP M&V guidelines, Version 2.2, and

- Provides an example of the format for M&V Plans for Federal ESPC projects, as detailed by the M&V Plan Outline.

This document contains the basis for M&V Plan for chiller retrofit measures, using Option x with some modifications. This methodology is recommended for most one-for-one chiller replacement projects, as outlined in Section 2.1.

# How to use this Guide

## User Notes

The M&V approach outlined herein contains many specific parameters. The prescribed methodologies were developed with consideration for technical accuracy, cost effectiveness, and appropriate risk allocation.

This draft plan is intended to be used as a starting point, and must be customized for each project. This plan only covers section three, M&V Plan and Savings Calculation Methods, of the M&V Plan Outline, and must be used with the first two sections Executive Summary / M&V Overview & Proposed Savings Calculations and Whole Project Data / Global Assumptions.

All text highlighted Yellow should be customized for the project. Highlighted text underlined in italics indicates project specific data that should be included. In some locations, footnotes are included to provide additional instructions.

For projects that deviate from the prescribed methodologies, the ESCO is expected to document the deviations from the base plan, which:

- Allows government staff to easily assess the M&V approach; and

- Helps to ensure a minimum level of rigor is maintained on individual projects in order to maintain the integrity of the DOE program.

This approach is suitable for projects that:

- Consist of one-for-one chiller replacements; a project size of XYZ tons or payback of XY Years, a one-for one replacement on tons, and includes control measures

- Projects where energy saving are more than $x per year and chiller savings comprise more than X% of total project savings

- Projects where the agency seeks a “best practice” approach, which considers risk allocation, engineering accuracy, and cost-effectiveness.

## Risk and Responsibility Matrix

The risk and responsibility matrix provides an overview of risk allocation in a Super ESPC contract. Since the matrix must align with the M&V plan, the following are key items that need to be properly addressed in the Risk and Responsibility matrix for this ECM are outlined in Table 1.

Table 1 : Summary of Risk and responsibility Matrix Items for this ECM

| Responsibility/Description |  |
| --- | --- |
| Financial: |  |
| Interest rates: | N/A |
| Energy prices: | Will use peak demand rates, no ratchet |
| Construction costs: | N/A |
| M & V costs: | Yet to be determined |
| Non-Energy Cost Savings: | $2000 for non-routine maintenance, replacement R-11 |
| Delays: | N/A |
| Major changes in facility: | See Load, below |
| Operational: |  |
| Operating hours: | See Load, below |
| Load: | ESCo not responsible for changes in load. |
| Weather: | ESCo not responsible for weather. |
| User participation: | See Operations, below |
| Performance: |  |
| Equipment performance: | ESCO responsible for equipment performance, as defined by kW/ton performance curves |
| Operations: | Customer must comply with operational sequence installed with ECM. ESCO is responsible for oversight. |
| Preventive Maintenance: | Customer must comply with ESCO specs and manufacturer’s requirements. ESCO is responsible for oversight. |
| Equipment Repair and Replacement: | Agency is responsible for equipment repair and replacement. |

## Instrumentation Requirements

The sample M&V plan specifies the minimum accuracy requirements of the instrumentation to be used for measurements. Specific instrumentation identified in the sample plan are provided as examples of the type of measurement device which should be used. Include the actual specifications and measurement accuracies of any equipment used. If the accuracy is much less than prescribed, the measurements from equipment may not be suitable as they introduce additional error into the energy calculations.

Table 2-2 : Example Instrumentation Specifications

| Equipment Type | Purpose | Accuracy of Measurement | Example Brand Names |
| --- | --- | --- | --- |
| Portable Flow meter | Chilled water flow (GPM) |  |  |
| Inline Flow meter | Chilled water flow (GPM) |  |  |
| Temperature Sensors | Chilled water supply and return temperatures (ºF) |  |  |

## M&V Plan Summary

The following table summarizes the key elements present in this Standard M&V plan for chiller replacements. The content is organized into four sections: Baseline M&V Activities, Post-Installation M&V Activities, Annual / Periodic M&V Activities, and Energy Use and Savings Calculations.

Table 3 : Summary of Key Elements in Standard M&V Plan for Chiller Replacement

| ECM – Chiller Replacement |
| --- |
| Brief ECM Description: |
| M&V Option: | Option: A / B | Protocol: | FEMP M&V Guidelines V 2.2 |
| Baseline M&V Activities: (Summary of Measurements Performed, Assumptions, Other Sources of Data, Baseline Energy Use Calculation Methodology) Mandate baseline meter calibration & accuracy (see Draft ASHRAE G-22 on Central plant instrumentation and efficiency measurements) Perform comprehensive baseline data collection during shoulder and peak months (either April to July or August - October) and include: chiller kWs, Metered tons (Chilled water flow, CHWST, CHSRT), condenser water supply and return temperatures, pump kWs (if affected), cooling tower fan kWs (if affected), outdoor air temperature Baseline documentation: Nameplate data, Operating schedules; Chiller ages and condition; Loads served; location |
| Post-Installation M&V Activities Summary of Inspections, Measurements to be performed, Reporting Requirements and Submittals Post-Installation report in accordance with IDIQ Requirements. Factory test results Commissioning report Measured pump kWs (if affected), cooling tower fan kWs (if affected) |
| Annual or Periodic M&V Activities: (Summary of Inspections, Measurements to be performed, Reporting Requirements and Submittals) O&M data to be provided by facility and included in Annual Report Annual Report in accordance with IDIQ Requirements. Verify O&M has been properly executed, including periodic calibration of instrumentation to prescribed accuracies Perform system performance test utilizing permanently installed metering. Compare measured kW/Ton to expected values Calculate post-installation energy use using measured values applied to baseline load profile |
| Energy Use and Savings Calculations: (Summary of Savings Calculation Method) Use baseline measured data to determine existing operational efficiency curve and load profiles. Determine baseline load relation to outside air temperature (assume linear relationship). Apply to 8760 typical meteorological year (TMY) weather data to normalized baseline. To account for interactions (reductions in load) from other measures, loads saved will be subtracted to arrive at the adjusted baseline. Each year, measured kW/ton of chillers will be applied to adjusted baseline load to determine energy and demand savings. Apply stipulated demand and energy rates to determine cost savings Minimal savings from reduced replacement parts |

# Chiller Re M&V Plan and Savings Calculation Methods

## 3.1	Overview of ECM, M&V Plan, and Savings Calculation for ECM

3.1.1	Three 225-ton centrifugal chillers using R-11 refrigerant will be replaced with three high-efficiency 225-ton centrifugal chillers using R-134a refrigerant. ECM scope includes recovery of the R-11 refrigerant as well as demolition and removal of the old chillers. Related ECMs include control upgrades which will reduce the load on the central plant. Central plant peripheral equipment will be reused.

The chilled water plant supplies 44º F chilled water during the months of April to October. The three existing cooling towers will be reused, along with the pumping and distribution systems. Both the new and old chillers will use condenser water temperatures of down to 70ºF when available.

Capital investment for this ECM is $1,215,000 ($1,800/ton), and first year energy cost savings are estimated to be $35,000/yr, O&M savings of $2,000 are being claimed based on documented replacement parts and purchased R-11 that will be eliminated. The SPB of 33 years is long, but necessary due to the need to replace the aging chillers and to convert refrigerants.  The other measures in this project help to shorten the overall payback of the project.

3.1.2	This measure uses a combination of FEMP M&V options A and B, retrofit isolation with measurement. Although both post-installation loads and energy use of the chillers are being measured continuously, this is not an option B approach since the measured energy use is not used to directly calculate savings.

This approach was selected for this project so the ongoing responsibilities of the project are aligned as agreed to in the risk and responsibility matrix for this project. Since the ESCo is not responsible for changes in loads or weather, the cooling load is stipulated based on measured data during the baseline, and adjusted to “typical” weather. Similarly, since the ESCo is responsible for the performance of the new chillers, equipment performance is validated during each performance year, and savings are recalculated if significant change have occurred. The ongoing performance of the chillers is dependant upon the Agency conducting all operational and maintenance items required.

3.1.3	The M&V plan for this ECM is based on the very thorough baseline data collection and analysis that was conducted which was sufficient to fully quantify the performance of the existing chillers as well as the hourly cooling loads experienced. Baseline metering was conducted for a period of three months which covered both peak cooling and swing month conditions. During the baseline, the existing chillers’ electric power use and load variables (chilled water flow, chilled water supply temperature, chilled water return temperature, condenser water temperature, chiller kW) were metered.

The purpose of collecting baseline chiller data was to develop two models: 1) the existing chillers’ efficiencies and, 2) the cooling loads experience by the plant based on outdoor air temperature. Approximately three months of baseline metering was conducted, with enough data points collected to successfully build both the performance model and the cooling load model.

The baseline cooling load model which was constructed using local measured weather conditions was applied to typical meteorological year (TMY) weather data for the site to determine the average annual cooling load profile for the facility. Performance models of the existing and proposed chillers were applied to this average load profile to determine the estimated savings. Proposed chiller performance was based on manufacture’s performance data under various load and operating conditions.

During the performance period, the cooling load and chiller performances (kWs) will be continuously metered by the EMCS to ensure operation is within expected ranges and to determine actual cooling load. During August of each year the ESCo will perform an annual chiller plant sensor calibration and chiller performance test. The performance test period will start immediately after annual calibration is completed, and will last for 2 weeks.

During the first year, the data from the performance test shall be used to develop a performance model of each of the chillers. These models will be applied to the stipulated load profile and compared to the baseline conditions to determine savings.

After the first year, the year 1 chiller models shall be validated, then the model is still valid and can be re-used to calculate savings. If the model is not found to still be valid, metered data from that performance period will be used to develop an updated model, which will be applied to determine savings.

    - Energy and demand savings calculations will be based on the cooling load profile developed during the baseline that was adjusted to typical TMY weather data. The post-installation chiller energy and demand is determined from validated performance period models.

The new chiller performance model using verified kW/ton values is applied to the cooling load profile, and total energy and peak demand for each month is determined. Baseline and post-installation model results are compared for each hour of the year, and energy and demand savings are calculated from the coincident time periods. The annual energy savings are the sum of the hourly energy savings and the peak demand savings are determined for each month during the time period which corresponds to the times when the building’s peak demand is typically set.

## 3.2	Energy and Water Baseline Development

### 3.2.1	Data collection of each of the existing chillers’ demand, entering and leaving chilled water temperatures occurred during April 3 to July 17, 2006. Also collected were total chilled water flow and condenser water temperatures for the entire plant. The nameplate data for the existing chillers is summarized in Table 4.

Table 4 : Summary of Nameplate Data for Baseline Chillers

| Item | Chiller #1 | Chiller #2 | Chiller #3 |
| --- | --- | --- | --- |
| Brand | Trane Cetravac | Trane Cetravac | Trane Cetravac |
| Model | Model F-GD2-GO2 | Model F-GD2-GO2 | Model F-GD2-GO2 |
| Capacity | 225 tons | 225 tons | 225 tons |
| Rated kW | 194 kW | 194 kW | 194 kW |
| Serial # | N/A | N/A | N/A |

### The data was collected in coincident 15-minute intervals using both stand-along data loggers and the EMCS system, as detailed in Table 5. In order to collect data over a full range of operating conditions (chilled and condenser water temperatures, chiller demand), the condenser and chilled water temperatures were reset manually.

### The data was analyzed and an appropriate model of chiller performance was developed for each chiller, as described below. Similarly, an hourly ton-hour load model based on the metered load and outdoor air temperatures was developed. The hourly load model was adjusted to TMY data, and the chiller models were applied to this “average” load profile to determine baseline energy and peak demand use for each month.

3.2.2	The key variables affecting baseline energy use are total cooling load, chiller staging, chilled water temperature, condenser water temperature, chilled water flow rate, condenser water flow rate and the efficiency of the existing chillers.

### 3.2.3	The key system performance factors that characterize the baseline are total cooling load, chilled water temperature, chilled water flow rate, condenser water temperature, and chiller efficiency.

### 3.2.4	Requirements for government witnessing of measurements are as defined in whole project data requirements earlier in the M&V plan. The baseline measurements for the chiller were witnessed and certified by Facilities Supervisor Don Wong on 7/17/06, and documentation is included in the Appendix.

### 3.2.5	Chiller plant metering utilized both the EMCS data and stand-along loggers. Prior to starting data collection, the EMCS sensors were calibrated to ensure accuracy.  Data were collected for all points in coincident 15 minute intervals.  A summary of the data points collected and calibration performed is provided Table 5. The calibration forms used are included in the Appendix. An excerpt of the measured data is shown in Table 6, and all data were submitted in spreadsheet format along with this M&V plan.

Table 5 : Chiller Baseline Data Collection

| Data Point | Collection Device | Make / Model | Measurement Accuracy | Calibration Device |
| --- | --- | --- | --- | --- |
| Chilled Water Supply temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Chilled Water return temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Condenser water supply temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Condenser water return temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Chilled water flow rate | Portable ultrasonic flow meter |  |  | ? |
| Chiller kW | Elite 6-channel data recorder |  |  | Fluke 40 |
| Outdoor Air Temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Outdoor Air Wet-bulb Temperature |  |  |  | ? |

Table 6 : Excerpt from Baseline Data Collected

### The baseline data was analyzed to determine 1) building cooling load profile, and 2) performance of the existing chillers. The baseline data was manipulated to calculate tons of cooling for each chiller at each 15-minute time interval, per equation below.

Equation 1:

### TONSt = (CHWF)(500)(CHWRT – CHWST) / (12,000)

Where:

CHWF	Chilled water flow in gallons per minute (GPM) for chiller

(Total chilled water flow/number of chillers on-line)

CHWRT	Entering chilled water temperature (return temperature, (F)

CHWST	Leaving chilled water temperature (supply temperature, (F)

500		Conversion from GPM to Btu per hour-degree Fahrenheit

12,000	Conversion from BTUH to tons

The calculated baseline cooling loads were correlated to measured outdoor air temperature, as shown in Figure 1. Although the correlation of tons to temperature had a coefficient of variation (R2) was less 0.5, this correlation is sufficient to predict the annual cooling loads. The load profile of the facility was then applied to hourly TMY data from WBAN 94728 weather site to determine annual loads.

Figure 1 : Measured Tons and Outdoor Air Temperature

The cooling loads calculated to be saved from the other measures included in this project were then subtracted to determine the adjusted cooling loads. The occupancy schedule of the facility was applied, and loads during unoccupied hours were deleted. The baseline adjustments made and resulting monthly loads are in Table 7.

The result is an hourly model of the chiller load profile using “average” weather conditions shown below.

Table 7 : Baseline TMY Loads and Adjustments Made

| Month | ECM #1- Cooling Ton-Hours Saved | ECM #2- EMCS Cooling Ton-Hours saved | Total Cooling Ton-Hours Adjusted | Ton Hours |
| --- | --- | --- | --- | --- |
| 1 | - | - | - | - |
| 2 | 2 | - | 2 | 283 |
| 3 | 79 | - | 79 | 12,767 |
| 4 | 177 | - | 177 | 28,640 |
| 5 | 845 | 685 | 1,531 | 137,082 |
| 6 | 1,223 | 992 | 2,215 | 198,335 |
| 7 | 1,470 | 1,192 | 2,661 | 238,346 |
| 8 | 1,344 | 1,090 | 2,433 | 217,918 |
| 9 | 1,106 | 897 | 2,003 | 179,388 |
| 10 | 496 | - | 496 | 80,499 |
| 11 | 111 | - | 111 | 17,947 |
| 12 | 60 | - | 60 | 9,698 |
| Totals: | 6,911 | 4,855 | 11,767 | 1,120,902 |

Figure 2 : Measured Cooling Load Applied to TMY Weather Data

Options for Analysis:

There are several component based models that work well with metered chiller data. Two options are presented herein.  Picking a model to use should be based on the level of variation expected in the operating parameters of the chiller.

For  systems utilizing fairly constant chilled and condenser water temperatures,  a simplified linear model is appropriate:

1/COP = C1(1/Load) + C0

This approach offers a simplified regression technique by using the reciprocal values of COP and Load. The coefficients C1 and C0 can be determined from measured data. The final equation can be manipulated and used to predict actual COP, and then kW/ton.

For systems using more dynamic operating conditions, a temperature dependent model should be used. Measured data should be used to determine the coefficients A0 to A9. The resulting equation can then be applied to the load profile and actual operating conditions.

Power = A0 + A1*TCHW  + A2*TCHW2  + A3*TCW + A4*TCW2  + A5*PLR  + A6*PLR2 + A7*TCHW*TCW  + A8*TCHW*PLR + A9*TCW*PLR

### The chiller performance models were developed for each chiller using the metered data and applied to the following component based model:

Equation 2:

Power = A0 + A1*TCHW  + A2*TCHW2  + A3*TCW + A4*TCW2  + A5*PLR  + A6*PLR2 + A7*TCHW*TCW  + A8*TCHW*PLR + A9*TCW*PLR

Metered data from was used along with equipment nameplate data to determine the coefficients A0 through A9 for the existing chillers.

Although the chillers are identical and are operated in parallel, a performance model for each chiller was developed and applied. This approach ensures any differences in the performance of the existing units are captured. The models were developed using Microsoft Excel’s regression function. These models have a close fit to measured data, as shown in Figure 3  below. The statistical results of the analyses are included in the Appendix.

Table 8 : Baseline Chiller Model Coefficients

| Coefficient | CH 1 | CH2 | CH3 |
| --- | --- | --- | --- |
| A0 | 456.0386 | 70.45294 | 15.51836 |
| A1 | -9.43391 | -1.43935 | -0.02565 |
| A2 | 0.01412 | 0.004126 | -0.00018 |
| A3 | -6.20574 | -0.9671 | -0.38504 |
| A4 | 0.007466 | 0.002007 | 0.002305 |
| A5 | 143.6792 | 0 | 0 |
| A6 | -55.2703 | -55.1646 | -33.4058 |
| A7 | 0.107666 | 0.013987 | 0.000566 |
| A8 | 0.360037 | 1.882767 | 1.531132 |
| A9 | 0.499539 | 1.364763 | 1.38086 |

Figure 3 : Measured and Predicted kW for Chiller-1

## 3.3	Proposed Energy & Water Savings Calculations and Methodology

3.3.1	The savings calculation approach for this measure compares hourly energy use of the baseline as predicted by the chiller models developed from measured data and adjusted to TMY load conditions to that of the verified post-case performance. Post-case chiller performance will be based on mathematical models developed from short-term metered data collected in the first performance year, using the same strategies used to build the baseline models.

The post-installation chiller models will be applied to the adjusted load profile that is based on TMY data. Energy and demand savings will be calculated for each hour, and peak demand savings will be determined for each calendar month. The peak demand savings will only be considered between 1 and 4 PM on weekdays, which is when the building’s overall peak demand is set. Manufacturer’s performance data was used to initially predict the performance of the new chillers.

After the first year, the post-installation chiller models shall be validated to ensure continued accuracy by  using the model validation strategy detailed in Section 3.7.7. If the model is found to still be valid, it will  be used to calculate savings. If the model is not found to still be valid, metered data from that performance period will be used to develop an updated model, which will be applied to adjusted loads to determine performance period energy and demand use.

### 3.3.2	Key assumptions included in this approach are:

### The identical chillers operating in parallel will have equal loading between the operating units.

### The total chilled water flow measured in the shared supply header is equally shared between operating chillers.

### TMY weather data from WBAN 94728 weather site (Central Park) accurately depicts a “typical” weather year for the site.

### The load profile that was determined from measured data during the baseline and applied to the TMY data accurately depicts the load profile for the facility.

- The baseline and post-installation chiller performances are accurately depicted in the mathematical models developed.

- Cooling tower performance (approach and range) measured during the baseline will remain constant during the performance period.

### 3.3.3	The energy and demand savings will be calculated using Equations 3 and 4.

Equation 3:

Energy Savings (kWh) = (t (kWht, baseline – kWht, post )

Where:

kWht,baseline=		Energy that the baseline chillers would have used under the average TMY load conditions encountered for hour interval t in the post-installation period

kWht, measured, post 	=	Energy required by the new chillers under the average TMY load conditions encountered for hour interval t in the post-installation period

Equation 4:

Monthly Demand Savings (kW) = MAX{(kWt,baseline) – (kWt,post)}

Where:

(kWt,baseline) is the baseline chiller demand predicted for each 15-minute interval during the building’s peak period during hour t using the model developed for the baseline chiller.

(kWt,post) is the measured demand of the new chiller during the same interval.

Annual cost savings will be calculated using Equation 5.

Equation 5:

Annual Cost Savings = Energy Savings (kWh) * RatekWh + 
					(month(Monthly Demand Savings * RatekW)

### 3.3.4	The chiller load and performance baseline is fixed for the duration of the contract and will not be adjusted. Post-installation savings may vary from year to year if the measured post-installation performance of the chillers varies significantly.

### The energy and demand rates used to calculate cost savings are based on actual utility cost structures, and discussed in Whole Project Data / Global Assumptions section of this M&V plan. The peak demand charges apply to the maximum peak demand set for the building, which usually occurs from 1 PM to 4 PM weekdays for all calendar months. Therefore, chiller demand savings will only be considered during those hours.

### These rates will be escalated at a rate of 2.2% per year as shown in Table 9 : Performance Period Energy and Demand Rates and discussed in Whole Project Data / Global Assumptions section of this M&V plan.

Table 9 : Performance Period Energy and Demand Rates

| Performance Year | Energy $/kWh | Peak Demand $/kW |
| --- | --- | --- |
| 0 | $ 0.0525 | $ 9.57 |
| 1 | $ 0.0537 | $ 9.78 |
| 2 | $ 0.0548 | $10.00 |
| 3 | $ 0.0560 | $10.22 |
| 4 | $ 0.0573 | $10.44 |
| 5 | $ 0.0585 | $10.67 |
| 6 | $ 0.0598 | $10.90 |
| 7 | $ 0.0611 | $11.14 |
| 8 | $ 0.0625 | $11.39 |
| 9 | $ 0.0639 | $11.64 |
| 10 | $ 0.0653 | $11.90 |
| 11 | $ 0.0667 | $12.16 |
| 12 | $ 0.0682 | $12.43 |
| 13 | $ 0.0697 | $12.70 |
| 14 | $ 0.0712 | $12.98 |
| 15 | $ 0.0728 | $13.26 |
| 16 | $ 0.0744 | $13.56 |
| 17 | $ 0.0760 | $13.85 |
| 18 | $ 0.0777 | $14.16 |
| 19 | $ 0.0794 | $14.47 |
| 20 | $ 0.0811 | $14.79 |

### 3.3.6	The proposed annual savings for this energy conservation measure for performance period and cost savings for year 1 are Summarize information in Table 11.

## 3.4	Operations and Maintenance and Other Cost Savings

### 3.4.1	O&M cost savings will result from the replacement of the chillers. The savings will be due to reduced replacement parts, specifically refrigerant R-11. The existing chillers all have small leaks in the evaporator bundles, which have made quarterly refrigerant recharges mandatory for the last 3 years. Refrigerant purchase data from the site from the last two years was reviewed to determine actual costs. The historical costs and analysis are presented in Table 10. The total baseline costs that will be offset by the installation for the new chillers averaged $2,315 per year.

Table 10 : Baseline Chiller Refrigerant Costs

| Date | Amount Purchased (Lbs) | Cost |
| --- | --- | --- |
| 1/12/04 | 150 | $ 922.50 |
| 6/6/05 | 150 | $ 934.75 |
| 1/6/05 | 100 | $ 622.00 |
| 3/31/05 | 100 | $ 622.00 |
| 7/1/05 | 100 | $ 675.00 |
| 12/15/05 | 100 | $ 675.00 |
| 3/22/06 | 100 | $ 688.00 |
| 6/6/06 | 100 | $ 688.00 |
| Total Purchased: | 900 | $5,827.25 |
| Amount remaining (7/30/06): | 150 | $ 971.21 |
| Total Used: | 750 | $4,856.04 |
| Average Cost / LB: | $ 6.47 |  |
| Number of Months: | 28 |  |
| Ave. Cost per Month | $ 173.43 |  |
| Cost per year: | $ 2,081.16 |  |

Annual O&M savings adjustment factors will be calculated at a rate of 2.2% per year, as detailed in the Whole Project Data / Global Assumptions section of this M&V plan.

3.4.2	No other cost savings will be generated by this measure.

## 3.5	Proposed Annual Savings For ECM

[Include all applicable fuels / commodities for project, e.g., electric energy, electric demand, natural gas, fuel oil, coal, water, etc.]

Table 11 : Proposed Annual Savings for ECM

|  | Total energy use (MBtu/yr) | Electric energy use (kWh/yr) | Electric energy cost, Year 1 ($/yr) | Electric demand* (kW/yr) | Electric demand cost, Year 1 ($/yr) | Natural gas use (MBtu/yr)* | Natural gas cost, Year 1 ($/yr) | Water use (gallons/yr) | Water cost, Year 1 ($/yr) | Other energy use (MBtu/yr) | Other energy cost, Year 1 ($/yr) | Other energy-related O&M costs, Year 1 ($/yr) | Total costs, Year 1 ($/yr) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Baseline use | 2,947 | 863,531 | $ 46,333 | 2,931 | $ 28,668 | 0 | $- | 0 | $- | 0 | $ 2,081 | $ - | $ 77,082 |
| Post-installation use | 1,880 | 550,977 | $ 29,563 | 1,870 | $ 18,292 | 0 | $- | 0 | $- | 0 | $ - | $ - | $ 47,854 |
| Savings | 1,067 | 312,554 | $ 16,770 | 1,061 | $ 10,376 | - | $- | - | $- | - | $ 2,081 | $ - | $ 29,228 |
| Notes *Annual electric demand savings (kW/yr) is the sum of the monthly demand savings. MBtu = 106 Btu. If energy is reported in units other than MBtu, provide a conversion factor to MBtu for link to delivery order schedules (e.g., 0.003413 MBtu/kWh). |

## 3.6	Post-Installation M&V Activities

3.6.1	The intent of the post-installation verification activities is to verify the ECM has been installed as intended, and has the capacity to generate the expected savings.  This will be confirmed by developing post-installation performance models of the chillers using measured chiller performance, and then using those models to calculate expected energy savings.

Included in the report will be a summary of the specifications for the installed equipment as well as an inventory of installed control sensors, including their measurement accuracy and confirmation of calibration. The Post-Installation report will follow IDIQ requirements. A separate commissioning report including factory test results for the new chillers will also be submitted.

### 3.6.2	The key variables affecting post-installation energy use are total cooling load, chiller staging, chilled water temperature, condenser water temperature, chilled water flow rate, condenser water flow rate, rated capacity and efficiency of new chillers.

### 3.6.3	The key system performance factors that characterize the post-installation conditions are total cooling load, chilled water temperature, chilled water flow rate, condenser water flow rate, condenser water temperature, actual chiller efficiencies.

### 3.6.4	Requirements for government witnessing of post-installation measurements are the same as the whole project data requirements included in Whole Project Data / Global Assumptions section of this M&V plan.

3.6.5	Post-installation data collection for M&V purposes will focus on modeling the performance of the new chillers and confirming expected energy and demand savings. Commissioning activities will be conducted and are reported separately.

The EMCS system will be used to collect post-installation data, as all necessary instrumentaion will have been installed with the new chillers. Prior to collecting any data for the post-installation report, all related sensors will be field calibrated. Equipment to be field calibrated each year is listed in Table 14.

Table 12 : Summary of Annual EMCS Calibration Requirements

| Data Point | EMCS Collection Device | Make / Model | Measurement Accuracy | Calibration Device |
| --- | --- | --- | --- | --- |
| Chilled Water Supply temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Chilled Water return temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Condenser water supply temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Condenser water return temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Chilled water flow rate | IN-line flow meter |  |  | ? |
| Chiller kW |  |  |  | Fluke 40 |
| Outdoor Air Temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Outdoor Air Wet-bulb Temperature |  |  |  | ? |

Coincident 15-minute performance data, similar to what was collected in the baseline will be collected for a period of two-weeks after commissioning is completed, including sensor calibrations. An example data collection format is shown below.

Table 13 : Example Post-Installation Data Collection Format

### 3.6.6	The chiller performance models were developed for each chiller using the metered data and applied to the same component based model used in the baseline:

Equation 6:

Power = A0 + A1*TCHW  + A2*TCHW2  + A3*TCW + A4*TCW2  + A5*PLR  + A6*PLR2 + A7*TCHW*TCW  + A8*TCHW*PLR + A9*TCW*PLR

Metered data will be used along with equipment nameplate data to determine the coefficients A0 through A9 for the new chillers, following the same procedures used in the baseline.

Once validated, the models of the new chiller will be used to calculate expected energy and demand use of the new system.  The updated models will be applied to the stipulated load profile that is based on TMY data to calculate expected savings for the first performance year.

## 3.7	Performance Period Verification Activities

3.7.1	The key variables affecting post-installation energy use are total cooling load, chiller staging, chilled water temperature, condenser water temperature, chilled water flows, condenser water flows, and the actual efficiency of the chillers. The values used for these parameters in the energy calculations are estimated from measured baseline conditions and new equipment performance data.

3.7.2	The key system performance factors that characterize the performance period conditions are total cooling load, chilled water temperature, chilled water flow rate, condenser water flow rate, condenser water temperature, and actual chiller efficiencies.

### 3.7.3	The intent of performance period verification activities is to verify the new chillers are performing properly by comparing the measured performance to the expected performance. Validated performance models based on actual measured chiller performance will be used to calculate energy savings. For informational purposes only, the total monthly ton-hours measured during the performance period will be reported and compared to the stipulated cooling loads.

### 3.7.4	Field calibration and performance testing of the chillers will occur the last two weeks in August. The annual performance report will be submitted by September 15 each year.

### 3.7.5	Requirements for government witnessing of performance period measurements are the same as specified in Whole Project Data / Global Assumptions section of this M&V plan. The annual report will include certification of the data by an appropriate Agency representative.

### 3.7.6	The EMCS system will be used to collect performance period data, as all necessary instrumentaion has been installed with the new chillers. Prior to collecting any data for the annual performance report, all related sensors will be field calibrated. Equipment to be calibrated each year is listed in Table 14.

Table 14 : Summary of Annual EMCS Calibration Requirements

| Data Point | EMCS Collection Device | Make / Model | Measurement Accuracy | Calibration Device |
| --- | --- | --- | --- | --- |
| Chilled Water Supply temperature | Resistance temperature detectors (RTDs) |  | + / - 0.1ºF | Fluke Thermocouple Thermometer 51/51II |
| Chilled Water return temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Condenser water supply temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Condenser water return temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Chilled water flow rate | In-line turbine flow meter |  |  | ? |
| Chiller kW | True RMS Power Meter | ELITEpro™ Recording Poly-Phase Power Meter | + / - 1% | Fluke 40 Power Quality Analyzer |
| Outdoor Air Temperature |  |  |  | Fluke Thermocouple Thermometer 51/51II |
| Outdoor Air Wet-bulb Temperature |  |  |  | ? |

Coincident 15-minute performance data, similar to what was collected in the baseline will be collected for a period of two-weeks after sensor calibration has been completed. An example data collection format is shown below.

Table 15 : Example Post-Installation Data Collection Format

    - After the first year, the post-installation chiller models shall be validated to confirm their continued accuracy by comparing the kW predicted by the model to measured kW from each chiller.

Model Validation Procedures

Data points that will be excluded from this analysis include all measurements within 30 minutes of a chiller start, and any measurements taken after a chiller has been disabled. If the measured kW values are within…..state validation criteria here - IPMVP presents SE (standard error), coefficient of variation Cv(RMSE), and means bias error (MBE).

If the models are still valid, they will be re-used to calculate savings. If any model is not still valid, metered data from that performance period will be used to develop an updated model following the baseline and post-installation procedures. The updated model will be applied to the stipulated load profile that is based on TMY data to calculate savings for that performance period.

### 3.7.8	The Agency is responsible for preventive maintenance, repair, and replacement. A part of this responsibility requires the Agency track and report all related activities conducted each performance year. Since the ESCo is responsible for equipment performance, they must be sure that all operations and maintenance activities are suitable and sufficient.

Detail verification activities and reporting responsibilities of government and ESCO on operations, preventive maintenance, repair, and replacement items.

Annual maintenance reports from the Agency will be submitted to the ESCo by August 1 of each year. The maintenance reports shall document the completion of all required preventative maintenance as defined on the O&M manuals and summarized below. The ESCo will report in the annual report on the adequacy of the chiller maintenance performed.

Table 16 : Summary of Required Chiller Maintenance Items and Frequency

| Quarterly Operation & Maintenance Tasks for Chillers | Organization responsible for the activity | Frequency Required |
| --- | --- | --- |
| Check vane control settings | Check settings per manufacturer’s specifications | Agency | Every 3 months |
| Verify motor load limit control | Check settings per manufacturer’s specifications | Agency | Every 3 months |
| Verify load balance operation | Check settings per manufacturer’s specifications | Agency | Every 3 months |
| Check chilled water reset settings and function | Check settings per manufacturer’s specifications | Agency | Every 3 months |
| Annual Operation & Maintenance Tasks for Chillers |  |  |
| Check chiller lockout setpoint | Check settings per manufacturer’s specifications | Agency | Every 12 months |
| Clean condenser tubes | Clean tubes at least annually as part of shutdown procedure | Agency | Every 12 months |
| Eddy current test condenser tubes | As required, conduct eddy current test to assess tube wall thickness | Agency | Every 12 months |
| Clean evaporator tubes | Clean tubes at least annually as part of shutdown procedure | Agency | Every 12 months |
| Eddy current test evaporator tubes | As required, conduct eddy current test to assess tube wall thickness | Agency | Every 12 months |
| Compressor motor and assembly | • Check all alignments to specification • Check all seals, provide lubrication where necessary | Agency | Every 12 months |
| Compressor oil system | • Conduct analysis on oil and filter • Change as required • Check oil pump and seals • Check oil heater and thermostat • Check all strainers, valves, etc. | Agency | Every 12 months |
| Electrical connections | Check all electrical connections/terminals for contact and tightness | Agency | Every 12 months |
| Water flows | Assess proper water flow in evaporator and condenser | Agency | Every 12 months |
| Check refrigerant level and condition | Add refrigerant as required. Record amounts and address leakage issues. | Agency | Every 12 months |

# Appendix Materials

Measured baseline chiller data

Documentation of Government Witnessing of Baseline Measurements

Statistical Results for baseline chiller models

# Footnotes

FEMP M&V Guideline V 2.2 available at http://www1.eere.energy.gov/femp/financing/superespcs_mvresources.html

Based on V1.0  M&V Plan Outline for FEMP Super ESPC projects is available at http://www1.eere.energy.gov/femp/financing/superespcs_mvresources.html

op cit

Site - New York Central Park; http://rredc.nrel.gov/solar/old_data/nsrdb/tmy2/State.html

Brademuehl, et al, Methodology Development to Measure In-Situ Chiller, Fan, and Pump Performance, ASHRAE Research Project 827-RP March 1996. The temperature dependent model included in this paper is not recommended as it is difficult to apply appropriately.

Bradford, et al., First Principles Model for Integrated Cooling Systems, 2000 ACEEE Summer Study on Energy Efficiency in Buildings

# Comments

Needs to be defined

See section 3.7.8 -WG should verify risk allocation

Need example equipment list; see IPMVP or G-22 (Cannot find) for accuracy

Complete with other metering tables

Need to validate baseline model

Model validation strategy needed. State how PI model will be validated.

Need G-22 or other source for reference and data. Complete with other metering tables.

Model validation strategy needed  - MBE from IPMVP used here

This is the only reference to R&R. Is this allocated properly? Could we have it go either way?