Standard Measurement & Verification Plan

for

Chiller Replacement Projects

Conducted Under DOE’s Super ESPC Program

FINAL

Approved by ESPC Steering Committee

6/05/08

Federal Energy Management Program (FEMP)

Office of Energy Efficiency and Renewable Energy

U.S. Department of Energy

This document was developed for the U.S. Department of Energy’s Federal Energy Management Program by Nexant, Inc. This document will be posted on FEMP’s web site at http://www1.eere.energy.gov/femp/financing/superespcs_mvresources.html.

Contents

1.	Background	2

2.	How to use this guide	2

2.1	Notes to the User	2

2.2	Risk and Responsibility Matrix	3

2.3	Instrumentation Requirements	4

2.4	M&V Plan Summary	5

3.	Chiller Retrofit M&V Plan and Savings Calculation Methods	8

3.1	Overview of ECM, M&V Plan, and Savings Calculation for ECM	8

3.2	Energy and Water Baseline Development	9

3.3	Proposed Energy & Water Savings Calculations and Methodology	15

3.4	Operations and Maintenance and Other Cost Savings	18

3.5	Proposed Annual Savings For ECM	20

3.6	Post-Installation M&V Activities	21

3.7	Performance Period Verification Activities	22

4.	Appendix Materials	25

Engineering Supplement to FEMP’s Standard M&V Plan for Chiller Replacement Projects	25

# Background

This document provides a comprehensive framework for a measurement and verification (M&V) plan for chiller replacement projects performed via an energy savings performance contract. A working group of industry and private-sector parties involved with DOE’s Super ESPC Program developed this document. It should serve the following purposes:

- Provide a foundation for an M&V plan for a common chiller replacement project utilizing a “best practice” approach, which considers risk allocation, engineering accuracy, and cost-effectiveness. This document provides a base document that must be customized for individual applications.

- Reduce development and review times on individual projects.

- Provide guidance to Federal agencies on what is essential for a robust M&V plan for chiller replacement projects.

- For one of the most common measures in ESPCs, provide an example of an M&V Plan that complies with the requirements set forth in the FEMP M&V guidelines.

- Provide an example of the format for M&V plans for Federal ESPC projects, as detailed in the M&V Plan Outline.

This M&V plan for chiller replacement projects relies on an M&V Option B retrofit isolation approach using periodic on-site measurements. This methodology is recommended for most one-for-one chiller replacement projects, as outlined in this section.

# How to use this guide

## Notes to the User

The M&V approach outlined herein contains many specific parameters. The prescribed methodologies were developed with consideration for technical accuracy, cost-effectiveness, and appropriate risk allocation.

This draft plan is intended to be used as a starting point and must be customized for each project. This plan only covers section three, M&V Plan and Savings Calculation Methods, of the M&V Plan Outline, and must be used in conjunction the first two sections, Executive Summary / M&V Overview & Proposed Savings Calculations and Whole Project Data / Global Assumptions.

All text underlined and highlighted yellow indicates data that should be customized for the project. In some locations, footnotes or text boxes are included to provide additional instructions. Instructions should not be included in the M&V plan.

For projects that deviate from the prescribed methodologies, the ESCO is expected to document the deviations from the base plan. This approach will serve the following purposes:

Allow government staff to easily assess the M&V approach, and

Help to ensure that a minimum level of rigor is maintained on individual projects in order to maintain the integrity of the Super ESPC program.

The methodology included herein is suitable for the following projects:

- Projects that consist of one-for-one replacements of medium and large size chillers.

- Projects in which risks and responsibilities are to be allocated as indicated in Table 1.

- Projects where energy cost saving of approximately $30,000 per year or more result from the chiller replacement. If savings are less, economize on M&V activities. If savings are more, enhance M&V activities.

    - These annual M&V activities are estimated to amount to about 80 hours of engineering labor, with an additional 25 hours for annual O&M activities (sensor calibrations or replacements).

    - Most projects will also include additional initial M&V costs for installing the permanent instrumentation required to conduct these activities.

Companion Document: Engineering Supplement to the Standard Chiller M&V Plan

A companion document, Engineering Supplement to FEMP’s Standard Chiller M&V Plan, is attached as an appendix. The Engineering Supplement provides an outline of the analyses required to implement this M&V plan.

## Risk and Responsibility Matrix

The Super ESPC Risk and Responsibility Matrix provides an overview of risk allocation in a Super ESPC contract. In order to use this standard M&V plan, the project must allocate risks and responsibilities that align with the plan. The risk allocation herein is based on the typical arrangement for Super ESPC projects. Table 2-1 outlines the key items that need to be included in the project’s Risk and Responsibility Matrix for this ECM.

Table 2-1: Summary of Risk and Responsibility Matrix Items For This ECM

| Item of Responsibility | Description of Allocation |
| --- | --- |
| Financial: |  |
| Interest rates: | N/A |
| Energy prices: | ESCO is not responsible for changes in energy rates. |
| Construction costs: | N/A |
| M & V costs: | Included in project costs. First year M&V cost estimated at $6150. |
| Non-Energy Cost Savings: | Inclusion is optional based on project parameters. This example includes $2000 annual cost savings for non-routine maintenance as a place holder. |
| Delays: | N/A |
| Major changes in facility: | See Load, below |
| Operational: |  |
| Operating hours: | See Load, below |
| Load: | ESCO is not responsible for changes in load. |
| Weather: | ESCO is not responsible for weather. |
| User participation: | See Operations, below |
| Performance: |  |
| Equipment performance: | ESCO responsible for equipment performance, as defined by kW/ton |
| Operations: | Customer must comply with operational sequence installed with ECM. ESCO is responsible for oversight. |
| Preventive Maintenance: | Customer must comply with ESCO specifications for preventive maintenance and manufacturer’s requirements. ESCO is responsible for oversight. |
| Equipment Repair and Replacement: | Responsibility for equipment repair and replacement is negotiable specific to Agency policy. |

## Instrumentation Requirements

For the use of this standard M&V plan to be successful, the sensors used for baseline and post-installation measurements must meet minimum accuracy requirements and must be properly calibrated, as shown in Table 2-2. If the accuracy of any instrument is less than prescribed, the measurements may not be suitable, as they will introduce unacceptable levels of error into the energy calculations.

The instrumentation accuracy requirements are designed to ensure that overall energy and cost estimates are reasonable. Although error analysis is not required by Super ESPC projects, it is important to keep in mind that the inaccuracies introduced by the instrumentation will likely be the greatest source of uncertainty in calculated savings.  For a chiller project, the most important measurements are the chilled water temperatures. Additional care should be taken to ensure these sensors have the recommended accuracies.

Table 2-2: Required Instrumentation Accuracies

| Equipment Type | Purpose | Accuracy of Instrumentation |
| --- | --- | --- |
| Flow meter | Chilled water flow (GPM) | ±2% |
| Immersion temperature sensors | Chilled water temperatures (ºF) | ±0.3ºF |
| Immersion temperature sensors | Condenser water temperatures (ºF) | ±0.5ºF |
| Power meters | True RMS Power | ±2% |
| Outdoor air relative humidity / wet-bulb temperature sensors | Outdoor air wet-bulb temperatures | ±3% |
| Outdoor air temperature sensors | Outdoor air dry-bulb temperatures | ±1.0ºF |

The actual specifications and measurement accuracies of any equipment used should be included in the M&V plan. Specific instrumentation types identified herein are provided as examples of the measurement devices that should be used. Other important factors that must be considered in selecting proper instrumentation are locations, installation requirements, signal outputs, and calibration requirements.

## M&V Plan Summary

The following table summarizes the key elements present in this standard M&V plan for chiller replacements. The content is summarized in Table 2-3 into four sections: Baseline M&V Activities, Post-Installation M&V Activities, Annual / Periodic M&V Activities, and Energy Use and Savings Calculations.

Table 2-3 : Summary of Key Elements in Standard M&V Plan for Chiller Replacement

| ECM – Chiller Replacement |
| --- |
| Brief ECM Description: |
| M&V Option: | Option B | Protocol: | IPMVP 2007 |
| Baseline M&V Activities: (Summary of measurements performed, assumptions, sources of data, baseline energy use calculation methodology) Confirm baseline meter calibration and accuracy Collect baseline data across expected range of operating conditions (e.g., load, outside air temperature and humidity), including both shoulder and peak months (either April – July or August – October). Parameters measured include: Chiller electric demand (kW) and energy use (kWh) Chilled water load (tons), calculated from coincident measurements of chilled water flow (gpm), chilled water supply and return temperatures (ºF), Condenser water supply and return temperatures (ºF), Pump and cooling tower demand (kW) and energy use (kWh) (if affected), cooling tower fan kWs (if affected), Outdoor air temperature and humidity. Calculate chilled performance (kW/ton) across expected range of operating conditions (e.g., load, outside air temperature and humidity)., extrapolate short term cooling load measurements to annual cooling load profile for baseline conditions, and verify cooling tower performance (Approach and Range), chilled water and condenser water setpoints , chiller sequencing and other baseline parameters Collect baseline documentation: nameplate data, operating schedules, chiller ages and condition, loads served, location. Document assumptions including: baseline weather conditions (based on TMY2 weather data for nearest site with similar weather conditions), seasonal operating schedules, Month and time of day of peak building demand |
| Post-Installation M&V Activities (Summary of inspections, measurements to be performed, reporting requirements and submittals) Confirm post-installation meter accuracy and calibration Conduct post-installation performance test for two weeks. Parameters to be measured include: Chiller electric demand (kW) and energy use (kWh), Chilled water load (tons), calculated from coincident measurements of chilled water flow (gpm), chilled water supply and return temperatures (ºF), Condenser water supply and return temperatures (ºF), Pump (if affected) and cooling tower fan (if affected) demand (kW) and energy use (kWh), Outdoor air temperature and humidity. Measured pump demand (kW) and energy (kWh) (if affected), cooling tower fan demand (kW) and energy use (kWh) (if affected) Post-Installation report in accordance with IDIQ requirements |
| Annual or Periodic M&V Activities (Summary of inspections, measurements to be performed, reporting requirements and submittals) Confirm meter accuracy and perform calibrations Perform system performance test using permanently installed metering Parameters to be measured include: Chiller electric demand (kW) and energy use (kWh), Chilled water load (tons), calculated from coincident measurements of chilled water flow (gpm), chilled water supply and return temperatures (ºF), Condenser water supply and return temperatures (ºF), Pump (if affected) and cooling tower fan (if affected) demand (kW) and energy use (kWh), Outdoor air temperature and humidity. Calculate chiller performance (kW/Ton) and compare to proposed chiller performance values Calculate performance period energy use and savings using measured values applied to baseline load profile Annual Report in accordance with IDIQ requirements. O&M data to be provided by facility and included in Annual Report Verify O&M has been properly executed, including periodic calibration of instrumentation to prescribed accuracies |
| Energy Use and Savings Calculations (Summary of savings calculation method) Use baseline measured data to determine existing operational efficiency curve and load profiles. Determine baseline load relation to outside air temperature (assume linear relationship). Apply to 8760 typical meteorological year (TMY) weather data to normalized baseline. To account for interactions (reductions in load) from other measures, loads saved will be subtracted to arrive at the adjusted baseline. Each year, measured kW/ton of chillers will be applied to adjusted baseline load to determine energy and demand savings. Apply stipulated demand and energy rates to determine cost savings. There will be minimal savings from reduced replacement parts. |

CHILLER M&V PLAN STARTS ON THE NEXT PAGE

# Chiller Retrofit M&V Plan and Savings Calculation Methods

## Overview of ECM, M&V Plan, and Savings Calculation for ECM

Three 225-ton centrifugal chillers using R-11 refrigerant will be replaced with three high-efficiency 225-ton centrifugal chillers using R-134a refrigerant. ECM scope includes recovery of the R-11 refrigerant as well as demolition and removal of the old chillers. Related ECMs include ECM #1 - Lighting Retrofit and ECM#2 - EMCS (energy management control system upgrade). Both these ECMs will reduce the load on the central plant. All central plant peripheral equipment such as pumps, piping, and cooling towers will be reused.

The chilled water plant uses a constant volume primary loop and a secondary variable flow pumping system to supply 46º F chilled water during the months of April to October. The plant is off-line during November through March of each year. Existing control sequences for the central plant will be maintained. For example, both the new and old chillers will use condenser water temperatures of down to 70ºF when available, and will maintain chilled water temperatures at 46ºF. Chiller staging strategies will also remain the same.

Capital investment for this ECM is $1,215,000 ($1,800/ton), and first year energy cost savings are estimated to be $35,000/yr. O&M savings of $2,000 are being claimed based on documented replacement parts and purchased R-11 that will be eliminated. The SPB of 33 years is long, but necessary, due to the need to replace the aging chillers and to convert refrigerants.  The other measures in this project help to shorten the overall payback of the project.

This measure uses FEMP/IPMVP M&V Option B, retrofit isolation with all parameter measurement. This is an Option B approach since the energy use is measured periodically and is used to directly calculate performance period savings. Performance period savings will be normalized to average weather conditions.

The M&V plan for this ECM is based on thorough baseline and post-installation data collection and analysis. The purpose of collecting baseline chiller data was to define three models:

1) the cooling loads experienced by the plant based on outdoor air temperatures and other variables as needed, and

2) the existing chillers’ efficiencies (i.e., kW/ton),

3) key operating conditions of the chiller plant (e.g. condenser water supply temperatures, chilled water supply temperatures, chiller sequencing).

Baseline metering was conducted for a period of three months which covered both peak cooling loads and swing month conditions. The baseline cooling load model was applied to average weather data (Typical Meteorological Year or TMY) for the site to determine the typical annual cooling load profile for the facility.

Immediately after installation and commissioning is complete, the data from the post-installation performance test shall be used to develop a performance model for each of the chillers. Once validated, these models will be applied to the hourly load profile and compared to the baseline conditions to predict the energy and demand savings for performance Year 1.

During August of each year in the contract period the ESCO will perform an annual chiller plant sensor calibration and chiller performance testing. The performance test period will start immediately after annual calibration is completed and will last for  2 to 8 weeks.

After the first year, measured data will be collected and used to create chiller models for the current performance period. The new chiller performance models will be validated and applied to the hourly load profile to determine savings.

Key operating parameters of the chiller plant will be recorded hourly by the EMCS, and reviewed monthly by the ESCO. Data collected will include chilled water supply and return temperatures, chiller status, condenser water supply temperature, and outdoor air temperature. Periodic verification is required to ensure the proper operating sequences continue to be implemented by facilities staff.

Energy and demand savings calculations will be based on measured baseline chiller demands, key plant operating parameters, and the average cooling load profile for the site. The new chiller performance models, developed and verified using measured values, will be applied to the average cooling load profile. Baseline and post-installation model results are compared for each hour of the year, and energy and demand savings are calculated from the coincident time periods. The annual energy savings are the sum of the hourly energy savings, and the peak demand savings are determined for each month during the time period which corresponds to the times when the building’s peak demand is typically set.

## Energy and Water Baseline Development

### Continuous baseline data collection occurred from April 3 to July 17, 2006. Data collected included each of the existing chillers’ power use and key operating parameters, discussed below. The nameplate data for the existing chillers is summarized in Table 3-1.

Table 3-1: Summary of Nameplate Data for Baseline Chillers

| Item | Chiller #1 | Chiller #2 | Chiller #3 |
| --- | --- | --- | --- |
| Brand | Trane Cetravac | Trane Cetravac | Trane Cetravac |
| Model | Model F-GD2-GO2 | Model F-GD2-GO2 | Model F-GD2-GO2 |
| Capacity | 225 tons | 225 tons | 225 tons |
| Rated kW | 194 kW | 194 kW | 194 kW |
| Serial # | N/A | N/A | N/A |

The key independent variables affecting baseline chiller efficiency and energy use are total building cooling load, chiller sequencing or staging, leaving (or supply) chilled water temperature, entering (or supply) condenser water temperature. Primary chilled water and condenser water flow rates affect the performance of the chillers but are essentially constant for the existing chiller plant.

### The key system performance factors that characterize the baseline conditions are chilled water supply temperature and maximum chiller capacity.

### Baseline chiller plant metering utilized both the EMCS data and stand-alone loggers. Prior to starting baseline data collection, the accuracy of the EMCS sensors were evaluated and were then calibrated or replaced with new calibrated sensors to ensure precision. The sensors used are shown in Table 3-2, and completed calibration forms and certificates are included in the Appendix.

Table 3-2: Chiller Baseline Data Collection Instrumentation Accuracies

| Data point | Location of Sensor(s) | Sensor | Accuracy of Sensor | Data Acquisition & Storage | Measurement Interval |
| --- | --- | --- | --- | --- | --- |
| Chilled water supply temperature | CH-1 CH-2, & CH-3 | Precon STW-24 Thermister | +0.3ºF | EMCS | 15 minutes |
| Chilled water return temperature | CH-1 CH-2, & CH-3 | Precon STW-24 Thermister | +0.3ºF | EMCS | 15 minutes |
| Condenser water supply temperature | Common supply header | Veris TI HC1F2 | +0.2ºC | EMCS | 15 minutes |
| Condenser water return temperature | Common supply header | Veris TI HC1F2 | +0.2ºC | EMCS | 15 minutes |
| Chilled water flow rate | CH-1 CH-2, & CH-3 | Siemens SITRANS FUP1010 | +2.0% flow rate | Siemens SITRANS FUP1010 | 5 minutes |
| Chiller power and energy use (kW & kWh) | CH-1 CH-2, & CH-3 | DENT ELITEpro Poly-Phase Power Meters | +2% | DENT ELITEpro Poly-Phase Power Meters | 5 minutes |
| Outdoor air temperature | Roof | JCI TE-6363 P-1 Outdoor Air Temperature Sensor | +1.0ºF | EMCS | 15 minutes |
| Outdoor air wet-bulb temperature | Roof | Veriteq Spectrum 200 | +3% | EMCS | 15 minutes |

### An excerpt of the measured data is shown in Table 3-3, and all data were submitted in spreadsheet format along with this M&V plan.

### Requirements for government witnessing of measurements are as defined in whole project data requirements earlier in the M&V plan. The baseline measurements for the chiller were witnessed and certified by Facilities Supervisor Don Wong on 7/17/06, and documentation is included in the Appendix.

Table 3-3 : Excerpt from Baseline Data Collected

### The baseline data was analyzed to determine 1) building cooling load profile, 2) performance of the existing chillers, and 3) chiller plant operating parameters.

Building Cooling Load Profile

### The baseline data was manipulated to calculate tons of cooling for each chiller at each 15-minute time interval, per Equation 1.

Equation 1:

### TONSt = (CHWF)(500)(CHWRT – CHWST) / (12,000)

Where:

CHWF	Chilled water flow in gallons per minute (GPM) for chiller

CHWRT	Entering chilled water temperature (return temperature, (F)

CHWST	Leaving chilled water temperature (supply temperature, (F)

500		Conversion from GPM to Btu per hour-degree Fahrenheit

12,000	Conversion from Btuh to tons

The calculated baseline cooling loads were correlated to measured outdoor air temperature, as shown in Figure 1. Although the correlation of tons to temperature had a coefficient of variation (R2) less 0.5, this correlation is sufficient to predict the annual cooling loads. The load profile of the facility was then applied to hourly TMY data from WBAN 94728  weather site to determine annual loads.

Figure 1: Measured Tons and Outdoor Air Temperature

The cooling loads calculated to be saved from the other measures (ECM #1 - Lighting and ECM #2 - EMCS) included in this project were then subtracted to determine the adjusted cooling loads. The occupancy schedule of the facility was applied to the hourly model, and loads during unoccupied hours were deleted. The baseline adjustments made and resulting monthly loads are in Table 3-4.

Table 3-4: Baseline TMY Loads and Adjustments Made

| Month | Baseline Cooling Load (ton-hours) | ECM #1- Lighting Cooling Ton-Hours Saved | ECM #2- EMCS Cooling Ton-Hours saved | Total Cooling Ton-Hours Adjusted | Adjusted Baseline Cooling Load (Ton-Hours) |
| --- | --- | --- | --- | --- | --- |
| 1 |  | - | - | - |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 | 30,022 | 1,382 | - | 1,382 | 28,640 |
| 5 | 139,150 | 1,382 | 685 | 2,067 | 137,082 |
| 6 | 200,709 | 1,382 | 992 | 2,374 | 198,335 |
| 7 | 240,920 | 1,382 | 1,192 | 2,574 | 238,346 |
| 8 | 220,390 | 1,382 | 1,090 | 2,472 | 217,918 |
| 9 | 181,667 | 1,382 | 897 | 2,279 | 179,388 |
| 10 | 81,881 | 1,382 | - | 1,382 | 80,499 |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |
| Totals: | 1,094,738 | 9,674 | 4,855 | 14,529 | 1,080,209 |

The monthly reduction in cooling load due to ECM#1- Lighting Retrofit was estimated from monthly kWh savings. Based on Rundquist method and location, 35% of the lighting energy saved during cooling months was attributed to the cooling load reduction. The cooling load reductions due to ECM #2 - EMCS are detailed in the M&V plan for that measure.

Performance of the Existing Chillers

### A chiller performance model was developed for each chiller using the metered data and applied to the following component-based model:

Equation 2:

Power = A0 + A1 ( TCHW+ A2 ( TCHW2+ A3 ( TCW + A4 ( TCW2+ A5 ( PLR+ A6 ( PLR2 + A7 ( TCHW ( TCW+ A8 ( TCHW ( PLR + A9 ( TCW ( PLR

Where:

TCHW = Chilled Water Supply Temperature

TCW = Condenser Water Supply Temperature

PLR = Part-load ratio (rated tons/actual tons)

A0 - A9= Coefficients determined from measured data

Metered data from was used to determine the coefficients A0 through A9 for the existing chillers.

Although the chillers are identical and are operated in parallel, a performance model for each chiller was developed. This approach ensures any differences in the performance of the existing units are captured. The coefficients in Equation 2 were determined using Microsoft Excel’s regression function. The calculated coefficients A0 – A9 for each chiller are shown in Table 3-5.

Table 3-5: Baseline Chiller Model Coefficients

| Coefficient | CH1 | CH2 | CH3 |
| --- | --- | --- | --- |
| A0 | 456.0386 | 70.45294 | 15.51836 |
| A1 | -9.43391 | -1.43935 | -0.02565 |
| A2 | 0.01412 | 0.004126 | -0.00018 |
| A3 | -6.20574 | -0.9671 | -0.38504 |
| A4 | 0.007466 | 0.002007 | 0.002305 |
| A5 | 143.6792 | 0 | 0 |
| A6 | -55.2703 | -55.1646 | -33.4058 |
| A7 | 0.107666 | 0.013987 | 0.000566 |
| A8 | 0.360037 | 1.882767 | 1.531132 |
| A9 | 0.499539 | 1.364763 | 1.38086 |

Figure 2: Measured and Predicted kW for Chiller 1

Model Validation Procedures

Because the energy use of the chillers is fundamental to the savings guarantee, these models must be validated as sufficiently accurate. Four statistical parameters are checked to verify that the models will not introduce an unacceptable level of uncertainty into the calculated saving.

Data points excluded from this analysis include all measurements within 30 minutes of a chiller start and any measurements taken after a chiller has been taken off-line. Four statistical parameters will be checked to verify that the models will not introduce an unacceptable level of uncertainty into the calculated saving. The parameters evaluated and the recommended acceptable values for these chiller models are shown in Table 3-6. The calculation methodologies for these parameters are detailed in the Engineering Supplement in the Appendix.

Table 3-6 : Statistical Validations Guidelines

| Parameter evaluated | Suggested acceptable values |
| --- | --- |
| Coefficient of variation (R2) | > 0.75 |
| CV(RSME) | < 15% |
| t-statistic | > 2 |
| Mean bias error | < + 7% |

Baseline Model Validation Results

The parameters evaluated, the recommended acceptable values, and the actual values determined for these baseline chiller models are shown in Table 3-7. The calculation methodologies for these parameters are detailed in the Engineering Supplement in the appendix.

These models have a close fit to measured data, as shown in Figure 2 above. The detailed statistical results of the analyses of the baseline chillers are included in the electronic Appendix materials.

Table 3-7: Statistical Validation Guidelines and Results

| Parameter evaluated | Suggested acceptable values | Actual values |
| --- | --- | --- |
|  |  | CH-1 | CH-2 | CH-3 |
| Coefficient of Variation (R2) | > 0.75 | 0.84 | 0.82 | 0.78 |
| CV (RSME) | < 15% | 9.6% | 8.9% | 10.6% |
| t-statistics | Absolute value > 2 |  |
| TCHW |  | 10 | 2 | 18 |
| TCHW^2 |  | -10 | -2 | -3 |
| TCW |  | 3 | 3, | -2 |
| TCW^2 |  | -9 | 2, | -23 |
| PLR |  | 3 | 8 | 27 |
| PLR^2 |  | 4 | 65535 | 655 |
| TCHW*TCW |  | 193 | -204 | -581 |
| TCHW*PLR |  | 11 | 2 | 3 |
| TCW*PLR |  | 0.5 | 33 | 646 |
| TCHW |  | 7 | 34 | 869 |
| Mean Bias Error | < + 7% | 4.2% | -5.5% | -6.4% |

Chiller Plant Operating Parameters

Since the sequences of operation for the chiller plant impacts overall plant efficiency and energy use, the baseline model must include chilled and condenser water temperatures and flows as well as the chiller staging sequences. Actual baseline sequences of operation were confirmed using metered data. The appropriate values for these parameters were then incorporated into the hourly chiller model, and baseline energy and demand usage were then determined. Table 3-8 shows the baseline operating parameters that were determined and then applied.

Table 3-8: Baseline Operating Parameters

| Item | Description of sequences | Baseline values used |
| --- | --- | --- |
| Chilled water temperatures | Chilled water supply temperature is kept at a constant 46ºF. | 46ºF |
| Chilled water flow rates | Chilled water flow rates based on flow measurements at each chiller | ~540 GPM / Chiller up to 1620 GPM & field testing |
| Condenser water temperatures (cooling tower performance) | Cooling tower approach (outdoor air wet-bulb temperature — condenser water supply temperature) was determined to be 7 ºF. Minimum temperature allowed is 75ºF. | 75ºF to 83ºF based on TMY wet-bulb temperatures |
| Condenser water flow rates | Constant condenser water flow rate based on design data and number of pumps operating | 675 GPM / Chiller up to 2025 GPM |
| Chiller staging | Chillers 1, 2, & 3 are rotated evenly based on run-time. Additional chillers are staged on at a maximum PLR of 0.80 and are taken off-line at a minimum PLR of 0.5. |  |

## Proposed Energy & Water Savings Calculations and Methodology

As detailed in the previous section, a performance model of each chiller was developed from measured data, and the building’s cooling loads were determined under typical weather conditions. The estimated savings were determined by comparing energy used by the baseline chiller plant to the manufacturer’s published data on the energy use of the new chillers under the same conditions for each hour of the year. The conditions assumed in both the baseline and post-installation cases include appropriate chiller plant operating conditions and TMY cooling loads.

Based on the TMY cooling loads and plant operating conditions, baseline chiller plant demand use was calculated for each hour of the year. Using the same 8760 hour model, the post-installation chiller plant demand was estimated from manufacturer’s data. Demand savings were determined for each hour, and peak periods were identified. The peak demand savings were calculated for each utility billing month, and the year’s total energy savings were estimated, as described by Equations 3 & 4 below.

Table 3-9: Data Calculation Excerpt

An electronic version of the savings calculations were submitted with this report and are summarized in Table 3-10.

Table 3-10: Estimated Chiller Use and Savings by Month

| Month | Ton Hours | Baseline Peak kW | Baseline kWh | Post-Installation Peak kW | Post-Installation kWh | Peak kW saved | kWh Saved |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | - | - | - | - | - | - | - |
| 2 | - | - | - | - | - | - | - |
| 3 | - | - | - | - | - | - | - |
| 4 | 28,640 | 262 | 21,389 | 160 | 13,647 | 102 | 7,742 |
| 5 | 137,082 | 349 | 104,262 | 212 | 66,525 | 137 | 37,738 |
| 6 | 198,335 | 372 | 153,629 | 222 | 98,023 | 150 | 55,606 |
| 7 | 238,346 | 393 | 186,370 | 238 | 118,914 | 155 | 67,456 |
| 8 | 217,918 | 345 | 168,766 | 201 | 107,681 | 144 | 61,085 |
| 9 | 179,388 | 312 | 137,562 | 185 | 87,771 | 127 | 49,790 |
| 10 | 80,499 | 264 | 59,881 | 159 | 38,207 | 105 | 21,674 |
| 11 | - | - | - | - | - | - | - |
| 12 | - | - | - | - | - | - | - |
| Totals: | 1,080,209 | 2,297 | 831,860 | 1,377 | 530,769 | 920 | 301,091 |

### Key assumptions included in this approach are the following.

### Chilled water flow is measured individually for each chiller.

- Condenser water flows are based on design data.

### TMY weather data used accurately depicts a “typical” weather year for the site.

### The load profile that was determined from measured data during baseline development and applied to the TMY data accurately depicts the load profile for the facility.

- The baseline chiller performances are accurately depicted in the mathematical models developed.

- After installation, new chiller performance will be similarly modeled from periodic performance test data. The manufacturer’s published data accurately estimated performance of the new chillers.

- Cooling tower performance (approach and range) measured during baseline development will remain constant during the performance period.

- Baseline chiller staging sequence as well as chilled and condenser water temperatures are defined from metered baseline data.

- Performance period chiller staging sequence as well as chilled and condenser water temperatures will be periodically confirmed from metered data.

- Factory performance testing will be performed on the new chillers.

- Building peak demand is driven by the chiller plant, and is coincident with the chillers’ peak usage.

### The energy and demand savings are calculated using Equations 3 and 4.

Equation 3:

Energy Savings (kWh) = (t (kWht, baseline – kWht, post )

Where:

kWht, baseline		=	Energy that the baseline chillers would have used under the average TMY load conditions encountered for hour interval t in the post-installation period

kWht, measured, post 	=	Energy required by the new chillers under the average TMY load conditions encountered for hour interval t in the post-installation period

Equation 4:

Monthly Demand Savings (kW) = {(kW baseline) – (kW post)}t-peak

Where:

Time period (t-peak) is defined as the one-hour interval during the building’s peak period (between 1 and 4 PM on weekdays) for that billing month during which the highest baseline demand is set by the chillers. Billing months are defined by the serving electric unity.

(kW baseline) is the demand for the baseline chillers predicted during time t

(kW post) is the  demand of the new chillers predicted during the same interval t

Annual cost savings will be calculated using Equation 5.

Equation 5:

Annual Cost Savings = Energy Savings (kWh) ( RatekWh + 
			(month(Monthly Demand Savings ( RatekW)

### Since the savings are normalized to average conditions, the chiller load and performance baseline is fixed for the duration of the contract and will not be adjusted. These parameters are defined in Table 3-4 and Table 3-5. Performance period savings may vary from year to year if the measured energy performance of the chillers varies significantly. Initial savings estimates used manufacturer’s data to predict post-installation chiller performance, which are included in the Appendix.

### The energy and demand rates used to calculate cost savings are based on actual utility cost structures, and discussed in the Whole Project Data / Global Assumptions section of this M&V plan. The peak demand charges apply to the maximum peak demand set for the building, which corresponds to the chiller peak load. Therefore, chiller demand savings will only be considered during those hours.

### These energy and demand rates will be escalated at a rate of 2.2% per year as shown in Table 3-11.

### Table 3-11: Performance Period Energy and Demand Rates

| Performance Year | Energy $/kWh | Peak Demand $/kW |
| --- | --- | --- |
| 0 | $ 0.0725 | $ 11.25 |
| 1 | $ 0.0741 | $ 11.50 |
| 2 | $ 0.0757 | $ 11.75 |
| 3 | $ 0.0774 | $ 12.01 |
| 4 | $ 0.0791 | $ 12.27 |
| 5 | $ 0.0808 | $ 12.54 |
| 6 | $ 0.0826 | $ 12.82 |
| 7 | $ 0.0844 | $ 13.10 |
| 8 | $ 0.0863 | $ 13.39 |
| 9 | $ 0.0882 | $ 13.68 |
| 10 | $ 0.0901 | $ 13.98 |
| 11 | $ 0.0921 | $ 14.29 |
| 12 | $ 0.0941 | $ 14.61 |
| 13 | $ 0.0962 | $ 14.93 |
| 14 | $ 0.0983 | $ 15.26 |
| 15 | $ 0.1005 | $ 15.59 |
| 16 | $ 0.1027 | $ 15.94 |
| 17 | $ 0.1050 | $ 16.29 |
| 18 | $ 0.1073 | $ 16.64 |
| 19 | $ 0.1096 | $ 17.01 |
| 20 | $ 0.1120 | $ 17.38 |

### The proposed annual savings for this ECM for the performance period and cost savings for year 1 are Summarize information in Table 10.

## Operations and Maintenance and Other Cost Savings

O&M cost savings will result from the replacement of the chillers. The savings will be due to reduced replacement parts, specifically refrigerant R-11. The existing chillers all have small leaks in the evaporator bundles, which have made quarterly refrigerant recharges mandatory for the last 3 years. Refrigerant purchase data from the site from the last two years was reviewed to determine actual costs. The historical costs and analysis are presented in

### Table 3-12. The total baseline costs that will be offset by the installation of the new chillers averaged $2,315 per year.

Table 3-12: Baseline Chiller Refrigerant Costs

| Date | Amount purchased (lb) | Cost |
| --- | --- | --- |
| 1/12/04 | 150 | $922.50 |
| 6/6/05 | 150 | $934.75 |
| 1/6/05 | 100 | $622.00 |
| 3/31/05 | 100 | $622.00 |
| 7/1/05 | 100 | $675.00 |
| 12/15/05 | 100 | $675.00 |
| 3/22/06 | 100 | $688.00 |
| 6/6/06 | 100 | $688.00 |
| Total Purchased: | 900 | $5,827.25 |
| Amount remaining (7/30/06): | 150 | $971.21 |
| Total Used: | 750 | $4,856.04 |
| Average Cost / LB: | $6.47 |  |
| Number of Months: | 28 |  |
| Ave. Cost per Month | $173.43 |  |
| Cost per year: | $2,081.16 |  |

Annual O&M savings adjustment factors will be calculated at a rate of 2.0% per year, as detailed in the Whole Project Data / Global Assumptions section of this M&V plan.

No other O&M cost savings will be generated by this measure.

## Proposed Annual Savings For ECM

Table 3-13: Proposed Annual Savings for ECM

|  | Total energy use (MBtu/yr) | Electric energy use (kWh/yr) | Electric energy cost, Year 1 ($/yr) | Electric demand* (kW/yr) | Electric demand cost, Year 1 ($/yr) | Natural gas use (MBtu/yr)* | Natural gas cost, Year 1 ($/yr) | Water use (gallons/yr) | Water cost, Year 1 ($/yr) | Other energy use (MBtu/yr) | Other energy cost, Year 1 ($/yr) | Other energy-related O&M costs, Year 1 ($/yr) | Total costs, Year 1 ($/yr) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Baseline use | 2,839 | 831,860 | $ 61,637 | 2,297 | $ 26,410 | 0 | $- | 0 | $- | 0 | $2,315 | $- | $90,361 |
| Post-installation use | 1,812 | 530,769 | $ 39,327 | 1,377 | $ 15,832 | 0 | $- | 0 | $- | 0 | $- | $- | $55,159 |
| Savings | 1,028 | 301,091 | $ 22,309 | 920 | $ 10,578 | - | $- | - | $- | - | $2,315 | $- | $35,202 |
| Notes *Annual electric demand savings (kW/yr) is the sum of the monthly demand savings. MBtu = 106 Btu. If energy is reported in units other than MBtu, provide a conversion factor to MBtu for link to delivery order schedules (e.g., 0.003413 MBtu/kWh). |

## Post-Installation M&V Activities

The intent of the post-installation verification activities is to verify that the ECM has been installed as intended and has the capacity to generate the expected savings. This will be confirmed by developing post-installation performance models of the chillers using measured chiller performance, and then using those models to calculate expected energy savings.

Included in the report will be a summary of the specifications for the installed equipment as well as an inventory of installed control sensors, including their measurement accuracy and confirmation of calibration. The Post-Installation report will follow IDIQ requirements and will include factory test results for the new chillers. A separate commissioning report will also be submitted.

The key independent variables affecting post-installation chiller efficiency and energy use are total building cooling load, chiller sequencing, chilled water temperature leaving the chiller, and condenser water temperature entering the chiller. Primary chilled water and condenser water flow rates affect the performance of the chillers but will be essentially constant for the new chiller plant.

### The key system performance factors that characterize the post-installation period conditions are chilled water supply temperature and maximum chiller capacity.

Requirements for government witnessing of post-installation measurements are the same as the whole project data requirements included in Whole Project Data / Global Assumptions section of this M&V plan.

Post-installation data collection for M&V purposes will focus on modeling the performance of the new chillers and confirming expected energy and demand savings. Commissioning activities will be conducted and are reported separately.

The EMCS system will be used to collect post-installation data, as all necessary calibrated instrumentation will be installed with the new chillers. Requirements for instrumentation are detailed in Table 3-14.

Table 3-14: Summary of Post-Installation Instrumentation Requirements

| Equipment Type | Purpose | Accuracy of Instrumentation |
| --- | --- | --- |
| Flow meter | Chilled water flow (GPM) | ±2% |
| Immersion temperature sensors | Chilled water temperatures (ºF) | ±0.3ºF |
| Immersion temperature sensors | Condenser water temperatures (ºF) | ±0.5ºF |
| Power meters | True RMS Power | ±2% |
| Outdoor air relative humidity / wet-bulb temperature sensors | Outdoor air wet-bulb temperatures | ±3% |
| Outdoor air temperature sensors | Outdoor air dry-bulb temperatures | ±1.0ºF |

Coincident 15-minute performance data, similar to what was collected for the baseline, will be collected for a period of at least two weeks after commissioning is completed. The data collection format will be the same as used in the baseline (Table 3-3).

### New chiller performance models will be developed for each chiller using the metered data using the same component-based model used in the baseline:

Equation 6:

Power = A0 + A1 ( TCHW+ A2 ( TCHW2+ A3 ( TCW + A4 ( TCW2+ A5 ( PLR+ A6 ( PLR2 + A7 ( TCHW ( TCW+ A8 ( TCHW ( PLR + A9 ( TCW ( PLR

Metered data will be used to determine the coefficients A0 through A9 for the new chillers, following the same procedures used in developing the baseline.

The model validation procedures described for the baseline chiller model will be use. Once validated, the models of the new chiller will be used to calculate expected energy and demand use of the new system. The updated models will be applied to the stipulated load profile that is based on TMY data and compared hour-by-hour to the baseline model to calculate expected savings for the first performance year.

If normal operating conditions for the chiller plant are not present at the time of project completion, the post-installation performance testing and model development may be deferred. In this case, the factory test results of the chillers’ performance should be used to calculate expected savings for year 1.

## Performance Period Verification Activities

The key independent variables affecting performance period chiller efficiency and energy use are total building cooling load, chiller sequencing, chilled water temperature leaving the chiller, and condenser water temperature entering the chiller. Primary chilled water and condenser water flow rates affect the performance of the chillers but are essentially constant for the existing chiller plant.

### The key system performance factors that characterize the performance period conditions are chilled water supply temperature and maximum chiller capacity.

### The intent of performance period verification activities is to verify that the new chillers are performing properly by comparing the measured performance to the expected performance. Validated performance models based on actual measured chiller performance will be used to calculate energy savings. For informational purposes only, the total monthly ton-hours measured during the performance period will be reported and compared to the stipulated cooling loads.

### Field calibration and performance testing of the chillers will occur in the last  weeks of August. The annual performance report will be submitted by September 30 each year.

### Requirements for government witnessing of performance period measurements are the same as specified in Whole Project Data / Global Assumptions section of this M&V plan. The annual report will include certification of the data by an appropriate Agency representative.

The EMCS system will be used to collect performance period data, as all necessary instrumentation has been installed with the new chillers. Prior to collecting any data for the annual performance report, all related sensors will be verified to be of sufficient accuracy and will be field calibrated by the ESCO. Equipment to be calibrated each year is listed in

### Table 3-15.

Table 3-15 : Summary of Annual Instrumentation Requirements

| Equipment Type | Purpose | Accuracy of Instrumentation |
| --- | --- | --- |
| Flow meter | Chilled water flow (GPM) | ±2% |
| Immersion temperature sensors | Chilled water temperatures (ºF) | ±0.3ºF |
| Immersion temperature sensors | Condenser water temperatures (ºF) | ±0.5ºF |
| Power meters | True RMS Power | ±2% |
| Outdoor air relative humidity / wet-bulb temperature sensors | Outdoor air wet-bulb temperatures | ±3% |
| Outdoor air temperature sensors | Outdoor air dry-bulb temperatures | ±1.0ºF |

Coincident 15-minute performance data, similar to what was collected in developing the baseline, will be collected each year for a period covering two to eight weeks immediately after sensor calibration has been completed. The data collection format will be the same as used in the baseline (Table 3-3).

Each year, new chiller models shall be developed and validated, per the post-installation procedures. The accuracy of the new models will be validated by comparing the kW predicted by the model to measured kW from each chiller, per the post-installation procedures.

The updated model will be applied to the stipulated load profile that is based on TMY data to calculate savings for that performance period.

### The Agency or ESCO is responsible for preventive maintenance, repair, and replacement as agreed upon in the project’s Risk & Responsibility matrix. A part of this responsibility requires the Agency/ESCO to track and report all related activities conducted each performance year. Since the ESCO is responsible for equipment performance, they must be sure that all operations and maintenance activities are suitable and sufficient.

Detail verification activities and reporting responsibilities of government and ESCO on operations, preventive maintenance, repair, and replacement items.

Annual maintenance reports from the Agency/ESCO will be submitted to the ESCO/Agency by August 1 of each year. The maintenance reports shall document the completion of all required preventive maintenance as defined in the O&M manuals and summarized below. The ESCO will report in the annual report on the adequacy of the chiller maintenance performed.

Table 3-16: Summary of Required Chiller Maintenance Items and Frequency

| Quarterly Operation & Maintenance Tasks for Chillers | Organization responsible for the activity | Frequency Required |
| --- | --- | --- |
| Check vane control settings | Check settings per manufacturer’s specifications | Agency | Every 3 months |
| Verify motor load limit control | Check settings per manufacturer’s specifications | Agency | Every 3 months |
| Verify load balance operation | Check settings per manufacturer’s specifications | Agency | Every 3 months |
| Check chilled water reset settings and function | Check settings per sequence of operation | Agency | Every 3 months |
| Annual Operation & Maintenance Tasks for Chillers |  |  |
| Check chiller lockout setpoint | Check settings per manufacturer’s specifications | Agency | Every 12 months |
| Clean condenser tubes | Clean tubes at least annually as part of shutdown procedure | Agency | Every 12 months |
| Eddy current test condenser tubes | As required, conduct eddy current test to assess tube wall thickness | Agency | Every 12 months |
| Clean evaporator tubes | Clean tubes at least annually as part of shutdown procedure | Agency | Every 12 months |
| Eddy current test evaporator tubes | As required, conduct eddy current test to assess tube wall thickness | Agency | Every 12 months |
| Compressor motor and assembly | • Check all alignments to specification • Check all seals, provide lubrication where necessary | Agency | Every 12 months |
| Compressor oil system | • Conduct analysis on oil and filter • Change as required • Check oil pump and seals • Check oil heater and thermostat • Check all strainers, valves, etc. | Agency | Every 12 months |
| Electrical connections | Check all electrical connections/terminals for contact and tightness | Agency | Every 12 months |
| Water flows | Assess proper water flow in evaporator and condenser | Agency | Every 12 months |
| Check refrigerant level and condition | Add refrigerant as required. Record amounts and address leakage issues. | Agency | Every 12 months |

# Appendix Materials

Instructions: The following are called for within the M&V Plan and should be included in the appendix:

- Baseline sensor calibration forms

- Statistical results for baseline chiller models

- Measured baseline chiller data

- Manufacturer’s performance data for new chillers

- Documentation of Government Witnessing of Baseline Measurements

## Engineering Supplement to FEMP’s Standard M&V Plan for Chiller Replacement Projects

This is a step-by-step overview of the data collection and analysis that is required to implement FEMP’s Standard Chiller M&V Plan. Instructions are included for executing the M&V activities during the Baseline Phase, Post-Installation Phase, and Annual M&V Phase. This overview is supplemental information to help facilitate the proper use of the Standard Chiller M&V Plan.

1.	Baseline Phase

Data Collection

Baseline Step 1

Document the make, model, and locations of existing sensors. Ensure that sensors are properly located and that manufacturer’s rated accuracies of sensors are sufficient, per requirements below. If not, replace sensors.

Baseline Step 2

Verify and document the accuracy and calibration of all instrumentation.

Table 4-1: Instrumentation Accuracy Requirements

| Equipment Type | Purpose | Accuracy of Instrumentation |
| --- | --- | --- |
| Flow meter | Chilled water flow (GPM) | ±2% |
| Immersion temperature sensors | Chilled water temperatures (ºF) | ±0.3ºF |
| Immersion temperature sensors | Condenser water temperatures (ºF) | ±0.5ºF |
| Power meters | True RMS Power | ±2% |
| Outdoor air relative humidity / wet-bulb temperature sensors | Outdoor air wet-bulb temperatures | ±3% |
| Outdoor air temperature sensors | Outdoor air dry-bulb temperatures | ±1.0ºF |

Baseline Step 3

Ensure that all required data points are collected. Install submeters or permanent metering, as appropriate, that adheres to accuracy requirements. Metered data should include RMS power (kW) for each chiller, cooling tons for each chiller (chilled water flow, chilled water supply and return temperatures), condenser water supply and return temperatures, and outdoor air dry-bulb and wet-bulb temperatures.

Flow and temperature measurements should be from each chiller to determine actual loads.

Baseline Step 4

Perform baseline data collection during shoulder and peak months (either April – July or August – October). Fifteen-minute trends should be used, with synchronized readings from data loggers and EMCS. (More frequent data logger readings, i.e. 5 minutes, can help.) Data collection should be continuous, and periodic verification of the data is strongly recommended.

Baseline Step 5

Document additional plant information: nameplate data, operating schedules, chiller age and condition, loads served, locations, and peripheral equipment details.

##### Data Analysis

Baseline Step 6

Determine building cooling load profile. Correlate outdoor air temperatures with measured cooling loads using regression analysis. If possible, use outdoor air conditions measured at a nearby government weather station for the same period, as site-measured outdoor air temperatures can be unreliable. Off-site weather data, however, should be verified as applicable to actual site conditions. A good source of weather data is NOAA through http://www.ncdc.noaa.gov/oa/climate/stationlocator.html.

It is typical for cooling load models to have rather poor statistical results ( R2 < 0.75). A non-linear relationship and/or additional variables may be included to define the load profile as needed, such as day of week or occupied status.

Other sources of data (plant shut-down schedules, air-side/water-side economizer use, etc.) should be considered to ensure that chiller plant load profile is accurate.

Baseline Step 7

Determine and document current chiller plant operating parameters and control sequences, including chilled water setpoints, chiller sequencing, condenser water setpoints, and actual temperatures. Actual operations should be verified from trend data, as they can vary from written sequences.

If condenser water setpoints are not maintained, determine cooling tower approach (outdoor air wet-bulb temperature - condenser water return temperature) in order to predict condenser water temperatures from outdoor air wet-bulb temperatures. Confirm operations using trend graph or scatter plot.

Baseline Step 8

Determine which calculation method (Option 1 or Option 2 below) will be used. Initial selection of the appropriate option should be based on the level of variation expected in the operating parameters of the chiller. There are several component-based models that work well with metered chiller data, and two options are presented herein. For systems utilizing fairly constant chilled and condenser water temperatures, a simplified linear model (Option 1) may be appropriate. For systems using more dynamic operating conditions, a temperature-dependent model (Option 2) should be used.

If the results of the selected analysis option do not meet the statistical criteria presented in Table 4-4, Statistical Validations Guidelines and Results, then the other analysis option should be evaluated for viability. The option providing the best statistical results should be used.

Analysis Option 1

For systems using fairly constant chilled and condenser water temperatures, a simplified linear model is appropriate. Measured data should be used to determine the coefficients C1 to C0. The resulting equation can then be applied to the load profile and baseline operating conditions (COP, Load).

1/COP = C1  ( (1/Load) + C0

Where:

COP =Coefficient of performance (COP = 3.516 / kW/Ton)

Load = Cooling load in tons (12,000 Btu)

C1, C0 = Coefficients determined from measured data

This approach offers a simplified regression technique by using the reciprocal values of COP and Load. The coefficients C1 and C0 can be determined from measured data. The final equation can be manipulated and used to predict actual COP, and then kW/ton.

Analysis Option 2

For systems using more dynamic operating conditions, a temperature-dependent model should be used. Measured data should be used to determine the coefficients A0 to A9. The resulting equation can then be applied to the load profile and baseline operating conditions (TCHW, TCW, PLR).

Power = A0 + A1 ( TCHW+ A2 ( TCHW2+ A3 ( TCW + A4 ( TCW2+ A5 ( PLR+ A6 ( PLR2 + A7 ( TCHW ( TCW+ A8 ( TCHW ( PLR + A9 ( TCW ( PLR

Where:

TCHW = Chilled Water Supply Temperature

TCW  = Condenser Water Supply Temperature

PLR = Part-load ratio (rated tons/actual tons)

A0 - A9 = Coefficients determined from measured data

Baseline Step 9

Apply cooling load model to TMY weather data set to create hourly model of baseline chiller energy use, considering all of the chiller plant operating parameters documented in Baseline Step 7. If using Option 2, the model will include additional parameters.

Baseline Step 10

Quantify any reductions in cooling loads from other ECMs planned to ensure that post-installation loads are not overestimated. Adjust hourly TMY cooling loads used to predicted chiller energy use accordingly.

Baseline Step 11

Build performance model(s) of the existing chiller(s). An independent model of each chiller is required. The first step is to clean up the data set to remove transient values. Data points that are within 30 minutes of a chiller’s startup should be discarded. Similarly, all data points after a chiller’s stop should be eliminated prior to performing the analysis for either option below.

Option 1

1/COP = C1 ( (1/Load) + C0

Where:

COP =Coefficient of performance (COP=3.516 / kW/Ton)

Load = Cooling load in tons (12,000 Btu)

C1, C0 = Coefficients determined from measured data

    - Set up a spreadsheet of the metered data for the chiller in question. Depending on instrumentation, individual chiller loads may be calculated from total plant load and chiller sequencing.

    - Calculate COP (COP = 3.516 / kW/Ton) and load on chiller (tons = 500 ( GPM ( (TCHWreturn - TCHWsupply)) for each metered interval

    - Correlate (1/COP) to (1/Load). Use regression analysis to determine C1 and C0.

Option 2

Power = A0 + A1 ( TCHW+ A2 ( TCHW2+ A3 ( TCW + A4 ( TCW2+ A5 ( PLR+ A6 ( PLR2 + A7 ( TCHW ( TCW+ A8 ( TCHW ( PLR + A9 ( TCW ( PLR

Where:

TCHW = Chilled water supply temperature

TCW = Condenser water supply temperature

PLR = Part-load ratio (rated tons/actual tons)

A0 - A9= Coefficients determined from measured data

  - Set up a spreadsheet of the metered data for the chiller in question.

Table 4-2: Example Spreadsheet Layout for Raw Data

  - Paste values from all rows with non-zero energy usage into a new spreadsheet page. Arrange and manipulate data as shown in Table 4-3. Use regression analysis, such as Microsoft Excel’s Regression Function, to determine coefficients A0 to A9 as well as some statistical results. Example results from Excel’s Regression Function are shown in Table 4-5.

Table 4-3: Example Spreadsheet Layout for Data Analysis of One Chiller

| Tons (CH-1) | TCHW | TCHW^2 | TCW | TCW^2 | PLR (CH-1) | PLR^2 | TCHW*TCW | TCHW*PLR | TCW*PLR |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 180.0 | 52 | 2704 | 80 | 6400 | 0.8 | 0.64 | 4160 | 41.6 | 64 |
| 180.0 | 52 | 2704 | 80 | 6400 | 0.8 | 0.64 | 4160 | 41.6 | 64 |
| 180.0 | 52 | 2704 | 75 | 5625 | 0.8 | 0.64 | 3900 | 41.6 | 60 |
| 180.0 | 52 | 2704 | 75 | 5625 | 0.8 | 0.64 | 3900 | 41.6 | 60 |

Baseline Step 12

Verify that the performance models of the chillers are valid by evaluating the statistical results for each model. Compare the metered kWs to those predicted by the model(s) created above and perform statistical analysis on the results.

Table 4-4: Statistical Validations Guidelines and Results

| Parameter evaluated | Suggested acceptable values |
| --- | --- |
| Coefficient of variation (R2) | > 0.75 |
| CV(RSME) | < 15% |
| t-statistic | > 2 |
| Mean bias error | < + 7% |

The four statistical parameters that need to be evaluated for each model are:

- Coefficient of variation (R2) — see results from regression analysis. Lower R2 values may indicates independent variables may be missing.

- t-statistic — See results from regression analysis. The absolute value of the t-stat for each coefficient included should be greater than 2 for the independent variable to be considered significant.

- CV(RSME) — coefficient of variation of the root-mean-squared error. This value is always positive.

- Mean bias error — Overall indicator of bias in regression estimate. Positive values indicate higher than actual values, while negative value indicates that regression under-predicts values.

Most regression analysis tools will include some of the statistical parameters that need to be evaluated, typically R2 and t-statistic. Instructions for calculating Cv(RMSE) and mean bias error are detailed below.

Table 4-5: Example Results from Excel’s Regression Function

Note: The absolute value all of the t-stats are above 2 except for TCHW ( PLR. This is acceptable for this example. Any coefficient that has a t-stat out of acceptable range can be dropped from the model, which may improve the statistical results.

- Calculate Cv(RMSE):

Where:

= Measured energy value at time i

= Predicted energy value at time i

= Mean measured energy value

n = number of data points

p = number of independent variables used

- Calculate Mean Bias Error:

Baseline Step 13

Determine energy use of the baseline and post-installation chillers:

Calculate hourly baseline energy use of the chiller plant: apply the validated chiller performance model(s) to the hourly cooling load model (TMY 8760 data, adjusted in Baseline Step 10 for reductions in cooling loads) considering key operating parameters determined in Baseline Step 7 to predict energy use of each chiller, and the total for all chillers, for each hour of the year.

Using the same 8760 hour model, calculate the post-installation demand for the new chiller(s) from manufacturer’s data, considering the key operating parameters of the new chiller plant.

Baseline Step 14

Calculate proposed energy and demand savings for year 1:

Determine kW savings (predicted baseline kW – predicted post-install chiller energy use) for each hour of the year.

Identify all data that falls within the utility / building’s peak period (defined in the M&V plan) and further delineate data by monthly utility billing periods. For each utility billing period, the “peak” period, typically the highest one hour demand for predicted for the baseline chiller plant that occurs during the utility’s peak period. This assumes the building peak demand is coincident with the chiller plant’s peak demand use.

Apply savings equations:

Monthly Demand Savings (kW) = {(kW baseline) – (kW post)}t-peak

Where:

Time period (t-peak) is defined as the one-hour interval during the building’s peak period (between 1 and 4 PM on weekdays) for that billing month during which the highest baseline demand is set by the chillers. Billing months are defined by the serving electric unity.

(kW baseline) is the demand for the baseline chillers predicted during time t

(kW post) is the demand of the new chillers predicted during the same interval t

Baseline Step 15

Calculate proposed cost savings for year 1:

Annual Cost Savings = Energy Savings (kWh) ( RatekWh + 
			(month(Monthly Demand Savings ( RatekW)

2.	Post-Installation M&V Activities

##### Data Collection

Post-Install Step 1

Data collection should follow Baseline Step 1 through Step 3 including sensor verification and calibration.  Install submeters or permanent metering, as appropriate, that adhere to accuracy requirements. Typically permanent metering equipment will be installed with the new chillers.

Conduct metering immediately following installation and commissioning. Collect data for a minimum of two weeks, longer if possible. If chiller plant is off line or typical operating conditions are not present at time of project completion, post-installation metering may be deferred. In this case, the expected year 1 savings estimates included in the Post-installation Report will be based on the Factory Performance test results reported by the manufacturer.

Ensure that all required data points are collected. If peripheral equipment in the plant has been affected, additional points will be required.

Table 4-6: Post-Installation Data Required for Analysis

Points Needed for Analysis

Chilled water flow (GPM) per chiller

Condenser water supply temperatures (ºF)

Chilled water supply temperatures (ºF)

Chilled water return temperatures (ºF)

True RMS Power (kW) per chiller

Chiller on/off Status

Synchronize readings from data loggers and EMCS to collect trends in 15-minute intervals. (More frequent data, i.e. 5 minute, logger readings can help.) Data collection should be continuous, and periodic verification of the data is strongly recommended.

Post-Install Step 2

Document additional information on post-installation conditions: nameplate data, operating schedules, chiller age and condition, loads served, locations, and peripheral equipment details.

Data Analysis

Post-Install Step 3

Follow Baseline Step 7 to determine post-installation chiller plant operating parameters and controls sequences. Document results including: chilled water setpoints, chiller sequencing, condenser water setpoints and actual temperatures. All operational parameters should be verified with trended field data.

Post-Install Step 4

Follow Baseline Step 11 to build a performance model of each of the new chillers. Typically, the performance calculation option selected in Baseline Step 8 should be used.

Post-Install Step 5

Follow Baseline Step 12 to verify that performance models of the new chillers are statistically valid.

Post-Install Step 6

Apply new chiller performance models developed in Post-Install Step 4 to the hourly TMY cooling loads developed and adjusted during Baseline Step 10. Use the new chiller operating parameters determined in Post-Install Step 3 to predict the hourly post-installation chiller energy use.

Post-Install Step 7

Calculate the expected demand and energy savings for year 1 by following Baseline Step 14.

Post-Install Step 8

Calculate expected cost savings for year 1 by following Baseline Step 15.

Post-Install Step 9

Draft Post-Installation Report in accordance with IDIQ requirements. Include all analysis, metered data, and Factory performance test results on the chiller(s) per the M&V plan.

3.	Annual M&V Activities

Data Collection

Annual Step 1

Collect metered data to develop performance models of each chiller for this performance period. Data collection should follow Baseline Step 1 through Baseline Step 3 including sensor verification and calibration.

Collect data for a minimum of two weeks and up to eight weeks if possible while cooling loads and typical operating conditions are present. Any variations in operating conditions expected over the year should be used during the test period to ensure the models developed will adequately cover those conditions. This may require adjusting normal operating set point to achieve seasonal any variations, such as cooling tower temperatures.

Data Analysis

Annual Step 2

Using the data collected, create a chiller performance model for each chiller by following Baseline Step 11. Typically, the performance calculation option selected in Post-Installation Step 4 should be used.

Verify the validity of the models by following Baseline Step 12. If results from the statistical analyses are acceptable, then the post-installation performance model(s) are still valid. If results are not acceptable, then new models shall be developed using Baseline Step 11 and validated and Baseline Step 12.

Annual Step 3

Using the data collected, verify that key operating parameters documented during the post-installation phase are still valid by following Baseline Step 7. Current operating conditions may be different than in the post-installation case.

Annual Step 4

Using the validated chiller performance models and key operating conditions in the current performance period, develop an hourly energy use model of the chillers

Apply new chiller performance models developed in Annual Step 3 to the hourly TMY cooling loads developed and adjusted during the baseline. Use the new chiller operating parameters determined in Annual Step 3 to predict the hourly post-installation chiller energy use.

Annual Step 5

Calculate the verified demand and energy savings for year 1 by following Baseline Step 14.

Annual Step 6

Calculate verified cost savings for year 1 by following Baseline Step 15.

Annual Step 7

Verify that O&M activities have been properly executed. Gather documentation from the party responsible, and compare to O&M requirements specified in the contract.

Annual Step 8

Develop Annual Report in accordance with IDIQ Requirements and M&V plan details. provide all analysis and metered data in electronic format. Data on O&M activities should be included in Annual Report.

# Footnotes

Based on v1.0  M&V Plan Outline for FEMP Super ESPC projects, available at http://www1.eere.energy.gov/femp/financing/superespcs_mvresources.html

The Super ESPC Energy Savings Contract Risk, Responsibility and Performance Matrix, available at http://www1.eere.energy.gov/femp/financing/superespcs_espcbasicsp2.html

See ASHRAE Guideline 14-2002 for additional information on instrumentation selection.

INSTRUCTIONS: If peripheral equipment will be modified, include description here and expand all other sections to discuss related impacts.

INSTRUCTIONS: If sequences of operation will be modified, discuss specific changes.

INSTRUCTIONS: If possible, use outdoor air conditions (dry-bulb and wet-bulb temperatures) measured at a nearby government weather station for the same period. A good source of weather data includes NOAA through http://www.ncdc.noaa.gov/oa/climate/stationlocator.html. Weather station data should be validated with site data to ensure it is applicable.

Site - New York Central Park; http://rredc.nrel.gov/solar/old_data/nsrdb/tmy2/State.html

Rundquist, et al. Calculating Lighting and HVAC Interactions, ASHRAE Journal 1993.

INSTRUCTIONS: See Engineering Supplement for details on the two chiller performance models recommended.

See ASHRAE Guideline 14-2002 and IPMVP Volume 1 (EVO 10000-1.2007) for additional information on statistical validation techniques.

As the T-statistic for this parameter is low, it could be eliminated to help reduce uncertainty. Since it is only low for one of the chillers, and the validation criteria are met, it has been kept in all of the chiller models.

Energy rates are typically included in the Whole Project Data/Global Assumptions section of the M&V plan. It is included here for clarity.

See ASHRAE Guideline 14-2002 and IPMVP Volume 1 (EVO 10000-1.2007) for additional information on statistical validation techniques and regression analysis.

See ASHRAE Guideline 14-2002 and IPMVP Volume 1 (EVO 10000-1.2007) for additional information on statistical analysis and validation techniques.

This is defined in the project specific M&V  Plan.