## Condition Report - Market
Condition Report - Market
Asset/Def | Asset | WBS | Location | Ranking Priority | Work Type | Deficiency Title | Est Cost | Ref Photo | Year | Projects | Deficiency Description | FMSS WO
Def | Market | B1010 | Storage/Office | 2 Sub-Serious | DM | Install FLOOR TILE | 2879.028 |  | 2008 | Replace Floor Covering | REPLACE WOOD PLANK FLOORING,(SPLIT EDGES/UNEVEN/ROUGH), NATURAL TONGUE AND GROOVE HARDWOOD, OFFICE/STORAGE - 339 SF. | 1151468
Def | Market | B1010 | South Porch | 3 Serious | DM | Perform PAINT PORCH DECK | 1307.484 |  | 2008 | Exterior Repair, Prep & Paint | PREPARE AND PAINT PORCH DECK,(DETERIORATED), SOUTH PORCH. | 1151476
Def | Market | B1020 | South Porch | 3 Serious | DM | Perform PAINT EXTERIOR CANOPY | 649.404 |  | 2008 | Exterior Repair, Prep & Paint | PREPARE/PAINT EXTERIOR CANOPY/PORCH OVERHANG,(DETERIORATED), SOUTH PORCH - 288 SF | 1151474
Def | Market | B2010 | North Elevation | 3 Serious | DM | Replace FASCIA BOARD | 388.824 |  | 2008 | Exterior Repair, Prep & Paint | REPLACE EXTERIOR WOOD FASCIA BOARD. SINGLE STORY,(MOISTURE DAMAGE), 2" X 8", NORTH EXTERIOR TOTAL - 30 LF. | 1151472
Def | Market | B2010 | All Exterior Elevations | 3 Serious | DM | Perform PAINT WOOD CORNICE | 1493.1 |  | 2008 | Exterior Repair, Prep & Paint | PREPARE AND PAINT NON-ORNAMENTAL EXTERIOR WOOD CORNICE,(DETERIORATED), THROUGHOUT EXTERIOR PERIMETER. | 1151473
Def | Market | B2010 | All Exterior Elevations | 2 Sub-Serious | DM | Perform PAINT EXTERIOR WOOD SIDING | 13082.952 |  | 2008 | Exterior Repair, Prep & Paint | PREPARE/PAINT EXTERIOR WOOD SIDING,(DETERIORATED), THROUGHOUT EXTERIOR. | 1151485
Def | Market | B2010 | East Elevation | 3 Serious | DM | Replace SIDING | 3326.94 |  | 2008 | Exterior Repair, Prep & Paint | REPLACE BOARD AND BATTEN SIDING, PAINTED, (MOISTURE DAMAGE), EAST FOUNDATION - 40 SF, NORTH FOUNDATION SKIRT - 120 SF, AND WEST EXTERIOR - 60 SF | 1151486
Def | Market | B2010 | South Elevation | 3 Serious | DM | Replace SIDING | 262.128 |  | 2008 | Exterior Repair, Prep & Paint | REPLACE PAINTED BEVEL OR CLAPBOARD SIDING, MULTIPLE STORY,(DAMAGED), SOUTHWEST GABLE END - 4 SF | 1151487
Def | Market | B2020 | North Elevation | 3 Serious | DM | Replace WINDOW | 1524 |  | 2008 | Door & Window Replacement | REPLACE AWNING WINDOW, INCLUDING SINGLE PANE GLASS, WOOD FRAME, 7 TO 12 SF, NORTH ELEVATION, (DETERIORATED), HOPPER. 42 IN X 24 IN | 1151488
Def | Market | B2030 | East Elevation | 3 Serious | DM | Replace DOOR | 1403.088 |  | 2008 | Door & Window Replacement | REPLACE WOOD EXTERIOR DOOR, FRAME AND HARDWARE,EAST ELEVATION OFFICE,(DETERIORATED),.36 IN X 78 IN | 1151481
Def | Market | B2030 | East Elevation | 3 Serious | DM | Replace DOOR | 1403.088 |  | 2008 | Door & Window Replacement | REPLACE WOOD EXTERIOR DOOR, FRAME AND HARDWARE,EAST ELEVATION APARTMENT,(DETERIORATED),.32 IN X 79 IN | 1151482
Def | Market | B2030 | South Elevation | 3 Serious | DM | Replace DOOR | 3347.736 |  | 2008 | Door & Window Replacement | REPLACE DOUBLE DOOR WITH FRAME, FLUSH WOOD EXTERIOR WITH HARDWARE, UP TO 8' X 8', SOUTH ELEVATION GROCERY,(DETERIORATED),.64 IN X 81 IN | 1151483
Def | Market | C1020 | Restroom | 3 Serious | DM | Perform PAINT INTERIOR | 391.66 |  | 2008 | Restroom Rehab | PREPARE AND PAINT INTERIOR WALLS, CEILING, DOOR AND FRAME, AT RESTROOM. | 1151471
Def | Market | C1030 | Kitchen | 2 Sub-Serious | DM | Replace BASE CABINETS | 568.5 |  | 2008 | Personal Property Replacement | REPLACE BASE CABINETS, HARDWOOD, PREFINISHED,(DETERIORATED), IN KITCHEN TOTAL 4 LF | 1151469
Def | Market | C3010 | Restroom | 1 Minor | DM | Replace MASONITE WAINSCOT | 651.48 |  | 2008 | Restroom Rehab | REPLACE FIBERGLASS REINFORCED PLASTIC PANELS,(DETERIORATED), MASONITE WAINSCOT, RESTROOM - 74 SF. | 1151470
Def | Market | C3010 | Storage/Office | 1 Minor | DM | Perform TAPE/FINISH DRYWALL JOINTS | 2119.8 |  | 2008 | Interior Painting | TAPE/FINISH DRYWALL JOINTS,(DETERIORATED/EXISTING JOINTS ARE ROUGH), OFFICE/STORAGE TOTAL - 663 LF. | 1151467
Def | Market | C3020 | Restroom | 5 Critical | DM | Replace FLOOR TILE | 296.172 |  | 2008 | Replace Floor Covering | REPLACE VINYL ASBESTOS FLOOR TILES WITH 12" X 12" VINYL FLOOR TILES,(DETERIORATED), AT RESTROOM - 21 SF | 1151477
Def | Market | C3020 | Retail Area | 4 Sub-Critical | DM | Replace FLOOR TILE | 7798.2 |  | 2008 | Replace Floor Covering | REPLACE 12" X 12" VINYL FLOOR TILE,(DAMAGED), AT STORE - 1,290 SF | 1151478
Def | Market | C3030 | Storage/Office | 1 Minor | DM | Perform TAPE/FINISH DRYWALL JOINTS | 897.852 |  | 2008 | Interior Painting | TAPE/FINISH DRYWALL JOINTS ON INTERIOR CEILING,(DETERIORATED), ORIGINAL TAPE ONLY, NO EXISTING PAINT, OFFICE STORAGE - 339 SF. | 1151465
Def | Market | C3030 | Storage/Office | 1 Minor | DM | Perform PAINT INTERIOR CEILING | 3159.792 |  | 2008 | Interior Painting | PREPARE AND PAINT INTERIOR CEILING,(MISSING), EXISTING IS RAW DRYWALL, OFFICE/STORAGE - 339 SF, RESTROOM - 20 SF, AND STORE - 1,290 SF. | 1151466
Def | Market | D2010 | Restroom | 3 Serious | DM | Replace WATER CLOSET | 1728.264 |  | 2008 | Restroom Rehab | REPLACE TANK TYPE WATER CLOSET,(BROKEN/CRACKED), RESTROOM. | 1151459
Def | Market | D2010 | Restroom | 2 Sub-Serious | DM | Replace LAVATORY | 1534.332 |  | 2008 | Restroom Rehab | REPLACE WALL MOUNTED LAVATORY WITH FAUCET AND DRAIN, 19'' X 17'',(DETERIORATED), RESTROOM. | 1151461
Def | Market | D2010 | Office | 2 Sub-Serious | DM | Replace KITCHEN SINK | 1218.132 |  | 2008 | Personal Property Replacement | REPLACE KITCHEN SINK, COUNTER TOP MOUNTED, SINGLE BOWL, WITH FAUCETS AND DRAIN,(DETERIORATED), OFFICE. | 1151462
Def | Market | D2020 | Crawl Space | 3 Serious | DM | Replace WATER HEATER | 1868.496 |  | 2008 | Replace Mechnical Components | REPLACE DOMESTIC WATER HEATER, ELECTRIC, UP TO 52 GALLONS,(INOPERATIVE), HOTPOINT, 40 GAL, IN CRAWL SPACE. | 1151463
Def | Market | D2030 | West Exterior Elevation | 3 Serious | DM | Replace CAST IRON PIPE | 3848.352 |  | 2008 | Replace Mechnical Components | REPLACE CAST IRON PIPE SECTION WITH 2 NO-HUB COUPLINGS, UP TO 4",(DETERIORATED), WEST EXTERIOR TOTAL 60 LF | 1151464
Def | Market | D3020 | Crawl Space | 3 Serious | DM | Replace FURNACE | 4712.268 |  | 2008 | Replace Mechnical Components | REPLACE FURNACE, HOT AIR HEATING, GAS/OIL, 95 TO 131 MBH, CRAWL SPACE,(DETERIORATED),. | 1151484
Def | Market | D3030 | Exterior | 3 Serious | DM | Replace EVAPORATIVE COOLER | 5865.084 |  | 2008 | Replace Mechnical Components | REPLACE EVAPORATIVE COOLER 4216 TO 8300 CFM,1-1/2 HP, WEST EXTERIOR, (CORRODED/RUSTED),. | 1151480
Def | Market | D3040 | Restroom | 2 Sub-Serious | DM | Replace EXHAUST FAN | 288.456 |  | 2008 | Restroom Rehab | REPLACE RESIDENTIAL BATHROOM EXHAUST FAN,(WORN), RESTROOM. | 1151460
Def | Market | D5020 | Throughout Building | 2 Sub-Serious | DM | Replace LIGHTING FIXTURES | 43668.444 |  | 2008 | Luminary Replacement | REPLACE LIGHTING FIXTURES IN OFFICE BUILDING,(DETERIORATED), THROUGHOUT BUILDING. TOTAL 2992 SF | 1151457
Def | Market | D5020 | Restroom | 5 Critical | IPH | Replace RECEPTACLE | 295.212 |  | 2008 | Correct IPH | REPLACE EXISTING 3-PRONG GROUNDED RECEPTACLE WITH A GFCI RECEPTACLE,(DETERIORATED), IN OFFICE AND RESTROOM. | 1151454
Def | Market | D5020 | Office | 5 Critical | IPH | Repair RECEPTACLE | 224.736 |  | 2008 | Correct IPH | REPAIR OPEN GROUND ON RECEPTACLE IN OFFICE | 1151455
Def | Market | D5020 | Exits & Office | 5 Critical | IPH | Replace LIGHTING FIXTURE | 2035.296 |  | 2008 | Correct IPH | REPLACE LIGHTING FIXTURE, INTERIOR, EXIT SIGN W/BATTERY BACKUP,(MISSING/REMOVED), IN GROCERY ROOM - 2 EA AND OFFICE | 1151456
Correct Deferred Maintenance
[6 empty] | Replace Floor Covering | 10973.4
[6 empty] | Exterior Repair, Prep & Paint | 20510.832
[6 empty] | Door & Window Replacement | 7677.912
[6 empty] | Restroom Rehab | 4202.532
[6 empty] | Interior Painting | 6177.444
[6 empty] | Personal Property Replacement | 1786.632
[6 empty] | Replace Mechnical Components | 16294.2
[6 empty] | Luminary Replacement | 43668.444
[6 empty] | Total | 111291.396
Correct Immediate Personel Hazards
[6 empty] | Replace Receptacle | 295.212
[6 empty] | Repair Receptacle | 224.736
[6 empty] | Replace Lighting Fixture | 2035.296
[6 empty] | Total | 2555.244

## PM & Cyclic (RM) - Market
Estimated Preventive and Cyclic Maintenance - Market
Asset/Def | Asset | WBS | Location | Work Type | Ref Photo | Year | Component | Project | Description | Annual Cost (Est.)
Asset | Market | B | Shell | PM |  | 2 x per yr | Exterior (All Components) | Inspect, clean & schedule repair as needed. | Inspect for repair. | 30
Asset | Market | B3010 | Roof | PM |  | 2 x per yr | Roof (All Components) | Inspect, clean & schedule repair as needed. | Inspect for repair. | 30
Asset | Market | B301005 | Roof | PM |  | 2 x per yr | Gutter | Inspect, clean & schedule repair as needed. | Clean debris from gutter. | 40
Asset | Market | C | Interior | PM |  | 2 x per yr | Interior (All Components) | Inspect, clean & schedule repair as needed. | Inspect for repair. | 30
Asset | Market | C3020 | Storage/Office | PM |  | 2 x per yr | Floor Covering | Clean & seal floors. | Clean and seal floor covering twice a year or more to sustain protective seal and manufactured finish. | 245
Asset | Market | C3020 | Restroom | PM |  | 2 x per yr | Floor Covering | Clean & seal floors. | Clean and seal floor covering twice a year or more to sustain protective seal and manufactured finish. | 120
Asset | Market | C3020 | Retail Area | PM |  | 2 x per yr | Floor Covering | Clean & seal floors. | Clean and seal floor covering twice a year or more to sustain protective seal and manufactured finish. | 770
Asset | Market | D201001 | Restroom | PM |  | 2 x per yr | Watercloset | Inspect, clean & schedule repair as needed. | Check for leaks and integrity of base caulking. Replace caulking as needed. | 35
Asset | Market | D201003 | Restroom | PM |  | 2 x per yr | Lavatoriy | Inspect, clean & schedule repair as needed. | Check for leaks and integrity of caulking. Replace caulking as needed. | 35
Asset | Market | D201003 | Office | PM |  | 2 x per yr | Kitchen Sink | Inspect, clean & schedule repair as needed. | Check for leaks and integrity of caulking. Replace caulking as needed. | 35
Asset | Market | D202003 | Crawl Space | PM |  | Annually | Water Heater | Inspect, clean & schedule repair as needed. | Check for leaks. Drain and flush annually. | 30
Asset | Market | D302003 | Crawl Space | PM |  | Annually | Furnace | Inspect, clean & schedule repair as needed. | Clean, adjust, inspect, lubricate, perform annual maintenance in accordance with manufacture's recommendations. | 60
Asset | Market | D3030 | Exterior | PM |  | Annually | Evaporative Cooler | Inspect, clean & schedule repair as needed. | Clean, adjust, inspect, lubricate, perform annual maintenance in accordance with manufacture's recommendations. | 145
Asset | Market | D3040 | Restroom | PM |  | Annually | Exhaust Fan | Inspect, clean & schedule repair as needed. | Clean, adjust, inspect, lubricate, perform annual maintenance in accordance with manufacture's recommendations. | 35
Asset | Market | D5020 | Throughout Building | PM |  | 2 x per yr | Luminaries | Inspect, clean & schedule repair as needed. | Clean, adjust, inspect, perform annual maintenance in accordance with manufacture's recommendations. | 135
Asset | Market | G20 | Site Improvements | PM |  | 2 x per yr | Paved Surfaces | Inspect, clean & schedule repair as needed. | Inspect for repair. Seal cracks. | 30
Asset | Market | B101004 | South Elevation | RM |  | 2014 | Front porch, columns and railings. | Exterior painting. | Prepare and paint as authorized. | 660
Asset | Market | B102004 | South Elevation | RM |  | 2014 | Front Porch ceiling. | Exterior painting. | Prepare and paint as authorized. | 225
Asset | Market | B2010 | All Exterior Elevations | RM |  | 2014 | All exterior walls and components. | Exterior painting. | Prepare and paint as authorized. | 3200
Asset | Market | B2020 | All Exterior Elevations | RM |  | 2014 | Windows | Exterior painting. | Prepare and paint as authorized. | 1200
Asset | Market | B2030 | All Exterior Elevations | RM |  | 2014 | Doors | Exterior painting. | Prepare and paint as authorized. | 735
Asset | Market | C1010 | Restroom | RM |  | 2014 | Interior Walls | Interior painting. | Prepare and paint as authorized. | 285
Asset | Market | C1010 | Storage/Office | RM |  | 2014 | Interior Walls | Interior painting. | Prepare and paint as authorized. | 575
Asset | Market | C1010 | Retail Area | RM |  | 2014 | Interior Walls | Interior painting. | Prepare and paint as authorized. | 1850
Asset | Market | C1020 | Restroom | RM |  | 2014 | Interior Door | Interior painting. | Prepare and paint as authorized. | 140
Asset | Market | G2020 | Parking Lot | RM |  | 2015 | Paved Surfaces | Pavement crack seal. | Seal cracks and asphalt surface. Repaint and stripe. | 3685
Summary of Preventive Maintenance (PM)
[9 empty] | Inspect, clean & schedule repair as needed. | 670
[9 empty] | Clean & seal floors. | 1135
[9 empty] | Estimated Total Annual PM | 1805
Summary of Cyclic Maintenance (RM)
[9 empty] | Exterior painting. (Year 2014) | 6020
[9 empty] | Interior painting. (Year 2014) | 2850
[9 empty] | Pavement crack seal. (Year 2015) | 3685
[9 empty] | Estimated Total Cyclic Maintenance (RM) | 12555