# Emergency Management Program

DATE:     SAMPLE

OPERATING UNIT:		Operating Rooms						  OPERATING UNIT MANAGER:

| Mission Critical System | Potential Problems | Contact for Assistance in Preparing for Potential Problems | Preparations to Make to Minimize Potential Problems | If there is an interruption in operations due to loss of the Critical System, then: Assess the situation for: Action required: |
| --- | --- | --- | --- | --- |
| 1. Lighting (Emergency Lights Available) | Staff unable to see in rooms. Unable to carry out duties. | Facility Engineering and Safety Office | Stock flashlights and batteries. Review evacuation procedures. Secure doorstops for enclosed rooms (held by CNM). | Determine extent of outage (unit or widespread) Determine ability of staff to continue operations Assess patient condition for evacuation | Report extent to command center with assessment Begin shutdown of procedures in progress Evacuate patients on command center instructions |
| 2. Electrical Power (Generator Power Available) | Electrical and electronic equipment is unavailable (after battery backup fails). | Facility Engineering and Safety Office | See #1. Lighting Review evacuation and emergency interruption procedures. | Determine extent of outage (unit or widespread) Determine ability of staff to continue operations Assess patient condition for evacuation | Report extent to command center with assessment Begin shutdown of procedures in progress Evacuate patients on command center instructions |
| 3. Steam Distribution | Sterilized tray and instrument availability. | Facility Engineering and SPD. | Obtain disposable instruments and suture trays. Insure all trays sterilized an available in advance | Assess needs for sterile supplies and laundry Ability to perform emergent cases with existing stock levels | Discuss stock and supply with appropriate service/section; report problems to ACOS Surgery for resolution and command center |
| 4. Heating, Ventilation & Air Conditioning (HVAC) | Inability to control temperature, humidity, and air exchanges; patient comfort and safety. | Facility Engineering and Safety Office | Obtain extra blankets Discuss portable heaters Discuss portable fans Review evacuation procedures | Determine extent of outage (unit or widespread) Determine ability of staff to continue operations Assess patient condition for evacuation | Report extent to command center with assessment Begin shutdown of procedures in progress Evacuate patients on command center instructions |
| 5. Room or Hood Exhaust | Increased staff risk due to waste gases, smoke plumes. Increased infection risk. | Facility Engineering, Safety Office, Infection Control. | Obtain portable fans Plan for possible use of portable suction devices to remove gases, etc. | Assess actual need for exhaust systems Prepare to terminate cases or use alternate exhaust | Report failure to command center with assessment Begin shutdown of procedures in progress if needed |
| 6. Water Delivery | Unable to provide water for patients needs, staff infection control. | Facility Engineering and Material Management | Provide for bottled water for patients and sanitary needs Stock waterless soaps | Assess patient needs and extent of problem | Report failure to command center with assessment Establish bottled water center(s) with control |
| 7. Water Conditioning Or Drinkability | Unable to use water for drinking or patient needs. Cannot scrub for cases. | Facility Engineering and Materiel Management | Obtain signs saying "Water Unsafe to Drink" for sinks, etc. Provide locations for bottled water for scrub sinks. | Assess patient needs and extent of problem | Report failure to command center with assessment Establish bottled water center(s) with control |
| 8. Waste Stream (Sanitary, Solid, Liquid, & Biohazard) | Cannot remove infectious and other waste; increased infection risk and pest hazard. Drains and toilets back-up. | Environmental Management and Facility Engineering | Minimize sanitary system usage Obtain extra biohazard boxes Obtain extra needle boxes Plan to minimize water use Plan for abbreviated scrubs | Assess extent of problem on unit for immediate problems Continuous assessment for waste and similar items | Report failure to command center with assessment for immediate problems Keep EMS informed of waste status; report problems to Chief, Patient Care Services |
| 9. Critical Supplies | Unable to supply patient needs including wound care and pharmacy items. | SPD, Pharmacy, and Warehouse | Obtain 1 month extra supply of necessary stock supplies; discussion stock with SPD Locate alternate suppliers | Continuing assessment of situation | Discuss stock and supply with appropriate service/section; report problems to ACOS, Surgery for resolution |
| 10. Communi- cations (Telephone, Radio, Intercom, Nurse Call; etc.) | Unable to call for emergency assistance or supplies. Unable to contact physicians or staff. Unable to contact clinical lab/blood bank | Business Practices and Telecommunications | Insure backup (2-way radio) is available. Orient staff to act as "runners" Lay in additional stock supplies Discuss communication and delivery protocols with PALMS | Assess extent of problem, check emergency phones Insure emergency lines are manned Check staffing and report | Report failure to command center with assessment Runners to be dispatched as needed with available communications (if available) Contact PALMS directly |
| 11. VISTA & Other Computer Applications | Cannot order tests or receive results. Medical records and images unavailable. Appointments and staffing schedules inaccessible. | IRMS, Information Security Officer | Orient staff to act as "runners" Check function of light boxes Print out patient records Manual backup of schedules Plan for portable radiology Test backup film printing sys. | Assess extent of problem on unit Continuous assessment of records system and actual needs of the unit | Report failure to command center; obtain patient records if not on unit Institute runner system Utilize manual schedules |
| 12. Alarms (Fire, Code Blue, Security, Medical Gases, Nurse Call, Refrigeration; etc.) | Inability to call or hear fire alarm. Unable to call Code Blue. Cannot tell when medical gas supply is compromised. | Facility Engineering, Safety Office, Materiel Management, Biomedical Engineering, Anesthesia | Insure backup (2-way radio) is available. Orient and review fire watch procedures Set up frequent walk-thrus for alarm conditions Orient staff to act as "runners" | Assess situation for each system; insure alarms are checked for accuracy on alarm Assess backup levels of available gases in cylinders | Report status to command center with assessment Institute fire watch, alarm watch, and frequent patient rounds with communications backup (if needed and available) |
| 13. Elevators & Other Vertical Transport | Unable to receive supplies, or medications by cart. Unable to transport patients on or off floor. | Facility Engineering, Safety Office, SPD, and Pharmacy | Plan for possible emergency stairwell usage (litters, etc) Coordinate patient housing in PACU, SICU, and A4N Establish runner/courier system | Assess patient needs for possible vertical evacuation. Determine patient needs for food, pharmacy, linens, and other supplies | Report patient status to command center Institute runner systems Institute emergency supply procedures |
| 14. Transport Systems (Robotic, Pneumatic Tube, Tracked Vehicle; etc.) | Minimal direct problems (administrative only). | Materiel Management (Mail Room) and Pharmacy | Orient staff to act as "runners" Plan for manual pickup and delivery of mail and similar items | Assess needs for mail and pharmacy items | Institute runner system for pharmacy items; administrative mail secondary |
| 15. Central Medical Gases (Oxygen) | Unable to continue surgery. | Anesthesia, Engineering, Materiel Mgmt. | Provide location for backup oxygen cylinders. Discuss stock level with anesthesia Insure extra supplies available | Verify extent of failure; check alarm panel Assess actual patient needs Assess backup levels of available gases in cylinders | Contact anesthesia (with runners if needed); establish small-cylinder therapy Contact command center with situation and assessment |
| 16. Medical Air | Compressed air operated devices unavailable. | SPD, Facility Engineering, Materiel Mgmt. and Anesthesia | Discuss air pump needs with SPD and provide location for storage. Insure proper fittings available | Verify extent of failure; check alarm panel Assess actual patient needs Assess backup levels of available gases in cylinders | Contact SPD (with runners if needed) for air pumps Contact command center with situation and assessment |
| 17. Central Vacuum | Unable to continue suctioning/draining of patients and suction-operated devices inoperable. | SPD, Facility Engineering, Materiel Mgmt, and Anesthesia | Discuss portable suction pump needs and availability with SPD Insure large-bore and large volume syringes (with tubing) are stocked | Verify extent of failure; check alarm panel Assess actual patient needs Assess backup levels of available gases in cylinders | Contact SPD (with runners if needed) for suction pumps Contact command center with situation and assessment |
| 18. Central Nitrous Oxide | Unable to continue surgery. | Anesthesia, Engineering, Materiel Mgmt. | Provide location for backup nitrous oxide cylinders. Discuss stock level with anesthesia Insure extra supplies available | Verify extent of failure; check alarm panel Assess actual patient needs Assess backup levels of available gases in cylinders | Contact anesthesia (with runners if needed); establish small-cylinder therapy Contact command center with situation and assessment |
| 19. I.V. Pumps or Blood Warmers | Cannot automatically infuse medication or provide properly warmed blood. | Biomedical Engineering and SPD | Obtain manual I.V. and blood administration sets and provide inservices Nursing competency training | Assess situation and type of pumps affected | Institute appropriate manual interventions Contact SPD and Biomedical Engineering for support |
| 20. Monitoring System Failure | Unable to make, display, or print out vital signs. Alarms will not function. | Biomedical Engineering and SPD | Insure manual B.P. units, thermometers, etc. and supplies are available; provide inservices Insure forms are available | Assess situation and type of pumps affected Use defibrillator monitor for ECG if warranted | Institute appropriate manual interventions Contact SPD and Biomedical Engineering for support |
| 21. Defibrillators | Inability to defibrillate or cardiovert life-threatening heart conditions | Biomedical Engineering and SPD | Identify alternate brands and locations; provide inservices Provide ACLS refresher training | Check defibrillator for proper operation on test mode; report any problems to Biomedical Engineering immediately | Continue appropriate CPR Contact SPD for delivery of alternate defibrillator Contact Biomed for support |
| 22. Electrosurgery Unit Failure | Cannot utilize electrocautery | Biomedical Engineering and SPD | Plan to revert to manual techniques; refresher training Stock O.R.s with additional supplies Locate alternate brands | Test for proper operation on cut and coag settings prior to beginning cases | Utilize manual techniques for surgery Delay cases if possible Notify Biomed for support or alternate equipment |
| 23. Anesthesia Machine Failure | Unable to perform or continue to perform surgery | Biomedical Engineering and Anesthesia; Detroit Medical Center | Review emergency surgery plans with Anesthesiology Locate alternate brands Discuss alternate surgery locations with DMC | Insure that machine is properly connected and that tanks, vaporizers, etc. are full Ability to continue the case | Begin shutdown of case Transfer to manual ventilation and medication for continuity of anesthesia level Contact Biomed for support |
| 24. Laser Failure (Intraoperative) | Unable to continue laser procedure. | Biomedical Engineering | Continue procedures with manual techniques; refresher training Alternate brand if available | Insure equipment is properly connected and enabled (keys, codes, etc.) Ability to perform case using manual techniques | Cases in progress change to manual techniques or begin shutdown of procedure Postpone elective cases Contact Biomed for support |
| 25. |  |  |  |  |  |
| 26. |  |  |  |  |  |
| 27. |  |  |  |  |  |
| 28. |  |  |  |  |  |