## Data >15HP
VSD Measurement Criteria Data Measurement and Cost Results >15HP
Building Information* | [5 empty] | Pre-ECP Measured/Nameplate |  |  |  |  | Post-ECP Predicted Performance |  |  | Post-ECP Acceptance | [16 empty] | Pre-ECP Financial Baseline |  |  | Post-ECP Predicted Financial |  |  |  |  | Year 1 - Post-ECP Yearly Reconciliation | [10 empty] | Year 2 - Post-ECP Yearly Reconciliation
[14 empty] | Measured / Inspected | [24 empty] | Measured | [6 empty] | Verified |  |  |  | Measured |  |  |  |  | Verified
Bld ID | Rm Name / # | Loc | Building Description | Building Schedule | Yearly Op Hrs | Size (hp) | Speed (rpm) | Load (%) | Eff (%) | Demand (kW) | Eff (%) | Ave Speed (RPMs) | Demand (kW) | Full-Speed Demand (kW) | Ave-Speed Demand (kW) | Motor Type | VFD Functional | VFD Tied Into EMCS | SetPoint Control Pressure Feedback | Accuracy (+/- %) | Measured Control Pressure Feedback | Accuracy (+/- %) | Accuracy Achieved (Pass/Fail) | 0% Motor Speed | 25% Motor Speed | 50% Motor Speed | 75% Motor Speed | 100% Motor Speed | Date | By | Elect Use (kWh) | Dmd (kW) | Cost** $ | Elect Use (kWh) | Dmd (kW) | Cost** $ | Savings $ | Guarantee $ | Measured | Elect Use (kWh) | Dmd (kW) | Cost** $ | Savings $ | Amount Over Guarantee ($) | Deduction From Payment ($) | VFD Functional | Deficiencies Corrected | Date | By | Elect Use (kWh) | Dmd (kW) | Cost $ | Savings $ | Amount Over Guarantee ($) | Deduction From Payment ($) | VFD Used and Functional | Deficiencies Corrected | Date | By
1202_PX | PX | CW-1 |  | 2 | 5040 | 50 | 1771.2649 | 79.386 | 83 | 35.4367 | 86 | 1180.8432 | 11.3746 | 35.9988 | 11.3859 | IR | Yes | Yes | 30 psi |  | 31 psi | [7 empty] | 2003-03-20 | JAC | 178601.1923 | 35.4367 | 13718.2725 | 57327.8072 | 11.3746 | 4403.3216 | 9314.951 | 8849.2034 | M | 59047.6414 | 11.7158 | 4535.4212 | 9035.5024 | 186.299 | 0 | YES | YES | 2004-03-21 | CKM
1202_PX | PX | ChW-1 |  | 2 | 5040 | 50 | 1704.4056 | 77.6641 | 82.1 | 35.0482 | 85.1 | 1136.2704 | 11.3789 | 35.9851 | 11.3903 | IR | Yes | Yes | 45 psi |  | 44 psi | [7 empty] | 2003-03-20 | CKM | 176642.833 | 35.0482 | 13567.8519 | 57349.7296 | 11.3789 | 4405.0054 | 9162.8465 | 8704.7041 | M | 59070.2215 | 11.7203 | 4537.1556 | 8887.9611 | 183.2569 | 0 | YES | YES | 2004-03-21 | JJ
1203_CO | CO A | CW-1 |  | 2 | 5040 | 25 | 1788.7485 | 80.3864 | 85 | 17.5195 | 88 | 1192.499 | 5.6826 | 18.0142 | 5.6883 | IR | Yes | Yes | 30 psi |  | 30 psi | [7 empty] | 2003-03-20 | CKM | 88298.2663 | 17.5195 | 6782.1478 | 28640.3765 | 5.6826 | 2199.8537 | 4582.2941 | 4353.1794 | M | 29499.5878 | 5.8531 | 2265.8493 | 4444.8253 | 91.6459 | 0 | YES | YES | 2004-03-21 | JJ
1203_CO | CO A | ChW-1 |  | 2 | 5040 | 15 | 1720.2761 | 80.4715 | 82 | 10.9078 | 85 | 1146.8508 | 3.4138 | 10.7951 | 3.4172 | IR | Yes | Yes | 45 psi |  | 46 psi | [7 empty] | 2003-03-20 | CKM | 54975.4062 | 10.9078 | 4222.6348 | 17205.6585 | 3.4138 | 1321.5584 | 2901.0763 | 2756.0225 | M | 17721.8283 | 3.5162 | 1361.2052 | 2814.044 | 58.0215 | 0 | YES | YES | 2004-03-21 | JJ
1204_CO | CO B | CW-1 |  | 2 | 5040 | 50 | 1753.1165 | 77.0211 | 82 | 34.8004 | 85 | 1168.7443 | 11.3794 | 35.9835 | 11.3908 | IR | Yes | Yes | 30 psi |  | 30 psi | [7 empty] | 2003-03-21 | WKD | 175393.8596 | 34.8004 | 13471.9188 | 57352.1951 | 11.3794 | 4405.1948 | 9066.724 | 8613.3878 | M | 59072.761 | 11.7208 | 4537.3506 | 8794.7223 | 181.3345 | 0 | YES | YES | 2004-03-21 | CKM
1204_CO | CO B | ChW-1 |  | 2 | 5040 | 25 | 1778.0005 | 79.8821 | 83 | 17.8291 | 86 | 1185.3336 | 5.6873 | 17.9994 | 5.693 | IR | Yes | Yes | 45 psi |  | 45 psi | [7 empty] | 2003-03-21 | WKD | 89858.6536 | 17.8291 | 6902.0004 | 28663.9036 | 5.6873 | 2201.6608 | 4700.3396 | 4465.3226 | M | 29523.8207 | 5.8579 | 2267.7106 | 4559.3294 | 94.0068 | 0 | YES | YES | 2004-03-21 | CKM
1205_CO C_102 | CO C | ChW-1 |  | 2 | 5040 | 25 | 1763.7966 | 77.7505 | 85 | 16.945 | 88 | 1175.8644 | 5.6826 | 18.0142 | 5.6883 | IR | Yes | Yes | 45 psi |  | 44 psi | [7 empty] | 2003-03-21 | JAC | 85402.9447 | 16.945 | 6559.7595 | 28640.3765 | 5.6826 | 2199.8537 | 4359.9058 | 4141.9105 | M | 29499.5878 | 5.8531 | 2265.8493 | 4229.1087 | 87.1981 | 0 | YES | YES | 2004-03-21 | CKM
1206_CO D_101 | CO D | CW-1 |  | 2 | 5040 | 25 | 1767.1168 | 78.4143 | 82 | 17.7149 | 85 | 1178.0778 | 5.6897 | 17.9918 | 5.6954 | IR | Yes | Yes | 30 psi |  | 30 psi | [7 empty] | 2003-03-21 | JAC | 89283.2373 | 17.7149 | 6857.8029 | 28676.0976 | 5.6897 | 2202.5974 | 4655.2055 | 4422.4453 | M | 29536.3805 | 5.8604 | 2268.6753 | 4515.5494 | 93.1041 | 0 | YES | YES | 2004-03-21 | CKM
1206_CO D_102 | CO D | ChW-1 |  | 2 | 5040 | 25 | 1774.8667 | 77.4679 | 84 | 17.0844 | 87 | 1183.2445 | 5.6849 | 18.0069 | 5.6906 | IR | Yes | Yes | 45 psi |  | 45 psi | [7 empty] | 2003-03-21 | CKM | 86105.5869 | 17.0844 | 6613.7291 | 28652 | 5.6849 | 2200.7465 | 4412.9826 | 4192.3335 | M | 29511.56 | 5.8555 | 2266.7689 | 4280.5932 | 88.2597 | 0 | YES | YES | 2004-03-21 | CKM
1207_CO E_101 | CO E | ChW-1 |  | 2 | 5040 | 15 | 1787.3598 | 78.4442 | 85 | 10.2577 | 88 | 1191.5732 | 3.4096 | 10.8085 | 3.413 | IR | Yes | Yes | 45 psi |  | 47 psi | [7 empty] | 2003-03-21 | CKM | 51698.9809 | 10.2577 | 3970.9741 | 17184.2259 | 3.4096 | 1319.9122 | 2651.0619 | 2518.5088 | M | 17699.7527 | 3.5119 | 1359.5096 | 2571.53 | 53.0212 | 0 | YES | YES | 2004-03-21 | KDA
1201_HQ | Mech 105 | AHU-101 |  | 5 | 8760 | 25 | 1782.0341 | 81.6617 | 83 | 18.2263 | 86 | 1188.0227 | 5.6873 | 17.9994 | 5.693 | IR | Yes | Yes | 1.5" |  | 1.5" | [7 empty] | 2003-03-21 | WKD | 159662.3026 | 18.2263 | 10445.8515 | 49820.5944 | 5.6873 | 3259.4953 | 7186.3561 | 6827.0383 | M | 51315.2122 | 5.8579 | 3357.2802 | 6970.7655 | 143.7271 | 0 | YES | YES | 2004-03-21 | KDA
1201_HQ | Mech 105 | AHU-103 |  | 5 | 8760 | 15 | 1777.8872 | 80.1345 | 82 | 10.8621 | 85 | 1185.2581 | 3.4138 | 10.7951 | 3.4172 | IR | Yes | Yes | 1.5" |  | 1.45" | [7 empty] | 2003-03-21 | WKD | 95152.2626 | 10.8621 | 6225.3042 | 29905.0732 | 3.4138 | 1956.5292 | 4268.775 | 4055.3363 | M | 30802.2254 | 3.5162 | 2015.225 | 4140.7118 | 85.3755 | 0 | YES | YES | 2004-03-21 | KDA
1201_HQ | HQ | AHU-104 |  | 5 | 8760 | 15 | 1750.8935 | 81.7406 | 83 | 10.9463 | 86 | 1167.2623 | 3.4124 | 10.7997 | 3.4158 | IR | Yes | Yes | 1.5" |  | 1.5" | [7 empty] | 2003-03-21 | JAC | 95889.9533 | 10.9463 | 6273.5674 | 29892.3566 | 3.4124 | 1955.6972 | 4317.8702 | 4101.9766 | M | 30789.1273 | 3.5147 | 2014.3681 | 4188.3341 | 86.3574 | 0 | YES | YES | 2004-03-21 | KDA
1202_PX | PX | AHU-1 |  | 5 | 8760 | 15 | 1746.1275 | 80.1285 | 85 | 10.478 | 88 | 1164.085 | 3.4096 | 10.8085 | 3.413 | IR | Yes | Yes | 1.5" |  | 1.5" | [7 empty] | 2003-03-21 | JAC | 91787.0945 | 10.478 | 6005.1392 | 29867.8212 | 3.4096 | 1954.092 | 4051.0473 | 3848.4949 | M | 30763.8558 | 3.5119 | 2012.7147 | 3929.5158 | 81.0209 | 0 | YES | YES | 2004-03-21 | JJ
1202_PX | PX | AHU-3 |  | 5 | 8760 | 40 | 1739.2851 | 77.9867 | 83 | 27.8497 | 86 | 1159.5234 | 9.0997 | 28.7991 | 9.1088 | IR | Yes | Yes | 1.5" |  | 1.55" | [7 empty] | 2003-03-21 | CKM | 243963.4571 | 27.8497 | 15961.2256 | 79712.951 | 9.0997 | 5215.1925 | 10746.0331 | 10208.7315 | M | 82104.3395 | 9.3726 | 5371.6483 | 10423.6521 | 214.9207 | 0 | YES | YES | 2004-03-21 | JJ
1202_PX | PX | AHU-4 |  | 5 | 8760 | 30 | 1740.505 | 78.4765 | 84 | 20.7682 | 87 | 1160.3367 | 6.8219 | 21.6083 | 6.8287 | IR | Yes | Yes | 1.5" |  | 1.5" | [7 empty] | 2003-03-21 | CKM | 181929.7472 | 20.7682 | 11902.6914 | 59759.8857 | 6.8219 | 3909.7701 | 7992.9213 | 7593.2753 | M | 61552.6823 | 7.0266 | 4027.0632 | 7753.1337 | 159.8584 | 0 | YES | YES | 2004-03-21 | JJ
1203_CO | CO A | AHU-10 |  | 5 | 8760 | 30 | 1721.1634 | 78.4218 | 82 | 21.26 | 85 | 1147.4422 | 6.8276 | 21.5901 | 6.8345 | IR | Yes | Yes | 1.5" |  | 1.5" | [7 empty] | 2003-03-22 | WKD | 186237.214 | 21.26 | 12184.5059 | 59810.1463 | 6.8276 | 3913.0583 | 8271.4476 | 7857.8752 | M | 61604.4507 | 7.0325 | 4030.4501 | 8023.3042 | 165.429 | 0 | YES | YES | 2004-03-21 | JJ
1203_CO | CO A | AHU-12 |  | 5 | 8760 | 25 | 1766.4944 | 81.4542 | 84 | 17.9636 | 87 | 1177.6629 | 5.6849 | 18.0069 | 5.6906 | IR | Yes | Yes | 1.5" |  | 1.65" | [7 empty] | 2003-03-22 | WKD | 157360.8234 | 17.9636 | 10295.278 | 49799.9048 | 5.6849 | 3258.1417 | 7037.1363 | 6685.2795 | M | 51293.9019 | 5.8555 | 3355.886 | 6826.0222 | 140.7427 | 0 | YES | YES | 2004-03-21 | JJ
1203_CO | CO A | AHU-13 |  | 5 | 8760 | 25 | 1762.3961 | 77.9389 | 85 | 16.9861 | 88 | 1174.9308 | 5.6826 | 18.0142 | 5.6883 | IR | Yes | Yes | 1.5" |  | 1.5" | [7 empty] | 2003-03-22 | WKD | 148798.2647 | 16.9861 | 9735.0755 | 49779.702 | 5.6826 | 3256.82 | 6478.2556 | 6154.3428 | M | 51273.093 | 5.8531 | 3354.5246 | 6283.9079 | 129.5651 | 0 | YES | YES | 2004-03-21 | JJ
1202_PX | PX | CW-1 |  | 2 | 5040 | 25 | 1713.7154 | 79.3413 | 83 | 17.7084 | 86 | 1142.4769 | 5.6873 | 17.9994 | 5.693 | IR | Yes | Yes | 30 psi |  | 29 psi | [7 empty] | 2003-03-20 | JAC | 89250.3913 | 17.7084 | 6855.2801 | 28663.9036 | 5.6873 | 2201.6608 | 4653.6193 | 4420.9383 | M | 29523.8207 | 5.8579 | 2267.7106 | 4514.0107 | 93.0724 | 0 | YES | YES | 2004-03-21 | CKM
1202_PX | PX | ChW-1 |  | 2 | 5040 | 25 | 1719.8728 | 77.2441 | 82.1 | 17.4293 | 85.1 | 1146.5819 | 5.6895 | 17.9925 | 5.6951 | IR | Yes | Yes | 45 psi |  | 45 psi | [7 empty] | 2003-03-20 | CKM | 87843.7366 | 17.4293 | 6747.2356 | 28674.8648 | 5.6895 | 2202.5027 | 4544.7329 | 4317.4962 | M | 29535.1107 | 5.8601 | 2268.5778 | 4408.3909 | 90.8947 | 0 | YES | YES | 2004-03-21 | JJ
1205_CO C_101 | CO C | CW-1 |  | 2 | 5040 | 110 | 1792.3232 | 80.1668 | 83 | 78.7276 | 86 | 1194.8821 | 25.024 | 79.1974 | 25.0491 | IR | Yes | Yes | 30 psi |  | 30 psi | [7 empty] | 2003-03-21 | WKD | 396787.2487 | 78.7276 | 30477.0396 | 126121.1759 | 25.024 | 9687.3075 | 20789.7322 | 19750.2456 | M | 129904.8112 | 25.7748 | 9977.9267 | 20166.0402 | 415.7946 | 0 | YES | YES | 2004-03-21 | CKM
1205_CO C_102 | CO C | ChW-1 |  | 2 | 5040 | 15 | 1727.262 | 78.8759 | 85 | 10.3142 | 88 | 1151.508 | 3.4096 | 10.8085 | 3.413 | IR | Yes | Yes | 45 psi |  | 45 psi | [7 empty] | 2003-03-21 | JAC | 51983.5034 | 10.3142 | 3992.8281 | 17184.2259 | 3.4096 | 1319.9122 | 2672.9159 | 2539.2701 | M | 17699.7527 | 3.5119 | 1359.5096 | 2592.7285 | 53.4583 | 0 | YES | YES | 2004-03-21 | CKM
1206_CO D_101 | CO D | CW-1 |  | 2 | 5040 | 15 | 1761.7048 | 81.5202 | 82 | 11.05 | 85 | 1174.4698 | 3.4138 | 10.7951 | 3.4172 | IR | Yes | Yes | 30 psi |  | 30 psi | [7 empty] | 2003-03-21 | JAC | 55691.8169 | 11.05 | 4277.6619 | 17205.6585 | 3.4138 | 1321.5584 | 2956.1035 | 2808.2983 | M | 17721.8283 | 3.5162 | 1361.2052 | 2867.4204 | 59.1221 | 0 | YES | YES | 2004-03-21 | CKM
1206_CO D_102 | CO D | ChW-1 |  | 2 | 5040 | 110 | 1723.6014 | 80.9396 | 84 | 78.5403 | 87 | 1149.0676 | 25.0137 | 79.2303 | 25.0387 | IR | Yes | Yes | 45 psi |  | 43 psi | [7 empty] | 2003-03-21 | CKM | 395843.2179 | 78.5403 | 30404.5291 | 126068.8 | 25.0137 | 9683.2845 | 20721.2446 | 19685.1823 | M | 129850.864 | 25.7641 | 9973.783 | 20099.6072 | 414.4249 | 0 | YES | YES | 2004-03-21 | CKM
1207_CO E_101 | CO E | ChW-1 |  | 2 | 5040 | 15 | 1710.8052 | 78.8886 | 85 | 10.3158 | 88 | 1140.5368 | 3.4096 | 10.8085 | 3.413 | IR | Yes | Yes | 45 psi |  | 45 psi | [7 empty] | 2003-03-21 | CKM | 51991.8613 | 10.3158 | 3993.4701 | 17184.2259 | 3.4096 | 1319.9122 | 2673.5579 | 2539.88 | M | 17699.7527 | 3.5119 | 1359.5096 | 2593.3512 | 53.4712 | 0 | YES | YES | 2004-03-21 | KDA
1201_HQ | Mech 105 | AHU-101 |  | 5 | 8760 | 25 | 1738.6099 | 81.0663 | 83 | 18.0934 | 86 | 1159.0733 | 5.6873 | 17.9994 | 5.693 | IR | Yes | Yes | 1.5" |  | 1.5" | [7 empty] | 2003-03-21 | WKD | 158498.3207 | 18.0934 | 10369.6984 | 49820.5944 | 5.6873 | 3259.4953 | 7110.203 | 6754.6929 | M | 51315.2122 | 5.8579 | 3357.2802 | 6896.8969 | 142.2041 | 0 | YES | YES | 2004-03-21 | KDA
1201_HQ | Mech 105 | AHU-103 |  | 5 | 8760 | 15 | 1708.9904 | 78.3416 | 82 | 10.6191 | 85 | 1139.3269 | 3.4138 | 10.7951 | 3.4172 | IR | Yes | Yes | 1.5" |  | 1.5" | [7 empty] | 2003-03-21 | WKD | 93023.3618 | 10.6191 | 6086.0216 | 29905.0732 | 3.4138 | 1956.5292 | 4129.4924 | 3923.0178 | M | 30802.2254 | 3.5162 | 2015.225 | 4005.6076 | 82.5898 | 0 | YES | YES | 2004-03-21 | KDA
1202_PX | PX | AHU-1 |  | 5 | 8760 | 15 | 1715.9076 | 78.6848 | 85 | 10.2892 | 88 | 1143.9384 | 3.4096 | 10.8085 | 3.413 | IR | Yes | Yes | 1.5" |  | 1.45" | [7 empty] | 2003-03-21 | JAC | 90133.3483 | 10.2892 | 5896.9434 | 29867.8212 | 3.4096 | 1954.092 | 3942.8515 | 3745.7089 | M | 30763.8558 | 3.5119 | 2012.7147 | 3824.5659 | 78.857 | 0 | YES | YES | 2004-03-21 | JJ
1202_PX | PX | AHU-3 |  | 5 | 8760 | 40 | 1750.0807 | 79.499 | 83 | 28.3898 | 86 | 1166.7204 | 9.0997 | 28.7991 | 9.1088 | IR | Yes | Yes | 1.5" |  | 1.5" | [7 empty] | 2003-03-21 | CKM | 248694.4069 | 28.3898 | 16270.7464 | 79712.951 | 9.0997 | 5215.1925 | 11055.5539 | 10502.7762 | M | 82104.3395 | 9.3726 | 5371.6483 | 10723.8873 | 221.1111 | 0 | YES | YES | 2004-03-21 | JJ
1202_PX | PX | AHU-4 |  | 5 | 8760 | 30 | 1763.2543 | 80.9861 | 84 | 21.4324 | 87 | 1175.5029 | 6.8219 | 21.6083 | 6.8287 | IR | Yes | Yes | 1.5" |  | 1.5" | [7 empty] | 2003-03-21 | CKM | 187747.8481 | 21.4324 | 12283.3387 | 59759.8857 | 6.8219 | 3909.7701 | 8373.5686 | 7954.8902 | M | 61552.6823 | 7.0266 | 4027.0632 | 8122.3615 | 167.4714 | 0 | YES | YES | 2004-03-21 | JJ
1203_CO | CO A | AHU-12 |  | 5 | 8760 | 25 | 1741.371 | 80.9104 | 84 | 17.8436 | 87 | 1160.914 | 5.6849 | 18.0069 | 5.6906 | IR | Yes | Yes | 1.5" |  | 1.5" | [7 empty] | 2003-03-22 | WKD | 156310.2485 | 17.8436 | 10226.5445 | 49799.9048 | 5.6849 | 3258.1417 | 6968.4028 | 6619.9826 | M | 51293.9019 | 5.8555 | 3355.886 | 6759.3507 | 139.3681 | 0 | YES | YES | 2004-03-21 | JJ
Totals (> 15HP) | [5 empty] | 990 | 1748.8512 | 79.4155 | 83.4125 | 699.6373 | 86.4125 | 1165.9008 | 225.1877 | 712.8678 | 225.4129 | [15 empty] | 4500841.3907 | 699.6373 | 319577.0681 | 1448009.8904 | 225.1877 | 102827.8598 | 216749.2083 | 205911.7479 |  | 1491450.1872 | 231.9434 | 105912.6956 | 210246.732 | 4334.9842 | 0
Totals (< 15HP) |  |  |  |  | 6900 | 8.3929 | 1700 | 1120.5544 | 82.9286 | 84.1285 | 1203 | 15866.6667 | 26.732 | 84.5916 | 26.7588 | [15 empty] | 598590.2885 | 84.1285 | 41296.9602 | 189742.386 | 26.732 | 13099.1503 | 28197.8099 | 26787.9194 |  | 189742.386 | 27.534 | 13492.1248 | 28027.7297 | 1239.8103 | 0
Totals | [30 empty] | 5099431.6791 | 783.7659 | 360874.0283 | 1637752.2764 | 251.9197 | 115927.0101 | 244947.0182 | 232699.6672 |  | 1681192.5731 | 259.4773 | 119404.8204 | 238274.4617 | 5574.7945 | 0
* For column definitions go to "DataColumnDef" worksheet.
**Assuming the cost per kWh is $.04 and $10 per kW

## Data <15HP
VSD Measurement Criteria, Data Measurement and Cost Results <15HP
Data < 15 HP
Building Information* | [6 empty] | Pre-ECP Measured/Nameplate |  |  |  |  | Post-ECP Predicted |  |  | Post-ECP Acceptance Measured / Inspected | [6 empty] | Pre-ECP Financial Baseline |  |  | Post-ECP Predicted Financial |  |  |  |  | Year 1 - Post-ECP Yearly Reconciliation | [11 empty] | Year 2 - Post-ECP Yearly Reconciliation
[30 empty] | Measured | [6 empty] | Verified |  |  |  |  | Measured |  |  |  |  | Verified
Bld ID | Rm Name / # | Loc | Building Description | Building Schedule | Control Pressure Feedback | Op Hrs | Size (hp) | Speed (rpms) | Load (%) | Eff (%) | Demand (kW) | Eff (%) | Weighted Ave Speed (RPMs) | Demand (kW) | Full-Speed Demand (kW) | Ave-Speed Demand (kW) | Motor Type | VFD Functional | VFD Tied Into EMCS | Date | By | Elect Use (kWh) | Dmd (kW) | Cost** $ | Elect Use (kWh) | Dmd (kW) | Cost** $ | Savings $ | Guarantee $ | Sampled / Measured | USAF Select | Elect Use (kWh) | Dmd (kW) | Cost** $ | Savings $ | Amount Over Guarantee ($) | Deduction From Payment ($) | VFD Used and Functional | Deficiencies Corrected | Date | By | Elect Use (kWh) | Dmd (kW) | Cost** $ | Savings $ | Amount Over Guarantee ($) | Deduction From Payment ($) | VFD Used and Functional | Deficiencies Corrected | Date | By
1205_CO C_101 | CO C | CW-1 |  | 2 | 30 psi | 5040 | 7.5 | 1700 | 80.2758 | 83 | 5.3751 | 86 | 1133.3333 | 1.7062 | 5.3998 | 1.7079 | IR | YES | Yes | 2003-03-21 | WKD | 27090.4764 | 5.3751 | 2080.8066 | 8599.1711 | 1.7062 | 660.4982 | 1420.3084 | 1349.2929 | S | X | 8599.1711 | 1.7574 | 680.3132 | 1420.3084 | 71.0154 | 0 | YES | YES | 2004-03-21 | CKM
1206_CO D_104 | CO E | CW-1 |  | 2 | 30 psi | 5040 | 7.5 | 1700 | 79.8421 | 83 | 5.3461 | 86 | 1133.3333 | 1.7062 | 5.3998 | 1.7079 | IR | YES | Yes | 2003-03-21 | CKM | 26944.0953 | 5.3461 | 2069.5631 | 8599.1711 | 1.7062 | 660.4982 | 1409.0649 | 1338.6116 | S | X | 8599.1711 | 1.7574 | 680.3132 | 1409.0649 | 70.4532 | 0 | YES | YES | 2004-03-21 | KDA
1201_HQ | Mech 105 | AHU-102 |  | 5 | 1.5" | 8760 | 10 | 1700 | 79.8503 | 82 | 7.2157 | 85 | 1133.3333 | 2.2759 | 7.1967 | 2.2782 | IR | YES | Yes | 2003-03-21 | WKD | 63209.8554 | 7.2157 | 4135.4831 | 19936.7154 | 2.2759 | 1304.3528 | 2831.1304 | 2689.5738 | S | X | 19936.7154 | 2.3442 | 1343.4834 | 2831.1304 | 141.5565 | 0 | YES | YES | 2004-03-21 | KDA
1202_PX | PX | AHU-2 |  | 5 | 1.5" | 8760 | 10 | 1700 | 80.4604 | 83 | 7.1833 | 86 | 1133.3333 | 2.2749 | 7.1998 | 2.2772 | IR | YES | Yes | 2003-03-21 | CKM | 62925.4301 | 7.1833 | 4116.8747 | 19928.2378 | 2.2749 | 1303.7981 | 2813.0766 | 2672.4228 |  |  | 19928.2378 | 2.3432 | 1342.9121 | 2728.6843 | 56.2615 | 0 | YES | YES | 2004-03-21 | JJ
1203_CO | CO A | CW-1 |  | 2 | 30 psi | 5040 | 7.5 | 1700 | 77.2514 | 85 | 5.0509 | 88 | 1133.3333 | 1.7048 | 5.4043 | 1.7065 | IR | YES | Yes | 2003-03-20 | CKM | 25456.4192 | 5.0509 | 1955.2954 | 8592.1129 | 1.7048 | 659.9561 | 1295.3393 | 1230.5724 |  |  | 8592.1129 | 1.7559 | 679.7548 | 1295.3393 | 64.767 | 0 | YES | YES | 2004-03-21 | JJ
1203_CO | CO A | ChW-1 |  | 2 | 45 psi | 5040 | 7.5 | 1700 | 81.8334 | 82 | 5.5462 | 85 | 1133.3333 | 1.7069 | 5.3975 | 1.7086 | IR | YES | Yes | 2003-03-20 | CKM | 27952.9048 | 5.5462 | 2147.0493 | 8602.8293 | 1.7069 | 660.7792 | 1486.2701 | 1411.9566 |  |  | 8602.8293 | 1.7581 | 680.6026 | 1486.2701 | 74.3135 | 0 | YES | YES | 2004-03-21 | JJ
1204_CO | CO B | CW-1 |  | 2 | 30 psi | 5040 | 10 | 1700 | 77.238 | 82 | 6.9797 | 85 | 1133.3333 | 2.2759 | 7.1967 | 2.2782 | IR | YES | Yes | 2003-03-21 | WKD | 35177.5948 | 6.9797 | 2701.9743 | 11470.439 | 2.2759 | 881.039 | 1820.9353 | 1729.8886 |  |  | 11470.439 | 2.3442 | 907.4701 | 1820.9353 | 91.0468 | 0 | YES | YES | 2004-03-21 | CKM
1204_CO | CO B | ChW-1 |  | 2 | 45 psi | 5040 | 5 | 1700 | 80.8582 | 83 | 3.6094 | 86 | 1133.3333 | 1.1375 | 3.5999 | 1.1386 | IR | YES | Yes | 2003-03-21 | WKD | 18191.3317 | 3.6094 | 1397.2675 | 5732.7807 | 1.1375 | 440.3322 | 956.9354 | 909.0886 |  |  | 5732.7807 | 1.1716 | 453.5421 | 956.9354 | 47.8468 | 0 | YES | YES | 2004-03-21 | CKM
1206_CO D_104 | CO E | CW-1 |  | 2 | 30 psi | 5040 | 7.5 | 1700 | 79.0113 | 83 | 5.2904 | 86 | 1133.3333 | 1.7062 | 5.3998 | 1.7079 | IR | YES | Yes | 2003-03-21 | CKM | 26663.7387 | 5.2904 | 2048.0291 | 8599.1711 | 1.7062 | 660.4982 | 1387.5308 | 1318.1543 |  |  | 8599.1711 | 1.7574 | 680.3132 | 1387.5308 | 69.3765 | 0 | YES | YES | 2004-03-21 | KDA
1201_HQ | Mech 105 | AHU-102 |  | 5 | 1.5" | 8760 | 10 | 1700 | 80.8948 | 82 | 7.3101 | 85 | 1133.3333 | 2.2759 | 7.1967 | 2.2782 | IR | YES | Yes | 2003-03-21 | WKD | 64036.6943 | 7.3101 | 4189.5788 | 19936.7154 | 2.2759 | 1304.3528 | 2885.226 | 2740.9647 |  |  | 19936.7154 | 2.3442 | 1343.4834 | 2885.226 | 144.2613 | 0 | YES | YES | 2004-03-21 | KDA
1201_HQ | HQ | AHU-104 |  | 5 | 1.5" | 8760 | 7.5 | 1700 | 78.5903 | 83 | 5.2622 | 86 | 1133.3333 | 1.7062 | 5.3998 | 1.7079 | IR | YES | Yes | 2003-03-21 | JAC | 46097.1825 | 5.2622 | 3015.8924 | 14946.1783 | 1.7062 | 977.8486 | 2038.0438 | 1936.1416 |  |  | 14946.1783 | 1.7574 | 1007.1841 | 2038.0438 | 101.9022 | 0 | YES | YES | 2004-03-21 | KDA
1202_PX | PX | AHU-2 |  | 5 | 1.5" | 8760 | 10 | 1700 | 81.3044 | 83 | 7.2586 | 86 | 1133.3333 | 2.2749 | 7.1998 | 2.2772 | IR | YES | Yes | 2003-03-21 | CKM | 63585.5142 | 7.2586 | 4160.0605 | 19928.2378 | 2.2749 | 1303.7981 | 2856.2624 | 2713.4492 |  |  | 19928.2378 | 2.3432 | 1342.9121 | 2770.5745 | 57.1252 | 0 | YES | YES | 2004-03-21 | JJ
1203_CO | CO A | AHU-10 |  | 5 | 1.5" | 8760 | 10 | 1700 | 81.4159 | 82 | 7.3572 | 85 | 1133.3333 | 2.2759 | 7.1967 | 2.2782 | IR | YES | Yes | 2003-03-22 | WKD | 64449.2331 | 7.3572 | 4216.569 | 19936.7154 | 2.2759 | 1304.3528 | 2912.2162 | 2766.6054 |  |  | 19936.7154 | 2.3442 | 1343.4834 | 2912.2162 | 145.6108 | 0 | YES | YES | 2004-03-21 | JJ
1203_CO | CO A | AHU-13 |  | 5 | 1.5" | 8760 | 7.5 | 1700 | 81.7283 | 85 | 5.3436 | 88 | 1133.3333 | 1.7048 | 5.4043 | 1.7065 | IR | YES | Yes | 2003-03-22 | WKD | 46809.818 | 5.3436 | 3062.5163 | 14933.9106 | 1.7048 | 977.046 | 2085.4703 | 1981.1968 |  |  | 14933.9106 | 1.7559 | 1006.3574 | 2085.4703 | 104.2735 | 0 | YES | YES | 2004-03-21 | JJ
Totals (< 15HP) | [5 empty] | 6900 | 8.3929 | 1700 | 1120.5544 | 82.9286 | 84.1285 | 1203 | 15866.6667 | 26.732 | 84.5916 | 26.7588 |  |  |  | 527814 | 0 | 598590.2885 | 84.1285 | 41296.9602 | 189742.386 | 26.732 | 13099.1503 | 28197.8099 | 26787.9194 | 0 | 0 | 189742.386 | 27.534 | 13492.1248 | 28027.7297 | 1239.8103 | 0
* For column definitions go to "DataColumnDef" worksheet.
**Assuming the cost per kWh is $.04 and $10 per kW

## OperatingScheds
OperatingScheds
Time Schedules
Sched # | Schedule Name | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 1 0 | 1 1 | 1 2 | 1 3 | 1 4 | 1 5 | 1 6 | 1 7 | 1 8 | 1 9 | 2 0 | 2 1 | 2 2 | 2 3 | Total Hours | Max Days | Max Hrs / Yr
| Peak Demand Hours | [24 empty] | 3 | bar: Time Schedules 1 3 to Time Schedules 1 5
1 | Dormitory Schedule | [24 empty] | 9 | 210 | 1890 | bar: Time Schedules 5 to Time Schedules 8; Time Schedules 1 8 to Time Schedules 2 2
2 | Cooling | [24 empty] | 24 | 210 | 5040 | bar: Time Schedules 0 to Time Schedules 2 3
3 | Admin Building | [24 empty] | 12 | 365 | 4380 | bar: Time Schedules 6 to Time Schedules 1 7
4 | Heating | [24 empty] | 24 | 225 | 5400 | bar: Time Schedules 0 to Time Schedules 2 3
5 | AHU Fans | [24 empty] | 24 | 365 | 8760 | bar: Time Schedules 0 to Time Schedules 2 3
6 | Stores | [24 empty] | 15 | 365 | 5475 | bar: Time Schedules 8 to Time Schedules 2 2
7 | Flight Operations | [24 empty] | 24 | 365 | 8760 | bar: Time Schedules 0 to Time Schedules 2 3

## MeasSpecs
Measurement Specifications and Costs
Measurement |  |  |  |  | Instrument Used | [6 empty] | Comments
Date | Purpose | Cost $/Each | Type | By1 | Accuracy | Type | Mfr | Model | Calibration
[9 empty] | Type2 | Date | By3
2003-04-22 | Acceptance Test | $30/motor | Power | WKD | ± 1% | Power Analyzer | XYZ | 380801 | Annual | 2003-01-21 | GGL | Calibrated per manufacturer’s specifications. Does not include travel.
2003-04-22 | Acceptance Test | $30/motor | Power | JAC | ± 1% | Power Analyzer | XYZ | 380801 | Annual | 2003-01-21 | GGL
2003-04-22 | Acceptance Test | $30/motor | Power | CKM | ± 1% | Power Analyzer | XYZ | 380801 | Annual | 2003-01-21 | GGL
Note: | Calibration Standard was included in Phase II Report
1 | Initials of individual taking the measurements
2 | Frequency of calibration was included in Phase II Report and is 1 year
3 | Initials of the individual responsible for calibrating the metering equipment.

## AcceptRept
Acceptance Report
The acceptance M&V check for ECP-04 - Variable Speed Drive Motors was performed on 4/22/03. The "< 15HP" worksheet lists the motors that were inspected and sampled and/or verified during acceptance in columns marked "Post-ECP Acceptance." The "> 15HP" worksheet lists the motors that were tested during acceptance in columns marked "Post-ECP Acceptance." The trend logs have been programmed and checked for proper operation. All items in the "Accept_Checklist" were completed and six deficiencies were found. All deficiencies have been corrected. Measurements taken during acceptance were recorded in the appropriate acceptance columns and the cost of the verifications and measurements was recorded in "MeasSpecs" spreadsheet. The Acceptance Report will contain all tabs (worksheets) in this workbook, updated with current measurements and data.
The following table lists the individuals that performed the acceptance tests:
|  | Name | Title | Specialty
| 1 | William K. Donaldson | Engineer I | Metering/Surveys
| 2 | Jim A. Carlson | Engineer I | Metering/Surveys
| 3 | Carl K. Matheson | Technician | Metering/Surveys
|  | B. K. Wilson - Manager | Date

## AcceptChecklist
Acceptance Checklist
ECP-04 - Variable Speed Drive Motors
Documents | Yes | No
Inspect design docs for complete set | x
Inspect docs for design conditions documentation | x
Complete all required sections of "ECP_04_VSD.xls" | x
All equipment / users manuals in place | x
Vendor Certifications / Tests
Certificate for construction performed to local / OSHA codes and requirements | x
Vendor tests (include results) | x
Overall condition
Specified equipment is installed per manufacturers specifications | x
Verify inverter rated motors installed | x
Adequate air flow to motors | x
Proper paint priming and exterior coatings | x
Access to maintenance and inspection areas at local / OSHA requirements | x
Verify hearing protection accessible if required by codes | x
Color coding and proper labeling on equipment (if required by USAF) | x
Record all nameplate information on each motor | x
Performance
Verify performance tests specification / all parameters specified complete | x
Measure Power of each motor over 15HP | x
Specify all parameters and equipment used in testing - Record in Excel Spreadsheet | x
Inspect all motors under 15HP and record data | x
Controls
Verify starter sequence is correct (w/ mfrs requirements) - Record information | x
Verify trend logs operate correctly - Record information | x
Accepted – USAF Date Certified By – “The ESCO” Date

## AnnualRept
Annual Report Year 1
The annual reconciliation for the ECP-04 - Variable Speed Drive Motors requires that all VSD motors over 15HP and a USAF selected sample set of VSD motors less than 15HP be monitored continuously throughout the year. Inspection will occur at the end of each year to ensure that all systems are functioning as guaranteed. The annual verification and reconciliation calculations can found in the "ECP_04_VSD.xls" worksheet. After the inspection was conducted, all deficiencies were corrected. A summary of the calculated savings along with the savings guarantee is listed in the table below. The savings guarantees are also included in the table below. As a result of meeting the guaranteed savings, full payment with no deductions will be made. The Annual Report will contain all tabs (worksheets) in this workbook, updated with Post-ECP End of Year 1 Measured values.
Savings Summary
| Predicted Savings |  |  | 229341
| Guaranteed Savings |  |  | 217874
| Measured Savings |  |  | 223074
| Amount Over Guarantee |  |  | 5200
| Payment Deductions |  |  | 0
The following table lists the individuals that performed the annual reconciliation and verification inspections:
|  | Name | Title | Specialty
| 1 | Jim Johnson | Engineer I | Metering/Surveys
| 2 | Kim D. Anderson | Engineer I | Metering/Surveys
| 3 | Carl K. Matheson | Technician | Metering/Surveys
Accepted – USAF Date Certified By – “The ESCO” Date

## Tracking
M&V Contract Deliverables Tracking Form for Year 1 thru Year N
ECP-04 - Variable Speed Drive Motor
|  | ESCO Delivery |  | USAF Acceptance
Year | Reports | USAF Signature | USAF Date | USAF Signature | USAF Date
Acceptance
Year 1 | Annual
Year 2 | Annual
Year 3 | Annual
Year 4 | Annual
Year 5 | Annual
Year 6 | Annual
Year 7 | Annual
Year 8 | Annual
Year 9 | Annual
Year 10 | Annual
Year 11 | Annual
Year 12 | Annual
Year 13 | Annual
Year 14 | Annual
Year 15 | Annual
Year 16 | Annual
Year 17 | Annual
Year 18 | Annual
Year 19 | Annual
Year 20 | Annual
Year 21 | Annual
Other Contract Specified Deliverables Required after Year 1 thru 21

## DataColumnDef
Variable Speed Drive Data Column Definitions
Column | Symbol | Definition / Equations
Yearly Op Hrs | YOH | This column contains the total yearly operating hours for the location and is determined by using the operating schedule worksheet demand table.
Load (%) |  | What portion of the motors power is used at the peak demand. Normally this is around 80%. If the average of this column is above 90% then motors must be sampled to verify with an 80% confidence +-20% precision.
Dmd (kW) | Dmd | The Demand of the motor is calculated as follows
(Size (HP))*(.741)*(Load (%)/Eff (%)) = Dmd
Control Pressure Feedback |  | Performance can be measured by verifying that the VFD motor provides adequate flow to maintain a pressure at the control point. The set point presure control feed back is specified by the manufacture or USAF for the application, and is measured in psi.
Elect Use (kWh) | EU | The total electric used for the year in question as a function of the demand and total operating hours.
YOH*Dmd = EU
Cost $ |  | This is the total cost of running the motor for an entire year as a function of a Blended Utility Rate (BUR), the Cost of Electricity (CE), and the calculated demand.
EU * CE + BUR *Dmd * 12 Months = Cost
Savings $ |  | This is the difference between the pre-ECP cost and the most recent calculated cost.
Measured |  | All motors above 15HP are to be measured and will be marked M after the measurements are complete. Motors 15 and bellow will be sampled and those motors that were measured as part of the sample set are to be marked as measured.
Savings Amount Over Guarantee ($) |  | This column contains those savings found that are above the guaranteed savings, which can now be claimed as savings.
Reconciliation ($) |  | This column contains those savings claimed in the guaranteed savings, which were not found and will be deducted from the total savings.