Fuel Storage and Maintenance Facility

Park Headquarters, Puerto Ayora, Santa Cruz Island

Inspection and Recommendations

6-2-2000 Met with Cristobal we walked over to the maintenance yard where he wanted to show me his fuel storage area and to look at the mechanical facilities. The fuel storage and oil facilities are in two bodegas, which have been in use for many years and have had leakage and spillage over the course of time, which has caused soil contamination in the area. The tanks for diesel are of welded flat plate construction and consist of one 4,000 and two 1,000 tanks; the gasoline tank is 300 gallons. They are above ground and tilted to allow for water accumulation and are gravity fed for jug transfer for vehicles and boats. There are no filters in place and a complaint from Cristobal is of bad fuel. There is also poor ventilation in one bodega and the petroleum fumes are thick. The bodegas are also in use for oil storage and for storage of other materials. There are no warning signs posted regarding no smoking or of flammable storage.

Generator Room. The generator is in a good open room, which could stand some cleaning due to sawdust contamination from the carpenter’s shop. The generator is fed from a 1,000-gallon tank, which is almost empty. Due to the present 24-hour electrical service from town the generator is now only in service around 40 hours per month and serves as a backup for when electrical service is disrupted. A small day tank to reduce potential for a large fuel spill and to provide for better fuel with less water should feed the generator.

The mechanical repair facility is cluttered and has a major vehicle overhaul going on which blocks access and service potential for other vehicles. The adjacent bodega has an elevated ramp, which is mostly unusable due to a low ceiling and is instead used primarily for storage. Electrical circuits in the facility are exposed in many cases and unprotected from damage. There is a drum designated for used motor oil for recycling, which should have containment.

Recommendations-

Short Term

- Install warning signs on the fuel storage bodegas regarding “No Smoking” and “Danger Flammable Storage”.

- Install the Racor type fuel filter on the main diesel fuel tank with a mechanical or manual pump feed.

- Install the Racor type fuel filter on the main gasoline fuel tank with a mechanical or manual pump feed. Note- On Monday morning Cristobal was already working on this project.

- Place the waste/recycle oil drum in some form of containment, to prevent a new contamination area, or place the drum near the fuel bodega where the soil is already contaminated.

- Perform house keeping in general throughout the compound and control the spread of new sawdust by having the carpenters clean after project work and practice sawdust control.

- Improve ventilation in the gasoline storage area, perhaps just cleaning the vent above the doors will be sufficient for now as that might improve cross ventilation.

- Install a day tank for the generator with a fuel filter. A 25-30 gallon tank would provide for over 12 hours of run time with a reserve. A side benefit of a smaller tank, which could be kept full, would be a minimal space for air transfer, which will reduce condensation accumulation. This will allow for the removal of the present generator tank that is located in the area proposed for the new fuel facility.

Long Term

1. Construct a new fuel storage facility, which will provide for containment of spillage and a combined site for diesel, gasoline, oil and waste oils. Provide access from the rear of the compound for truck delivery. Roof the structure to prevent excessive temperature change in the tanks and rain water intrusion on the drums and in the containment area while also allowing for good ventilation. Provide new fuel storage tanks Aluminum or coated steel. The decision on material will be based on cost. Aluminum has a greater life with minimal maintenance costs. Steel, even painted properly will require eventual exterior painting and has the potential if the interior coating is broached of introducing rust into the fuel. A properly coated steel tank, with maintenance will last for over 20 years. Provide for filtered, pumped fuel into the maintenance yard with meter. Requested are two 1,000-gallon diesel tanks, two 1,000-gallon gasoline tanks and room for 24 oil drums.

An area along side the generator room is available, 7.6m x 7.1m (54 sq. m) Road access from the recreation area for fuel delivery is convenient with little improvement and side access from the gate near the generator is available.

Construction of a new fuel storage facility would provide many benefits. Environmental contamination would no longer endanger the nearby marine area, storage rooms currently used for petroleum storage would open up for other use, and the safety/fire hazard would be reduced. New fuel tanks will provide cleaner, less contaminated fuel for equipment, which will reduce service cycles and improve reliability.

Basic plans for fuel tank design and specifications and construction notes for the fuel storage facility are attached to this report.

Once the new fuel facility is constructed and the old fuel tanks have been removed from the bodegas the area should be cleaned of fuel contamination. If possible remove up to 12 inches (or more) of the existing contaminated soils. Install a perforated 2-inch pipe below grade, with an exposed air intake in the shade and a black painted, sun exposed riser to above roof level. This will allow for natural convection and exposure of the underground soils to oxygen, which will facilitate decontamination of the soils. Fill the excavated areas with clean dirt/ local material. The removed contaminated soils should be spread evenly in the compound area, or on the adjacent dirt roads. This will expose the soils to oxygen and sun and allow for natural biological cleaning of the soils. This action should be done during the dry season to prevent any leaching by rains.

2. Provide for an improved mechanical repair facility by improving the existing service area and upgrading facilities. This will allow for more efficient repair and service of park equipment, a safer working area for employees, and improved environmental operations.

Overall reorganization of the maintenance compound by separating bodegas into function areas (carpentry, plumbing, storage/warehouse, and marine operations for example) will reduce clutter in the compound center and provide for a more efficient operation. These actions should occur prior to the construction of the fuel facility, which will take some time, but should allow for the planned reutilization of the fuel bodegas once they become avaliable for other uses. Included in this will be the removal of storage items from the ramp bay, which will allow it to better utilized for vehicle service.

The ramp bay should have the roof reconstructed with an increased elevation of perhaps one meter which will allow for vehicles such as the cargo truck to be serviced.

A 3-meter wide, 6-inch thick reinforced concrete apron should be poured in front of the mechanical areas and 4-inch thick in the ramp bay. This apron will provide for better environmental operations by allowing for cleanup of spilled oils and improve mechanical service by reducing dirt contamination of parts and ease of using jacks and other service tools.

Evaluate the electrical requirements of the facility, and if required consider rewiring with protected circuits with the capacity to handle required loads. Having circuits protected in steel conduit in mechanical work areas is important due to the increased likelihood of damage to the wires and of electrical shock hazards to employees.

Kent Bullard

Maintenance Supervisor

Channel Islands National Park

kent_bullard@nps.gov

FUEL TANK SPECIFICATIONS

Construct 4 fuel tanks of 1,000-gallon nominal capacity. The tanks will be of similar design, two for diesel and two for gasoline storage and distribution.

The tanks will cylindrical in shape 1.5 meters in diameter and 2.75 meters long. They are to be installed horizontally on two .3 meter wide support saddles, equal distance from the front and rear ends.

The tanks will be constructed from ¼ inch Aluminum or rolled steel from all new materials. The tank manufacturer may recommend thicker material due to structural requirements in mounting.

The tanks will be of welded construction, and will be provided with the following openings-

On the front bottom, centered 10 cm from the front edge, a ½ inch NPT bung for water drain installation.

On the front of the tank, centered 10 cm from the bottom, a 1 inch NPT bung for fuel discharge installation.

On the top of the tank, centered 10 cm from the front edge, a 2 inch NPT bung for fuel measurement opening installation.

Centered on the top of the tank, a .25 meter in diameter inspection port opening with bolted flange rising 10 cm from the tank with a gasketed cover plate. The flange and cover will be drilled for and provided with 12 each 3/8 inch or metric equal bolts and nuts.

On the top of the tank, to the rear of the inspection opening, centered to the rear edge, a 2 inch NPT bung for installation of a tank vent.

On the top of the tank, centered 10 cm from the rear edge, a 2 inch NPT bung for fuel fill installation.

All threaded bungs will be plugged to prevent contamination during shipment.

Once constructed the tanks will be pressure tested to confirm integrity of all welded seams.

Tank Finish-

The aluminum tanks will be labeled in 15 cm high letters, red in color, on both ends and sides with “Gasoline” or “Diesel”.

The steel tanks will be cleaned to bright metal and painted with an epoxy primer both inside and out. The paint is to be a sprayed application covering all metal surfaces to industry standard thickness. The finish coat both inside and out, is to be a two part marine grade epoxy paint, suitable for fuel contact, white in color and is to be a sprayed application covering all surfaces to industry standard thickness. The tanks will be labeled in 15 cm high letters, red in color, on both ends and sides with “Gasoline” or “Diesel”. The customer is to be provided with one liter of the finish paint for touch up purposes.

The customer is to be provided with four calibrated measuring rods, 1.75 meters in length. Calibrations to be in 50 gallon units.

Fuel Storage Facility Construction Notes

The fuel storage facility is being constructed to provide a central fuel storage area and will also provide containment of any leakage or spills into the environment of Galapagos National Park. Following are specifications regarding construction of the facility.

Site Work- The existing area has a fuel tank for the generator that will be removed and a day tank will be provided for the generator. After tank removal the area should be leveled to a grade a minimum of 8 inches below the grade in the generator room.

Foundation- The parameter and interior walls require a 6 inch concrete foundation, however the back wall may require a deeper foundation wall due to varying site conditions. Under the tank support saddles a 12 inch foundation should be provided which extends .3 meters around the dimensions of the supports. The saddles shall be tied to this foundation with a minimum of #4 or ¼ inch re-bar. This additional support is required as each tank when full will weigh over 4,000 kilos.

Slab-

The slab in the drum storage area shall be 4” thick and reinforced with 6” square mesh as a minimum.

The slab in the tank storage areas shall be 6” thick and reinforced with #4 or ¼” re-bar. This bar will be tied into the bars for the tank support saddles and the stem walls.

After the slab forms are built the interior areas should be filled with fine grade crushed lava to bring the area up and level and to prevent excessive requirements for concrete. The lava shall be compacted to prevent settling.

A 12 inch square by 6 inch deep sump shall be installed in the gasoline and diesel slabs to provide an area for water collection and cleanup.

Prior to pouring the slab concrete,  the compacted lava shall be wetted down with water to prevent excessive water loss from the concrete.

All slab surfaces should be finished as smooth as possible to provide for easier cleanup of any spilled oil or fuel, and a better surface for painting.

Walls- The walls shall be formed and poured, and tied with reinforcing materials to the slab/foundations. The walls will be a minimum of 4 inches thick and .75 meters tall above slab level. The opening into the drum storage area shall have a 6 inch rise, and be ramped to allow for movement of concrete drums. Where the walls will support the roof columns they may be required to be thicker. Prior to pouring the walls a concrete adhesive should be applied to the cold joint at the slab, this is especially critical on the walls forming the fuel containment area.

When pouring the walls the forms should be rodded or vibrated to prevent voids in the concrete.

Roofing- The roof should be constructed in a similar fashion of the adjacent bodegas. A minimum of one meter clearance above the fuel tanks shall be provided. This will allow for worker access on the tanks and for the removal of a tank if required with out having to disassemble the roof structure.

Finish-

The fuel lines from the tanks to the supply shall pass over, not through the walls to maintain integrity of the containment walls

Fuel supply to the generator day tank can be plumbed into the diesel supply lines with a ½ inch line, but it should be valved and is only to be used to fill the day tank. The valve shall be closed except for filling operations to prevent accidental discharge of fuel from the main tanks.

The sides of the fuel shelter may be screened with fence material, but should remain open to allow for adequate ventilation.

Once the slab concrete has been allowed to cure for 14 days, an epoxy type sealant should be applied around the interior of the joint between the slab and containment walls. The interior walls and slab should be painted to seal the concrete, protect the concrete from fuel contact and to provide for easier cleanup of any spillage.

Wooden steps should be provided to allow for worker access into the containment areas.

The electrical supply and pumps for diesel and gasoline shall be rated for use in a fuel environment, and for fuel pumping operations. The fuel discharge lines shall be valved at the end run into the maintenance area.

Signs warning of the danger of fuel storage and no smoking in the area shall be installed.