INTRODUCTION

It is a goal of each laboratory to ensure that safe work practices are established and followed. All laboratory personnel receive formal training in laboratory safety procedures and are familiar with and annually review the safety manual, which specifies practices and techniques designed to minimize hazards. Safety practices and techniques must be supplemented by appropriate facility design and engineering features, safety equipment and management policies.

Some general laboratory safety rules are outlined below. Since the risk of infection from work done in the clinical and diagnostic facilities in the Laboratory of Pathology is from contact-associated exposures, Biosafety Level 2 (BL2) practices, equipment and facilities are most applicable. The essential elements of BL2 practices, some general safety rules required by the College of American Pathologists (CAP), and practices related to chemical hygiene are outlined below.

BL2 is suitable for work involving agents of moderate potential hazard to personnel and environment. In particular, laboratory personnel must have specific training in handling pathogenic agents, access to the laboratory should be limited when work is being conducted, appropriate precautions are taken with contaminated sharp items, and certain procedures in which infectious aerosols or splashes may be created are conducted in biological safety cabinets.

Most work, however, is safely performed on the open counter consistent with BL2 work.

The following policies apply to both agents assigned to BL2 and chemical hazards. These polices must be practiced by all laboratory sections. Additional safety policies may be specified within each laboratory section.

STANDARD PRACTICES

- Food is stored outside the work area in cabinets or refrigerators designated for this purpose only.

- Access to the laboratory is limited when work with infectious agents is in progress.

- Laboratory personnel receive appropriate immunizations or tests for the agents handled (e.g., hepatitis B vaccine or TB skin testing). See Section I for more information regarding services provided by OMS.

- BL2 laboratory sections must have a BL2 sign (NIH 645-5) posted on the door. This sign designates the type of biohazardous agents used, special procedures or precautions for entry, and emergency contact information. Sections operating under Biosafety Level 1 designation do not require any posting. Refer to Biosafety in Microbiological and Biomedical Laboratories (BMBL) published by the Center for Disease Control at http://www.cdc.gov/od/ohs/biosfty/bmbl4/bmbl4toc.htm for specific practices, facilities, and equipment for each Biosafety Level designation. Contact the NIH Division of Safety (496-5291) to determine Biosafety Level designation and to obtain BL2 signs.

- The Clinical Chiefs have established policies and procedures whereby persons are advised of all potential hazards in the laboratory. Laboratory personnel are advised of special hazards and required to follow any special procedures.

- Smoking, eating, drinking, and/or chewing gum is not permitted in the work area.

- Application of cosmetics and/or lip balm is not permitted in the work area.

- Handling contact lenses is not permitted in the work area. Persons who wear contact lenses in laboratories should also wear goggles or a face shield.

- Handle and store brittle plasticware and glassware with care to avoid damage; do not use damaged glassware or plasticware.

- Recapping, purposeful bending, breaking, removing from syringes, or other manual manipulations of needles are strictly prohibited. Resheathing instruments or self-sheathing needles may be used to prevent recapping of needles by hand.

- Mouth pipetting is prohibited.

- Keep work areas clean. Work surfaces are decontaminated daily and after any spill of viable or chemical material.

- Persons wash their hands after handling chemicals, after removing gloves, and before leaving the laboratory.

- Immediately report all splashes, injuries, and spills to the Clinical Chief or designate when they occur. Medical evaluation and surveillance are provided as appropriate and written records are maintained. Employees with occupational injuries or illnesses that require medical treatment (more than first aid) must report to OMS. All accidents, spills, and injuries are reported to the Chair of the Safety Committee for evaluation and presentation to the Quality Improvement committee to avoid recurrence.

- Explicit instructions are posted, and appropriate supplies are available, for the emergency treatment of chemical splashes and injuries and the control of chemical spills wherever major chemical hazards exist in each section.

- For additional information, see web sites for emergency procedures involving:

- Medical Emergencies: http://www.nih.gov/od/ors/ds/medemergency.html

- First aid for Exposure to Blood or Other Potentially Infectious Materials h ttp://www.cc.nih.gov/hes/CC/up_book.html#firstaid

- Hazardous Materials Incidents and Spills: http://www.nih.gov/od/ors/ds/spills.html

- For spills of blood or other potentially infectious materials, see http://www.cc.nih.gov/hes/CC/up_book.html#spills

- Emergency procedures (Fire, Chemical, Biological, Radiological, Bomb Threats, Odor Management): http://www.nih.gov/od/ors/dps/emb/emrgproc.htm

- Telephone Bomb Threats http://www.nih.gov/od/ors/newsltrs/psn/psn34.htm

- Bomb Threat Check List http://www.nih.gov/od/ors/newsltrs/psn/bmblist.htm

- Handling NIH mail http://www.nih.gov/od/ors/security/mailsecurity.htm

- Guidelines for Identifying Suspicious Mail http://www.nih.gov/od/ors/security/idmail.htm

- CDC Anthrax Information http://www.bt.cdc.gov/

SAFETY EQUIPMENT AND PERSONAL PROTECTIVE EQUIPMENT

- Properly maintained biological safety cabinets are used whenever procedures with a potential for creating infectious splashes are done. Hazardous chemicals are used under chemical fume hoods. All hoods and cabinets are certified by the Division of Safety annually.

- All emergency eyewash stations must be located within 100 ft. or 10 seconds travel distance from every area of the laboratory in which hazardous chemicals (irritating, corrosive, or toxic by contact or absorption) are used. The eyewash is tested regularly and documented within each laboratory section.

- Appropriate personal protective equipment (gloves, gowns, masks and eye protectors, etc.) are provided and maintained in a sanitary and reliable condition in all technical work areas in which blood and body substances are handled and in circumstances during which exposure is likely to occur.

- Personnel must use the proper personal protective devices when handling corrosive, flammable, biohazardous, and carcinogenic substances.

- Face protection (goggles, mask, face shield, etc) is used when the possibility of splashes to the face exist.

- Protective lab coats are worn while in the laboratory. The lab coats must be removed when leaving the lab and should be laundered in-house and never taken home by personnel. All protective wear such as disposable gloves, surgical scrubs, aprons, and lab coats must be removed before leaving the technical work area.

- Open-toed shoes, sandals, shorts and other apparel that leave skin exposed are not appropriate when working with hazardous chemicals or infectious agents.

- All personnel are instructed in the proper use and care of disposable gloves and it is documented on the new employee safety orientation checklist.

- Laboratory personnel must use only non‑latex or powder‑free latex gloves when handling specimens.

- Nitrile gloves are recommended for chemicals.

- Heavy gloves are recommended for liquid nitrogen.

- Inspect gloves before use. Use the proper type of gloves (e.g., nitrile for hazardous chemicals).

- Gloves are worn when hands may contact infectious agents or hazardous chemicals.

- Gloves are disposed of as contaminated waste when work with materials is completed, and are not worn outside the laboratory.

- Wash hands after removing gloves and before leaving the work area.

LATEX PROGRAM

Personnel are protected from allergic reaction due to job-related exposure to natural rubber latex gloves and other products. The Safety Committee is responsible for selection of products and implementation of work practices that reduce the risk of allergic reactions. The Safety Committee is responsible for education of employees regarding latex allergies. Important information for healthcare professionals regarding natural rubber latex (NRL) allergy are provided at http://www.cc.nih.gov/hes/latex_healthpro.html. If latex gloves are used, the supervisor should provide reduced protein, powder-free gloves. Employees with latex allergies should report to OMS for medical evaluation. OMS can diagnose an employee with latex allergies and help with prevention and control strategies.

LABORATORY FACILITIES AND PHYSICAL SAFETY

- E ach lab contains a sink for hand washing.

- Vacuum breakers (anti‑siphon devices) must be provided on water outlets if the spigot or an extension extends below sink level, or if the outlet has a suction apparatus attached

- The laboratory is designed so that it can be easily cleaned. Work surfaces should be protected from contamination through the use of disposable, absorbent, plastic backed paper. Replace contaminated paper as necessary and handle as hazardous waste.

- There must be unrestricted access to an eyewash station and emergency shower. Eyewash stations are tested on a regular basis and documented in each laboratory. Emergency showers are tested and documented by maintenance on an annual basis.

- Laboratory airflow (negative pressure relative to corridor) may be checked through maintenance if requested.

- The laboratory is equipped with a zoned automatic fire detection system, an overhead sprinkler system and alarm systems. The fire alarm is audible in all parts of the laboratory, including storage areas, lavatories, and darkrooms. Fire alarm pull stations are located throughout the hallway corridors. ABC fire extinguishers are in the corridors. Corridors and stairwells have adequate emergency lighting for safe evacuation of the laboratory.

- Rooms larger than 1000 ft 2, or in which major fire hazards exist, have at least 2 exit access doors remote from each other, one of which opens directly into a means of egress.

ELECTRICAL AND EQUIPMENT SAFETY

Electrical Equipment Safety

- All instruments and appliances must be grounded, unless they are entirely encased in plastic (such as some cover slippers, stainers, microtomes).

- Instruments and appliances must be checked for adequate grounding and checked for current leakage by CC Biomedical Engineering (496-1311) before initial use, after repair or modification, and when a problem is suspected. At the time of the inspection a label will be affixed to the item to certify the results of the ground check.

- All shocks must be reported immediately including small tingles. Small shocks often precede major shocks and a light tingle may indicate potential trouble. Shut off the current and/or unplug the instrument if shocks occur. Do not attempt to use an instrument that is causing shocks, because it is potentially dangerous and all data gathered from the operation of that instrument may be unreliable.

- Do not work on or attempt to repair any instrument while it is plugged in. An exception is the calibration of instruments that require adjustments while plugged in. In this case, be sure hands are dry, remove all jewelry and proceed with caution. Contact the instrument manufacturer or biomedical engineering if repairs are needed. All repairs will be documented.

- Repairs on the electrical system of the building are prohibited. Any work to be performed on switches, outlets or circuit boxes (fuses, circuit breaker) must be referred to maintenance (ext. 496-1234).

- Extension cords should be avoided. If used, they must be 3-way type and properly grounded. Gauge plugs are prohibited.

- Employees must call 911 to report any electrical arc (constant luminous discharge of electricity) of equipment.

Polarity and Ground Checks

- Maintenance is responsible for checking each circuit supporting fixed electrical receptacles in technical work areas at least annually for polarity and ground integrity. Polarity checks on wall receptacles are necessary because many laboratory instruments cannot be checked for current leakage under conditions of reversed polarity.

- If at any time an outlet becomes faulty or if electric current problems are suspected, contact maintenance (ext. 496-1234) to resolve the problem.

- The safety officer of each section maintains the outlet polarity and ground check documentation in each laboratory. A copy is sent to the Program Assistant for central filing. All documentation must be readily available for inspection purposes and tracking of compliance.

Centrifuges

- Do not operate centrifuges unless the covers are closed. Keep hair, beard, neckties, hair ribbons, hair braids, or other dangling items out of the way.

- Do not centrifuge uncovered tubes containing specimens or flammable liquids. Use caps or parafilm.

- Before centrifuging check the integrity of tubes and tube holders.

- When the centrifuge is in operation, the lid must always be closed. If a noise or vibration begins, stop the centrifuge immediately and check for improper balancing of loads, caps and rotors.

- Tubes used in angle head rotors must never be filled in the point where the liquid is in contact with the lip of the tube when placed in the rotor.

- Avoid decanting, no matter what type of centrifuge tube is used. IF unavoidable, wipe off the outer rim afterwards with a disinfectant; otherwise, the fluid on the outer rim will spin off as an aerosol.

- When centrifuging infectious agents, safety carriers (carriers with individual screw caps) or rotors that are sealed shut should be used.

- Centrifuges should be clean and free of spills. The holders (cups) and centrifuge should be cleaned as needed. The cups should first be disinfected and then washed in warm soapy water and scrubbed with a nylon brush.

Other Equipment

Each laboratory section is responsible for training employees in the proper use of all equipment (e.g., Autoclave, Centrifuge, Cryostat, Electron Microscope, Lasers, Respirators, Ultraviolet Light Sources, etc.).

CHEMICAL HYGIENE PLAN

The responsibilities of the laboratory director (LP Chief), supervisors, clinical laboratory manager, and safety committee are outlined in Section I of this manual. The Environmental Safety Officer of the Clinical Center serves as the qualified chemical hygiene officer for LP and is available to work with the LP Safety Committee. Policies for all operations that involve hazardous chemicals and criteria for the use of personal protective equipment are found throughout the Safety Manual. Specific policies regarding hazardous chemicals are in each laboratory section where appropriate. Exposure monitoring and medical consultation is outlined in Section I. Each laboratory section has separate Chemical Inventory and Material Safety Data Sheets (MSDS), which are accessible to all employees, either in printed or online version. Other references that list the details of hazards and the precautions for safe handling and storage are also accessible to employees in each section. The LP Chemical Hygiene Plan is reviewed annually and updated by the LP Quality Improvement Committee. The NIH Chemical Hygiene Plan is reviewed annually and updated as needed by the Division of Safety and the NIH Occupational Safety and Health Committee. Comments and suggestions on the improvement of the NIH plan should be directed to the Chief, OSHB at 496-2960.

The following web resources are available:

- NIH Hazard Communication Program http://www.nih.gov/od/ors/ds/pubs/hcp/contents.htm

- NIH Chemical Hygiene Plan http://www.nih.gov/od/ors/ds/pubs/chp/index.htm

- OSHA Hazard Communication http://www.osha-slc.gov/SLTC/hazardcommunications/index.html

- OSHA Laboratory Standard (Code of Federal Regulations, Title 29, Part 1910 and all appendices) http://www.osha-slc.gov/OshStd_toc/OSHA_Std_toc_1910.html

- P rocedures for spills and waste disposal are contained at http://www.nih.gov/od/ors/ds/spills.html

- Material Safety Data Sheets http://www.nih.gov/od/ors/ds/msds.html

CHEMICAL SAFETY

- Do not smell or taste chemicals.

- Keep chemicals properly labeled. Do not remove manufacturer’s label. Hazardous caution labels must be placed on all primary and secondary containers based on information from manufacturer label, MSDS, or chemical inventory evaluation. Always include the name of chemical, lot number, date opened (or date prepared or received), and expiration date and initials, as specified by CAP requirements for each specific area. Each section should follow the labeling requirements of the specific CAP checklist designated for their area.

CHEMICAL STORAGE

- OSHA requires the establishment of special “designated areas” in laboratories for the storage of chemical substances of moderate to high chronic toxicity (and including carinogens, teratogens, and embryotoxins). A “designated area” may be a cabinet, desiccator, fume hood, or refrigerator where toxic substances can be stored or used. A sign should be present to alert other laboratory personnel that such substances are present. This also serves to alert housekeeping and maintenance personnel that they should be especially careful when working around these areas.

- Store chemicals according to the manufacturer’s recommendations.

- Do not store chemicals at high levels above arms reach.

- Safety cans are used instead of glass bottles for volumes of flammable solvents larger than one quart (or larger than one pint for solvents that are highly volatile such as ether or pentane) if the purity required does not mandate glass storage.

- S upplies of flammable and combustible liquids should be reasonable for the laboratory's needs, and must be properly stored. Storage areas and/or rooms where volatile solvents are used must be adequately ventilated.

- F lammable or combustible liquids or gas cylinders are positioned well away from open flame or other heat sources, not in corridors and not within exhaust canopies.

- Large drum (bulk) containers are not to be used.

- Bottle carriers are provided for transporting glass containers larger than 500 mL that contain hazardous chemicals. Carriers are not needed for shatter resistant plastic-coated bottles.

- Precautionary labels must be present on the containers of all hazardous chemicals (flammable liquids Classes I, II, and IIIA; corrosives; irritants; asphyxiants; potential carcinogens; etc.), indicating type of hazard and what to do if accidental contact occurs. If the container is too small for such a label, a sign may be posted in the area where the chemical is stored and/or used as appropriate.

- Additional information on general storage compatibility of chemicals and segregation information may be found at http://www.nih.gov/od/ors/ds/pubs/chp/compat.htm

GAS CYLINDERS

- No more than one extra cylinder of compressed, flammable gas (other than those actually connected for use) should be stored at any one workstation.

- All compressed gas cylinders must be secured to prevent accidental falling and damage to the valve or regulator.

- Use proper regulators for each type of gas tank as recommended by the instrument manufacturer.

- Only non-flammable gas cylinders are currently used in LP; if flammable gas cylinders are used in the future, the following polices will apply:

- Flammable gas cylinders must be stored in a separate, ventilated room or enclosure, reserved exclusively for that purpose, and which has a fire‑resistance classification of at least two hours.

- If acetylene or other flammable gas is piped in a manifold compressed gas system, the cylinders must be stored in a separate room and piping system must be properly installed and approved by the Division of Safety.

WASTE DISPOSAL

The NIH has five categories of waste and specific procedures for segregation, labeling & collection. See the NIH guide to waste disposal (waste calendar) at http://www.nih.gov/od/ors/ds/wastecal/guide.htm. The law requires proper disposal of waste. The generator is responsible for ensuring waste is properly segregated and labeled from the point of generation to collection by the contractor.

Additional information regarding waste disposal may be found at http://www1.od.nih.gov/oma/manualchapters/intramural/3032/

Additional information regarding proper management of chemical waste in laboratories is found in the Appendix in a memo format.

ERGONOMICS

Ergonomics is an applied science concerned with designing and arranging objects (e.g., equipment, computers, pipettes, etc) in the workplace to maximize a safe and efficient interaction with them. Ergonomics may reduce the number of injuries in the workplace particularly by reducing the number of repetitive motions. Guidelines on ergonomics are available at:

- http://www.nih.gov/od/ors/ds/ergonomics/index.html

- http://www.niehs.nih.gov/odhsb/ergoguid/home.htm

- http://odp.od.nih.gov/whpp/ergonomics/ergonomics.html

- http://www.cdc.gov/niosh/ephome2.html#second

- http://www.cdc.gov/niosh/ergoweb.html

REFERENCES

- Center for Disease Control: Office of Health and Safety. Microbiological and Biomedical Laboratories (BMBL). http://www.cdc.gov/od/ohs/biosfty/bmbl4/bmbl4toc.htm

- Chief, Waste Management Section, EPB, DS, ORS and Chief, Safety Operations Section, OSHB, DS, ORS. Memo: Proper Management of Chemical Waste in Laboratories. July 23, 2001.

- College of American Pathologists. Laboratory General Checklist. June 21, 2001.

NIH Clinical Center. Annual Review of the Environment of Care Program: Medical Equipment Management Plan http://www.cc.nih.gov/ccc/safety/ec2000/equip2000.html

- NIEHS Health and Safety Manual. Chapter 4 - General Safety and Laboratory Policies/ Centrifuge Safety. http://www.niehs.nih.gov/odhsb/manual/man4a.htm

- OSHA National News Release USDL: 01-170. June 7, 2001. Labor Secretary Announces Deadline on Ergonomics Plans Forums with Guiding Principles. Available: http://www.osha.gov/media/oshnews/june01/national-20010607.htm

STANDARD PRACTICES

# Food is stored outside the work area in cabinets or refrigerators designated for this purpose only.

# Access to the laboratory is limited when work with infectious agents is in progress.

# Laboratory personnel receive appropriate immunizations or tests for the agents handled (e.g., hepatitis B vaccine or TB skin testing). See Section I for more information regarding services provided by OMS.

# BL2 laboratory sections must have a BL2 sign (NIH 645-5) posted on the door. This sign designates the type of biohazardous agents used, special procedures or precautions for entry, and emergency contact information. Sections operating under Biosafety Level 1 designation do not require any posting. Refer to Biosafety in Microbiological and Biomedical Laboratories (BMBL) published by the Center for Disease Control at http://www.cdc.gov/od/ohs/biosfty/bmbl4/bmbl4toc.htm for specific practices, facilities, and equipment for each Biosafety Level designation. Contact the NIH Division of Safety (496-5291) to determine Biosafety Level designation and to obtain BL2 signs.

# The Clinical Chiefs have established policies and procedures whereby persons are advised of all potential hazards in the laboratory. Laboratory personnel are advised of special hazards and required to follow any special procedures.

# Smoking, eating, drinking, and/or chewing gum is not permitted in the work area.

# Application of cosmetics and/or lip balm is not permitted in the work area.

# Handling contact lenses is not permitted in the work area. Persons who wear contact lenses in laboratories should also wear goggles or a face shield.

# Handle and store brittle plasticware and glassware with care to avoid damage; do not use damaged glassware or plasticware.

# Recapping, purposeful bending, breaking, removing from syringes, or other manual manipulations of needles are strictly prohibited. Resheathing instruments or self-sheathing needles may be used to prevent recapping of needles by hand.

# Mouth pipetting is prohibited.

# Keep work areas clean. Work surfaces are decontaminated daily and after any spill of viable or chemical material.

# Persons wash their hands after handling chemicals, after removing gloves, and before leaving the laboratory.

# Immediately report all splashes, injuries, and spills to the Clinical Chief or designate when they occur. Medical evaluation and surveillance are provided as appropriate and written records are maintained. Employees with occupational injuries or illnesses that require medical treatment (more than first aid) must report to OMS. All accidents, spills, and injuries are reported to the Chair of the Safety Committee for evaluation and presentation to the Quality Improvement committee to avoid recurrence.

# Explicit instructions are posted, and appropriate supplies are available, for the emergency treatment of chemical splashes and injuries and the control of chemical spills wherever major chemical hazards exist in each section.

# For additional information, see web sites for emergency procedures involving:

- Medical Emergencies: http://www.nih.gov/od/ors/ds/medemergency.html

- First aid for Exposure to Blood or Other Potentially Infectious Materials h ttp://www.cc.nih.gov/hes/CC/up_book.html#firstaid

- Hazardous Materials Incidents and Spills: http://www.nih.gov/od/ors/ds/spills.html

- For spills of blood or other potentially infectious materials, see http://www.cc.nih.gov/hes/CC/up_book.html#spills

- Emergency procedures (Fire, Chemical, Biological, Radiological, Bomb Threats, Odor Management): http://www.nih.gov/od/ors/dps/emb/emrgproc.htm

- Telephone Bomb Threats http://www.nih.gov/od/ors/newsltrs/psn/psn34.htm

- Bomb Threat Check List http://www.nih.gov/od/ors/newsltrs/psn/bmblist.htm

- Handling NIH mail http://www.nih.gov/od/ors/security/mailsecurity.htm

- Guidelines for Identifying Suspicious Mail http://www.nih.gov/od/ors/security/idmail.htm

- Public Health Emergency Preparedness and Response information http://www.bt.cdc.gov/

SAFETY EQUIPMENT AND PERSONAL PROTECTIVE EQUIPMENT

- Properly maintained biological safety cabinets are used whenever procedures with a potential for creating infectious splashes are done. Hazardous chemicals are used under chemical fume hoods. All hoods and cabinets are certified by the Division of Safety annually.

- All emergency eyewash stations must be located within 100 ft. or 10 seconds travel distance from every area of the laboratory in which hazardous chemicals (irritating, corrosive, or toxic by contact or absorption) are used. The eyewash is tested regularly and documented within each laboratory section.

- Appropriate personal protective equipment (gloves, gowns, masks and eye protectors, etc.) are provided and maintained in a sanitary and reliable condition in all technical work areas in which blood and body substances are handled and in circumstances during which exposure is likely to occur.

- Personnel must use the proper personal protective devices when handling corrosive, flammable, biohazardous, and carcinogenic substances.

- Face protection (goggles, mask, face shield, etc) is used when the possibility of splashes to the face exist.

- Protective lab coats are worn while in the laboratory. The lab coats must be removed when leaving the lab and should be laundered in-house and never taken home by personnel. All protective wear such as disposable gloves, surgical scrubs, aprons, and lab coats must be removed before leaving the technical work area.

- Open-toed shoes, sandals, shorts and other apparel that leave skin exposed are not appropriate when working with hazardous chemicals or infectious agents.

- All personnel are instructed in the proper use and care of disposable gloves and it is documented on the new employee safety orientation checklist.

- Laboratory personnel must use only non‑latex or powder‑free latex gloves when handling specimens.

- Nitrile gloves are recommended for chemicals.

- Heavy gloves are recommended for liquid nitrogen.

- Inspect gloves before use. Use the proper type of gloves (e.g., nitrile for hazardous chemicals).

- Gloves are worn when hands may contact infectious agents or hazardous chemicals.

- Gloves are disposed of as contaminated waste when work with materials is completed, and are not worn outside the laboratory.

- Wash hands after removing gloves and before leaving the work area.

LATEX PROGRAM

Personnel are protected from allergic reaction due to job-related exposure to natural rubber latex gloves and other products. The Safety Committee may assist with selection of products and implementation of work practices that reduce the risk of allergic reactions and help educate employees regarding latex allergies. Important information for healthcare professionals regarding natural rubber latex (NRL) allergy are provided at http://www.cc.nih.gov/hes/latex_healthpro.html. If latex gloves are used, the supervisor should provide reduced protein, powder-free gloves. Employees with latex allergies should report to OMS for medical evaluation. OMS can diagnose an employee with latex allergies and help with prevention and control strategies.

LABORATORY FACILITIES AND PHYSICAL SAFETY

- Each lab contains a sink for hand washing.

- Vacuum breakers (anti-siphon devices) must be provided on water outlets if the spigot or an extension extends below sink level, or if the outlet has a suction apparatus attached

- The laboratory is designed so that it can be easily cleaned. Work surfaces should be protected from contamination through the use of disposable, absorbent, plastic backed paper. Replace contaminated paper as necessary and handle as hazardous waste.

- There must be unrestricted access to an eyewash station and emergency shower. Eyewash stations are tested on a regular basis and documented in each laboratory. Emergency showers are tested and documented by maintenance on an annual basis. A list of emergency showers is located in Appendix H.

- Laboratory airflow (negative pressure relative to corridor) may be checked through maintenance if requested.

- The laboratory is equipped with a zoned automatic fire detection system, an overhead sprinkler system and alarm systems. The fire alarm is audible in all parts of the laboratory, including storage areas, lavatories, and darkrooms. Fire alarm pull stations are located throughout the hallway corridors. ABC fire extinguishers are in the corridors. Corridors and stairwells have adequate emergency lighting for safe evacuation of the laboratory.

- Rooms larger than 1000 ft 2, or in which major fire hazards exist, have at least 2 exit access doors remote from each other, one of which opens directly into a means of egress.

ELECTRICAL AND EQUIPMENT SAFETY

- All instruments and appliances must be grounded, unless they are entirely encased in plastic (such as some cover slippers, stainers, microtomes).

- Instruments and appliances must be checked for adequate grounding and checked for current leakage by CC Biomedical Engineering (496-1311) before initial use, after repair or modification, and when a problem is suspected. At the time of the inspection a label will be affixed to the item to certify the results of the ground check.

- All shocks must be reported immediately including small tingles. Small shocks often precede major shocks and a light tingle may indicate potential trouble. Shut off the current and/or unplug the instrument if shocks occur. Do not attempt to use an instrument that is causing shocks, because it is potentially dangerous and all data gathered from the operation of that instrument may be unreliable.

- Do not work on or attempt to repair any instrument while it is plugged in. An exception is the calibration of instruments that require adjustments while plugged in. In this case, be sure hands are dry, remove all jewelry and proceed with caution. Contact the instrument manufacturer or biomedical engineering if repairs are needed. All repairs will be documented.

- Repairs on the electrical system of the building are prohibited. Any work to be performed on switches, outlets or circuit boxes (fuses, circuit breaker) must be referred to maintenance (ext. 496-1234).

- Extension cords should be avoided. If used, they must be 3-way type and properly grounded. Gauge plugs are prohibited.

- Employees must call 911 to report any electrical arc (constant luminous discharge of electricity) of equipment.

Polarity and Ground Checks

- Maintenance is responsible for checking each circuit supporting fixed electrical receptacles in technical work areas at least annually for polarity and ground integrity. Polarity checks on wall receptacles are necessary because many laboratory instruments cannot be checked for current leakage under conditions of reversed polarity.

- If at any time an outlet becomes faulty or if electric current problems are suspected, contact maintenance (ext. 496-1234) to resolve the problem.

- The safety officer of each section maintains the outlet polarity and ground check documentation in each laboratory. A copy is sent to the Program Assistant for central filing. All documentation must be readily available for inspection purposes and tracking of compliance.

CENTRIFUGES

- Do not operate centrifuges unless the covers are closed. Keep hair, beard, neckties, hair ribbons, hair braids, or other dangling items out of the way.

- Do not centrifuge uncovered tubes containing specimens or flammable liquids. Use caps or parafilm.

- Before centrifuging check the integrity of tubes and tube holders.

- When the centrifuge is in operation, the lid must always be closed. If a noise or vibration begins, stop the centrifuge immediately and check for improper balancing of loads, caps and rotors.

- Tubes used in angle head rotors must never be filled in the point where the liquid is in contact with the lip of the tube when placed in the rotor.

- Avoid decanting, no matter what type of centrifuge tube is used. IF unavoidable, wipe off the outer rim afterwards with a disinfectant; otherwise, the fluid on the outer rim will spin off as an aerosol.

- When centrifuging infectious agents, safety carriers (carriers with individual screw caps) or rotors that are sealed shut should be used.

- Centrifuges should be clean and free of spills. The holders (cups) and centrifuge should be cleaned as needed. The cups should first be disinfected and then washed in warm soapy water and scrubbed with a nylon brush.

OTHER EQUIPMENT

Each laboratory section is responsible for training employees in the proper use of all equipment (e.g., Autoclave, Centrifuge, Cryostat, Electron Microscope, Lasers, Respirators, Ultraviolet Light Sources, etc.).

CHEMICAL HYGIENE PLAN

The responsibilities of the laboratory director (LP Chief), supervisors, clinical laboratory manager, and safety committee are outlined in Section I of this manual. The Environmental Safety Officer of the Clinical Center serves as the qualified chemical hygiene officer for LP and is available to work with the LP Safety Committee. Policies for all operations that involve hazardous chemicals and criteria for the use of personal protective equipment are found throughout the Safety Manual. Specific policies regarding hazardous chemicals are in each laboratory section where appropriate. Exposure monitoring and medical consultation is outlined in the Section titled "Roles, Responsibilities, and Requirements," located here. Each laboratory section has separate Chemical Inventory and Material Safety Data Sheets (MSDS), which are accessible to all employees, either in printed or online version. Other references that list the details of hazards and the precautions for safe handling and storage are also accessible to employees in each section. The LP Chemical Hygiene Plan is reviewed annually and updated by the LP Quality Improvement Committee. The NIH Chemical Hygiene Plan is reviewed annually and updated as needed by the Division of Safety and the NIH Occupational Safety and Health Committee. Comments and suggestions on the improvement of the NIH plan should be directed to the Chief, OSHB at 496-2960.

The following web resources are available:

- NIH Hazard Communication Program http://www.nih.gov/od/ors/ds/pubs/hcp/contents.htm

- NIH Chemical Hygiene Plan http://www.nih.gov/od/ors/ds/pubs/chp/index.htm

- OSHA Hazard Communication http://www.osha-slc.gov/SLTC/hazardcommunications/index.html

- OSHA Laboratory Standard (Code of Federal Regulations, Title 29, Part 1910 and all appendices) http://www.osha-slc.gov/OshStd_toc/OSHA_Std_toc_1910.html

- P rocedures for spills and waste disposal are contained at http://www.nih.gov/od/ors/ds/spills.html

- Material Safety Data Sheets http://www.nih.gov/od/ors/ds/msds.html

CHEMICAL SAFETY

- Do not smell or taste chemicals.

- Keep chemicals properly labeled. Do not remove manufacturer’s label. Hazardous caution labels must be placed on all primary and secondary containers based on information from manufacturer label, MSDS, or chemical inventory evaluation. Always include the name of chemical, lot number, date opened (or date prepared or received), and expiration date and initials, as specified by CAP requirements for each specific area. Each section should follow the labeling requirements of the specific CAP checklist designated for their area.

- The LP has an overall goal of eliminating mercury and using non-mercury substitute when possible.  More information about the NIH has a mercury abatement program may be reviewed at http://orf.od.nih.gov/nomercuryhome.htm

- Each lab should post the Chemical Inventory and Accidental Notice contained in Appendix J

LIQUID NITROGEN SAFETY

Purpose

The purpose of this procedure is to insure that adequate policies, procedures, and practices in place for the safe handling of liquid nitrogen in Hematopathology, Ultrastructural Pathology, and Flow Cytometry.

Policy & Personal Protective Equipment

- Use of the following personal protective equipment is mandatory when decanting or entering an open container of liquid nitrogen:

  - Loose fitting, insulated gloves made to withstand cryogenic liquids. The gloves should be loose enough so they can be thrown off easily and rapidly.

  - Shield all or your skin with long sleeve shirts and trousers. Pant legs should go over the top of footwear so spills cannot get into footwear and cause extreme tissue damage before removal. Rubber aprons, overalls without pockets or cuffs, and hightop shoes are preferred.

  - Always wear chemical splash goggles AND face shield to guard against splashes and possible vessel rupture causing flying debris.

- The storage and use of all containers of liquid nitrogen must be only in well-ventilated areas. If working in an oxygen-deficient atmosphere, wear an oxygen-supplying respirator. When working in closed area, use an oxygen alarm to alert anyone in the room of oxygen-deficient atmosphere before dangerous levels are reached.

- Store liquid nitrogen tanks in upright position in cool, dry, well-ventilated area away from emergency exits or heavy traffic areas. Do not store liquid nitrogen tanks in areas of refuge. If cylinders are involved in a fire, safely relocate or keep cool with water spray. Do not store in areas greater than 125°F (51°C).

- Do not drag, slide or roll storage cylinders. Use suitable hand truck to move vessels and always secure in upright position during movement and transport.

- The Material Safety Data Sheet for liquid nitrogen is available in each lab using the material.

Special Safety Precautions

- Extreme temperatures of liquid nitrogen cause most solids to become brittle.

- Contact to eyes or skin can cause serious frostbite injuries or tissue damage resembling burns.

- Contact with a cryogenically cooled material is dangerous; do not touch cryogenically cooled material with bare flesh.

- To minimize chances of freezing material to skin, remove watches and jewelry from the hands and wrists before using liquid nitrogen.

- When liquid nitrogen warms to a gaseous state it displaces oxygen. Oxygen-deficient atmospheres can cause dizziness, nausea, vomiting, unconsciousness, confusion, and death. Unconsciousness could occur without any preceding signs of danger.

- Never plug or cover a cryogenic container, otherwise explosions or ruptures may occur.

- Use only containers designed specifically for cryogenic liquids such as Dewar flasks and cryogenic storage tanks. Fill slowly to protect from excessive stress that can damage the container. Do not fill containers past 80% capacity.

- Nitrogen is an asphyxiant. Rapid expansion of liquid nitrogen to gas is colorless, odorless, and tasteless and can lead to asphyxiation. Always work in well ventilated areas. Just one liter of gas can expand to 24.6 cubic feet, which is an expansion ratio of 1:696. Liquid nitrogen can rapidly fill small spaces causing very dangerous situations.

- The Division of Fire Safety and Prevention may be contacted at (301) 496-0487 to evaluate work space requirements for ventilation of oxygen alarms.

First Aid

Signs and symptoms of exposure:

- Nausea

- Drowsiness

- Blue coloration of skin and lips

- Unconsciousness

- Death

Remove an incapacitated worker from further exposure and implement appropriate emergency procedures and/or first aid. Immediately contact OMS (301-496-4411) for medical assistance or call code blue (111) if overcome by loss of oxygen.

The following procedures are recommended:

- EYE CONTACT: Remove victim from source of contamination. Open eyelids, allowing liquid to evaporate. See medical attention.

- SKIN CONTACT: Exposed tissues should be restored to normal body temperature by running warm water (100-108°F or 37-42°C) over the affected part. DO NOT USE AN OPEN FLAME FOR THIS PURPOSE. Water should never be more than 112°F (44°C) and the affected part should not be rubbed at any time -this can cause further damage to the area. The victim should get emergency care as quickly as possible to minimize further damage and for damage assessment.

- INHALATION: If a person is overcome by loss of oxygen while working with cryogenic liquids, that person should be moved to a well-ventilated area immediately. A self contained breathing apparatus (SCBA) may be required for rescue so the rescuer does not also fall victim. Artificial respiration should be applied if breathing has stopped. If the person is having difficulty breathing, oxygen should be supplied. Emergency medical help should be summoned.

References

- College of American Pathologists. General Checklist and Commentary. July 2003.

- Lab Safety Supply. How to Work Safely with Cryogenics. EZ Facts Safety Info-Document #290, What is Cryogenics?

- National Institute of Environmental Health Sciences. Health and Safety Manual, Chapter 4, General Safety and Laboratory Policies, Section C: Cryogenic Liquids

- OSHA Technical Links, Nitrogen

- Written communications regarding first aid and OMS procedures. James Schmitt, M.D., M.S., Medical Director, Occupational Medical Service. February 2004.

CHEMICAL STORAGE

- OSHA requires the establishment of special “designated areas” in laboratories for the storage of chemical substances of moderate to high chronic toxicity (and including carinogens, teratogens, and embryotoxins). A “designated area” may be a cabinet, desiccator, fume hood, or refrigerator where toxic substances can be stored or used. A sign should be present to alert other laboratory personnel that such substances are present. This also serves to alert housekeeping and maintenance personnel that they should be especially careful when working around these areas.

- Store chemicals according to the manufacturer’s recommendations.

- Do not store chemicals at high levels above arms reach.

- Safety cans are used instead of glass bottles for volumes of flammable solvents larger than one quart (or larger than one pint for solvents that are highly volatile such as ether or pentane) if the purity required does not mandate glass storage.

- S upplies of flammable and combustible liquids should be reasonable for the laboratory's needs, and must be properly stored. Storage areas and/or rooms where volatile solvents are used must be adequately ventilated.

- F lammable or combustible liquids or gas cylinders are positioned well away from open flame or other heat sources, not in corridors and not within exhaust canopies.

- Large drum (bulk) containers are not to be used.

- Bottle carriers are provided for transporting glass containers larger than 500 mL that contain hazardous chemicals. Carriers are not needed for shatter resistant plastic-coated bottles.

- Precautionary labels must be present on the containers of all hazardous chemicals (flammable liquids Classes I, II, and IIIA; corrosives; irritants; asphyxiants; potential carcinogens; etc.), indicating type of hazard and what to do if accidental contact occurs. If the container is too small for such a label, a sign may be posted in the area where the chemical is stored and/or used as appropriate.

- Additional information on general storage compatibility of chemicals and segregation information may be found at http://www.nih.gov/od/ors/ds/pubs/chp/compat.htm

GAS CYLINDERS

- No more than one extra cylinder of compressed, flammable gas (other than those actually connected for use) should be stored at any one workstation.

- All compressed gas cylinders must be secured to prevent accidental falling and damage to the valve or regulator.

- Only non-flammable gas cylinders are currently used in LP; if flammable gas cylinders are used in the future, the flammable gas cylinders must be stored in a separate, ventilated room or enclosure, reserved exclusively for that purpose, and which has a fire-resistance classification of at least two hours.

WASTE DISPOSAL

The NIH has five categories of waste and specific procedures for segregation, labeling & collection. See the NIH guide to waste disposal (waste calendar) at http://www.nih.gov/od/ors/ds/wastecal/guide.htm. The law requires proper disposal of waste. The generator is responsible for ensuring waste is properly segregated and labeled from the point of generation to collection by the contractor.

Additional information regarding waste disposal may be found at http://www1.od.nih.gov/oma/manualchapters/intramural/3032/

Additional information regarding proper management of chemical waste in laboratories is found in the Appendix in a memo format.

ERGONOMICS

Ergonomics is an applied science concerned with designing and arranging objects (e.g., equipment, computers, pipettes, etc) in the workplace to fully accommodate the worker and maximize a safe and efficient interaction with them. Ergonomics may reduce the number of injuries in the workplace particularly by promoting proper posture, reducing excessive reaching, force, and the number of repetitive motions promoting education of body mechanics. Guidelines on ergonomics are available at::

- http://www.nih.gov/od/ors/ds/ergonomics/index.html

- http://www.niehs.nih.gov/odhsb/ergoguid/home.htm

- http://odp.od.nih.gov/whpp/ergonomics/ergonomics.html

- http://www.cdc.gov/niosh/ephome2.html#second

- http://www.cdc.gov/niosh/ergopage.html

To prevent musculoskeletal disorders (MSDs) in the workplace, NIH has a program to evaluate your work area and suggest improvements for prevention and work control. To receive an ergonomic work assessment, please contact the Occupational Safety and Health Branch at 496-3457.

REFERENCES

- Center for Disease Control: Office of Health and Safety. Microbiological and Biomedical Laboratories (BMBL). http://www.cdc.gov/od/ohs/biosfty/bmbl4/bmbl4toc.htm

- Chief, Waste Management Section, EPB, DS, ORS and Chief, Safety Operations Section, OSHB, DS, ORS. Memo: Proper Management of Chemical Waste in Laboratories. July 23, 2001.

- College of American Pathologists. Laboratory General Checklist. June 21, 2001.

- NIH Clinical Center. Annual Review of the Environment of Care Program: Medical Equipment Management Plan http://www.cc.nih.gov/ccc/safety/ec2000/equip2000.html

- NIEHS Health and Safety Manual. Chapter 4 - General Safety and Laboratory Policies/ Centrifuge Safety. http://www.niehs.nih.gov/odhsb/manual/man4a.htm

- OSHA National News Release USDL: 01-170. June 7, 2001. Labor Secretary Announces Deadline on Ergonomics Plans Forums with Guiding Principles. Available: http://www.osha.gov/media/oshnews/june01/national-20010607.html