## 25F nomo
Custer 230kV PCB A-1250
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 052R1
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3168.7713
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3220.69 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 3226.2 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3246.08 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 3344.59 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 3226.2 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2967.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3309.48 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 2398.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3324.55 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 767.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3344.59 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 3246.08 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3022.87 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3324.55 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2989.15 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2989.15 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2967.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2410.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2479.82 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 880.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2410.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3220.69 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 2398.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 3309.48 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 994.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3022.87 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 880.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2479.82 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 767.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 994.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Custer 230kV PCB A-1250
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 052R1
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2495.37
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3164.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 3136.35 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3169.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 3267.53 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 3136.35 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2767.72 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3238.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 2142.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3253.83 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 118.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3267.53 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 3169.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2814.83 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3253.83 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2791.8 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2791.8 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2767.72 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2208.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2249.15 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 204.57 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2208.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3164.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 2142.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 3238.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 295.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2814.83 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 204.57 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2249.15 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 118.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 295.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Custer 230kV PCB A-1250
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 052R1
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2257.7973
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3084.34 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 3110.17 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 3091.3 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2920.31 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3110.17 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2619.85 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2901.65 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 1228.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2915.26 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -1164.45 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2920.31 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3091.3 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2693.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2915.26 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2654.63 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2654.63 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2619.85 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1328.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1468.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -1040.84 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1328.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3084.34 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1228.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2901.65 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -978.09 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2693.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | -1040.84 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1468.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -1164.45 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -978.09 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Custer 230kV PCB A-1250
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 052R1
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2783.9653
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2616.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2651.55 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2645.62 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2721.94 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2651.55 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2506.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2677.22 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 1675.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2736.28 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -540.26 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2721.94 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2645.62 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2629.49 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2736.28 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2609.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2609.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2506.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1772.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1874.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -490.75 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1772.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2616.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1675.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2677.22 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -407.96 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2629.49 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | -490.75 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1874.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -540.26 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -407.96 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Custer 230kV PCB A-1250
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 052R1
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3137.484
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2487.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2531.29 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2523.74 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2600.53 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2531.29 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2456.13 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2582.19 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 1778.52 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2601.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -397.61 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2600.53 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2523.74 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2568.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2601.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2550.23 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2550.23 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2456.13 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1877.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1945.4 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | -339.49 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1877.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2487.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1778.52 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2582.19 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -267.32 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2568.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | -339.49 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1945.4 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | -397.61 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -267.32 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Custer 230kV PCB A-1250
G0 | 3220.69 | 3164.91 | 3084.34 | 2616.37 | 2487.42
G1 | 3246.08 | 3169.24 | 3091.3 | 2645.62 | 2523.74 | Season/Year: | WINTER 2009
G2 | 3226.2 | 3136.35 | 3110.17 | 2651.55 | 2531.29 | Direction: | South-to-North (SN)
G3 | 3309.48 | 3238.66 | 2901.65 | 2677.22 | 2582.19 | Case Loads: | Light Loads
G4 | 3324.55 | 3253.83 | 2915.26 | 2736.28 | 2601.86 | Outage: | 052R1
G5 | 3344.59 | 3267.53 | 2920.31 | 2721.94 | 2600.53 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3022.87 | 2814.83 | 2693.32 | 2629.49 | 2568.91 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2989.15 | 2791.8 | 2654.63 | 2609.66 | 2550.23 | Study Person: | JGO7470
G8 | 2967.86 | 2767.72 | 2619.85 | 2506.06 | 2456.13 | Source: | 052R1WINTER09v5SNL(COV-CRES BYP)
G9 | 2479.82 | 2249.15 | 1468.77 | 1874.77 | 1945.4
G10 | 2410.2 | 2208.33 | 1328.13 | 1772.99 | 1877.41
G11 | 2398.64 | 2142.87 | 1228.24 | 1675.03 | 1778.52
G12 | 994.1 | 295.29 | -978.09 | -407.96 | -267.32
G13 | 880.99 | 204.57 | -1040.84 | -490.75 | -339.49
G14 | 767.97 | 118.35 | -1164.45 | -540.26 | -397.61
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Light Loads |  |  | 052R1 | Custer 230kV PCB A-1250
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3168.7713 | 3220.69 | 3246.08 | 3226.2 | 3309.48 | 3324.55 | 3344.59 | 3022.87 | 2989.15 | 2967.86 | 2479.82 | 2410.2 | 2398.64 | 994.1 | 880.99 | 767.97
35F | 2495.37 | 3164.91 | 3169.24 | 3136.35 | 3238.66 | 3253.83 | 3267.53 | 2814.83 | 2791.8 | 2767.72 | 2249.15 | 2208.33 | 2142.87 | 295.29 | 204.57 | 118.35
45F | 2257.7973 | 3084.34 | 3091.3 | 3110.17 | 2901.65 | 2915.26 | 2920.31 | 2693.32 | 2654.63 | 2619.85 | 1468.77 | 1328.13 | 1228.24 | -978.09 | -1040.84 | -1164.45
60F | 2783.9653 | 2616.37 | 2645.62 | 2651.55 | 2677.22 | 2736.28 | 2721.94 | 2629.49 | 2609.66 | 2506.06 | 1874.77 | 1772.99 | 1675.03 | -407.96 | -490.75 | -540.26
70F | 3137.484 | 2487.42 | 2523.74 | 2531.29 | 2582.19 | 2601.86 | 2600.53 | 2568.91 | 2550.23 | 2456.13 | 1945.4 | 1877.41 | 1778.52 | -267.32 | -339.49 | -397.61

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3220.57 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2704.86 | -2704.68 | 3245.43 | 3220.69 | -2088.88 | CTG_FAIL_IN_FULL
G1 | 3246.1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2717.37 | -2717.26 | 3174.51 | 3246.08 | -2083.11 | CTG_FAIL_IN_FULL
G2 | 3227.21 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.29 | 530.64 | 530.79 | 3184.32 | 3226.2 | -2049.13 | FULL
G3 | 3308.84 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2720.49 | -2721.09 | 3240.99 | 3309.48 | -2081.94 | CTG_FAIL_IN_FULL
G4 | 3323.21 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2720.51 | -2720.9 | 3171.1 | 3324.55 | -2067.13 | CTG_FAIL_IN_FULL
G5 | 3343.2 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2724.27 | -2724.68 | 3183.85 | 3344.59 | -2054.68 | CTG_FAIL_IN_FULL
G6 | 3023.18 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -803.38 | -803.93 | 3220.9 | 3022.87 | -1806.73 | FULL
G7 | 2990.3 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -813.69 | -813.1 | 3149.7 | 2989.15 | -1750.08 | FULL
G8 | 2967.96 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -808.02 | -808.55 | 3159.14 | 2967.86 | -1715.73 | FULL
G9 | 2481.77 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -838.76 | -838.02 | 3186.54 | 2479.82 | -1292.25 | FULL
G10 | 2411.84 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -839.07 | -838.58 | 3116 | 2410.2 | -1219.85 | FULL
G11 | 2400.13 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -840.2 | -839.88 | 3127.98 | 2398.64 | -1188.37 | FULL
G12 | 993.48 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -454.43 | -454.4 | 3163.22 | 994.1 | -307.03 | FULL
G13 | 882.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -453.35 | -453.33 | 3095.79 | 880.99 | -216.5 | FULL
G14 | 768.68 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -453.82 | -453.8 | 3112.1 | 767.97 | -126.21 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3165.77 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2632.22 | -2632.47 | 2567.2 | 3164.91 | -2013.47 | CTG_FAIL_IN_FULL
G1 | 3170.06 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2623.78 | -2624.02 | 2497.97 | 3169.24 | -1990.59 | CTG_FAIL_IN_FULL
G2 | 3137.09 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.29 | 510.61 | 510.72 | 2509.16 | 3136.35 | -1945.16 | FULL
G3 | 3239.53 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2632.32 | -2632.57 | 2564.48 | 3238.66 | -1995.54 | CTG_FAIL_IN_FULL
G4 | 3254.79 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2632.25 | -2632.52 | 2495.46 | 3253.83 | -1976.01 | CTG_FAIL_IN_FULL
G5 | 3268.17 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2630.78 | -2630.94 | 2508.12 | 3267.53 | -1963.9 | CTG_FAIL_IN_FULL
G6 | 2814.93 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -800.46 | -800.18 | 2539.4 | 2814.83 | -1636.5 | FULL
G7 | 2791.25 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -802.58 | -802.38 | 2467.94 | 2791.8 | -1593.69 | FULL
G8 | 2767.42 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -805.03 | -805.6 | 2479.93 | 2767.72 | -1556.54 | FULL
G9 | 2250.87 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -823.79 | -823.67 | 2512.19 | 2249.15 | -1114.41 | FULL
G10 | 2209.23 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -824.71 | -824.6 | 2442.61 | 2208.33 | -1060.23 | FULL
G11 | 2143.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -454.21 | -454.12 | 2455.57 | 2142.87 | -1000.63 | FULL
G12 | 295.29 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -444.46 | -444.62 | 2500.65 | 295.29 | 127.12 | FULL
G13 | 204.21 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -445.37 | -445.37 | 2436.04 | 204.57 | 204.79 | FULL
G14 | 118.59 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -446.58 | -446.57 | 2453.83 | 118.35 | 279.68 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3084.72 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2548.14 | -2548.23 | 2326.9 | 3084.34 | -1932.37 | CTG_FAIL_IN_FULL
G1 | 3091.6 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2539.73 | -2539.79 | 2257.94 | 3091.3 | -1901.42 | CTG_FAIL_IN_FULL
G2 | 3110.58 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -69.74 | -2545.61 | -2545.71 | 2270.85 | 3110.17 | -1894.81 | CTG_FAIL_IN_FULL
G3 | 2902.22 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2333.43 | -2334.52 | 2318.06 | 2901.65 | -1762.18 | FULL
G4 | 2915.48 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2325.52 | -2324.24 | 2248.91 | 2915.26 | -1741.96 | FULL
G5 | 2920.45 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -762.14 | -760 | 2261.25 | 2920.31 | -1724.24 | FULL
G6 | 2692.35 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -788.56 | -788.88 | 2296.6 | 2693.32 | -1537.4 | FULL
G7 | 2655.62 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -789.74 | -789.95 | 2226.12 | 2654.63 | -1489.15 | FULL
G8 | 2620.06 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -790.62 | -790.81 | 2238.23 | 2619.85 | -1443.17 | FULL
G9 | 1471.03 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -415.7 | -415.65 | 2263.29 | 1468.77 | -646.5 | FULL
G10 | 1328.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -410.75 | -410.7 | 2194.53 | 1328.13 | -539 | FULL
G11 | 1228.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -410.58 | -410.54 | 2209.18 | 1228.24 | -455.91 | FULL
G12 | -978.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.03 | -422.44 | -422.55 | 2286.54 | -978.09 | 851.96 | FULL
G13 | -1040.68 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.03 | -423.73 | -423.61 | 2224.05 | -1040.84 | 913.43 | FULL
G14 | -1164.99 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.03 | -423.43 | -423.56 | 2244.51 | -1164.45 | 1007.03 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2616.53 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2219.36 | -2220.6 | 2845.71 | 2616.37 | -1711.01 | FULL
G1 | 2645.73 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2238.82 | -2237.92 | 2775.6 | 2645.62 | -1705.14 | FULL
G2 | 2651.63 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2233.29 | -2234.61 | 2788.74 | 2651.55 | -1683.63 | FULL
G3 | 2677.38 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2266.64 | -2268.3 | 2844.32 | 2677.22 | -1689.33 | FULL
G4 | 2737.09 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2249.03 | -2247.94 | 2774.35 | 2736.28 | -1693.7 | FULL
G5 | 2722.08 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2222.08 | -2223.09 | 2787.5 | 2721.94 | -1653.83 | FULL
G6 | 2630.32 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -747.05 | -747.5 | 2829.84 | 2629.49 | -1544.86 | FULL
G7 | 2609.88 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -748.18 | -748.7 | 2759.3 | 2609.66 | -1500.03 | FULL
G8 | 2506.72 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -744.85 | -744.99 | 2769.33 | 2506.06 | -1405.73 | FULL
G9 | 1875.53 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -417.83 | -417.76 | 2802.41 | 1874.77 | -908.04 | FULL
G10 | 1772.73 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -417.02 | -416.93 | 2732.75 | 1772.99 | -824.06 | FULL
G11 | 1676.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -417.22 | -417.17 | 2745.25 | 1675.03 | -745.37 | FULL
G12 | -408.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.03 | -416.73 | -416.77 | 2805 | -407.96 | 502 | FULL
G13 | -491.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.03 | -417.23 | -417.27 | 2740.75 | -490.75 | 574.93 | FULL
G14 | -541.31 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.03 | -418.97 | -418.86 | 2758.63 | -540.26 | 629.04 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2487.41 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2148.55 | -2149.61 | 3195.89 | 2487.42 | -1646.14 | FULL
G1 | 2523.78 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2165.48 | -2166.4 | 3126.77 | 2523.74 | -1636.28 | FULL
G2 | 2533.12 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2163.35 | -2161.32 | 3139.44 | 2531.29 | -1612.52 | FULL
G3 | 2581.54 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2156.23 | -2158.34 | 3194.91 | 2582.19 | -1636.52 | FULL
G4 | 2601.91 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2159.17 | -2157.63 | 3125.51 | 2601.86 | -1614.41 | FULL
G5 | 2600.71 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -74.1 | -2206.51 | -2207.28 | 3138.28 | 2600.53 | -1582.09 | FULL
G6 | 2568.84 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -721.34 | -721.14 | 3185.04 | 2568.91 | -1514.46 | FULL
G7 | 2552.3 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -727.34 | -727.47 | 3113.9 | 2550.23 | -1474.96 | FULL
G8 | 2457.62 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -723.27 | -723.45 | 3124.25 | 2456.13 | -1388.46 | FULL
G9 | 1946.61 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -25.9 | -736.78 | -737.07 | 3160.49 | 1945.4 | -960.75 | FULL
G10 | 1879.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -420.34 | -420.3 | 3090.44 | 1877.41 | -888.89 | FULL
G11 | 1780.23 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -419.84 | -419.78 | 3102.53 | 1778.52 | -806.67 | FULL
G12 | -266.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.03 | -416.98 | -417.08 | 3159.31 | -267.32 | 420.73 | FULL
G13 | -338.46 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.03 | -417.99 | -417.97 | 3094.06 | -339.49 | 487.4 | FULL
G14 | -397.72 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.03 | -419.46 | -419.41 | 3111.44 | -397.61 | 548.04 | FULL
052R1WINTER09v5SNL(COV-CRES BYP)