SPECIAL SPECIFICATION

SECTION 15855

AIR HANDLING UNITS

Page

PART 1 - GENERAL

1.01  	Work Included	2

1.02  	Related Work	3

1.03  	Definitions	3

1.04 	 Performance Criteria	3

1.05  	Submittals	4

1.06  	Extra Stock	4

PART 2 - PRODUCTS

2.01  	Acceptable Manufacturers	5

2.02  	Fabrication And Design	5

2.03  	Casing	5

2.04  	Fan Section - Centrifugal, Plug Fan, And Axial Fan	7

2.05  	Coils	10

2.06 	 Mixing Box Section	12

2.07  	Access Modules	12

2.08  	Filter (Housings)	12

PART 3 - EXECUTION

SPECIAL SPECIFICATION

SECTION 15855

AIR HANDLING UNITS

PART 1 - GENERAL

1.01	WORK INCLUDED

A.	This section provides for furnishing and installing air handling units for heating, ventilating, air conditioning, and evaporative cooling and make-up air.

B.	Each air handling unit may have all or part of the following components (see drawing for layouts).

1.	Blower section.

a.	Centrifugal.

b.	Plug fan.

c.	Axial fan.

2.	Hot water heating coil.

3.	Steam heating coil.

4.	Chilled water cooling coil.

5.	Evaporative section.

6.	Access section.

7.	Filter section (Filters or Prefilter & Bag Filter)

8.	Mixing box section.

9.	Mixing box/filter section.

1.02	RELATED WORK

A.	Vibration Limits and Control.  Section 15200.

B.	Ductwork Systems.  Section 15890.

C.	HVAC Controls and EMCS System.  Section 13943.

D.	System Component Checkout and Balance.  Section 15901.

E.	Motors and Starters.  Division 16.

1.03	DEFINITIONS

A.	Low Pressure Units.  Total static pressures up to 3 inches w.g.

B.	Medium Pressure Units.  Total static pressures above and up to 6 inches w.g.

1.04	PERFORMANCE CRITERIA

Unit capacities and characteristics are scheduled on the drawings.  Each air handling unit shall have physical dimensions suitable to fit space allotted to the unit. Performance shall be based on elevation 5310' level conditions.

A.	Fan Performance Ratings.  Conform to AMCA 210 and bear the AMCA Certified Rating Seal.

B.	Sound Ratings.  AMCA 301; tested to AMCA 300 and bear AMCA Certified Sound Rating Seal.

C.	Fabrication.  Conform to AMCA 99 and ARI 430.

D.	Filter Media.  ANSI/UL 900 listed, Class I or Class II.

E.	Air Coils.  Certify capacities, pressure drops and selection procedures in accordance with ARI 410.

1.05	SUBMITTALS

A.	Submit shop drawings and product data in accordance with Section 01300.

B.	Shop drawings shall indicate assembly, unit dimensions, weight loading, required clearances, construction details, and field connection details.

C.	Product data shall indicate dimensions, weights, capacities, ratings, fan performance, motor electrical characteristics, and gages and finishes of materials.

D.	Provide fan curves with specified operating point clearly plotted.

E.	Submit sound power levels for both fan outlet and casing radiation at rated capacity.

1.06	EXTRA STOCK

Provide one complete matched set of drive belts for each AHU and one set of filters for each AHU.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

A.	Trane.

B.	Pace.

C.	McQuay.

2.02	FABRICATION AND DESIGN

A.	General.  Fabricate units with fan, coil, mixing box/filter section, access section, and cooling coil sections plus accessories as indicated on drawings.

B.	Structural Requirements

1.	Provide factory assembled modular units.  Large units may be shipped in assembled sections.

2.	Furnish units with sealing and fastening hardware supplied by the manufacturer.  Include written instructions needed to complete field assembly of the components.

3.	Provide units designed and constructed so that coils, panels, fan housing and fans can be removed without affecting the structural integrity of the unit.

2.03	CASING

A.	Construction.  All module sections (except fan sections) of components shall be 2" thick double-wall constructed.  Interior wall shall be of 18-gauge solid plate galvanized steel for components and perforated plate galvanized steel for 4" thick double-wall plug fan housing.  Foil faced insulation is not acceptable.

B.	Access.  Provide access to all sections of the unit by removable access panels big enough to permit removal of internal parts.  Provide gasketing ont he casing to seal access panels.  Provide fan and coils section access doors with ventlock hinges and latches.

C.	Finish.  Paint with one shop coat of industrial primer, or galvanize all parts of the unit, both inside and out, including belt guard and supports.  On painted units, add a coat of industrial enamel to the exterior.

D.	Insulation.  Insulate casing sections with 1-inch thick, 1-1/2 lbs. per cu. ft. density, neoprene coated, glass fiber insulation, "K" value at 75 F maximum 0.26 Btu/inch/sq.ft./degrees F/hr, applied to internal surfaces with adhesive and weld pins.  Coat exposed edges of insulation with adhesive.  Insulation with adhesive.  Insulation and adhesive:  conform to NFPA 90A.  Insulation shall not breed or promote fungi or bacteria, shall resist mold growth, shall not rot or sustain vermin.

E.	Drain Pan.  Provide the double-bottom type drain pan with 1/2-inch or more foam insulation in a sealed space between the two pans.

1.	Inside pan shall be all-welded construction and shall be coated with waterproofing material or shall be stainless steel.  Cross break and pitch to drain connection.

2.	Provide a large threaded drain connection on both sides at the low point of the pan.

3.	When two or more cooling coils are used,with one stacked above the other, individual drain troughs of galvanized steel with water-proofing material or stainless steel piped to the main drain pan shall be provided beneath each of the coils.

F.	Supports.  Provide suitable legs or support rods and clips as required to ensure adequate support of the complete unit.  Use a suitable suspension system for suspended units.

2.04	FAN SECTION - CENTRIFUGAL, PLUG FAN, AND AXIAL FAN

Provide double-inlet, squirrel-cage, centrifugal fans, with die-formed impeller blades.  Fans should be designed for quiet, slow-speed operation under specified rating conditions.

Primary air handling unit fan shall be single width, single inlet, multi-blade type plug (plenum) fans.  The fan blades shall be backward inclined airfoil (AF).

Plug fans shall be equipped with self-aligning, anti-friction split pillow block bearings with a minimum life of L-50 400,000 hours.

A.	Wheels.  Furnish wheels of rigid steel or aluminum construction, mechanically fastened to a common shaft.  Coat steel wheels with approved zinc-rich coat after fabrication.  For coating, use Zincilate, Sealube, Amercoat, or diametcoat.  Balance wheels statically and dynamically.  Design and test for continuous operation at maximum rated static pressure.

B.	Scrolls.  Provide fan scrolls of steel construction.  Rigidly secure the scrolls in the casing to prevent vibration.

C.	Shafts.  Provide solid hot rolled steel, ground and polished, with keyway and protectively coated with lubricating oil.

D.	Bearings

1.	Provide fan with self-aligning ball or roller type bearings selected for 200,000 hours minimum average life under actual load and speed conditions.

2.	Furnish adjustable block or flange mount bearings for accurate alinement of fan wheels in the scrolls.

3.	Bear shall be permanently lubricated or lubricated type with lubrication fitting externally accessible at the drive side of the unit.

4.	Bearing shall be supported by structural shapes, or die-formed sheet structural members, or support plates securely attached to the unit casing.

5.	Bearings shall not be fastened directly to the unit sheet metal casing.

6.	Blower wheels cantilevered on the ends of the shafts are not acceptable.

7.	Provide non-removable dust caps on the bearings.

E.	Drive.  Provide fans with a motor-driven V-belt designed for not less than 150 percent of connected motor horsepower.

1.	Furnish an adjustable-pitch motor sheave selected to produce specified capacity when set approximately at midpoint, and to provide not less than 20 percent variation in speed from full open to full closed.  Key the fan sheave to the fan shaft.

2.	Nonadjustable motor sheaves may be used for motors larger than 15 horsepower, provided that if for any reason it becomes necessary to change the sheave to produce specified capacity, replacement will be done at no additional cost.

F.	Belt Guard.  Fabricate to SMACNA Low Pressure Duct Construction Standards, of 12-gage, 3/4-inch, diamond mesh wire screen welded to steel angle frame or equivalent, prime coated.  Secure to fan or fan supports without short circuiting vibration isolation, with provision for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

G.	Motors

1.	Provide grease-lubricated ball bearings with alemite fittings.  For additional requirements, refer to Electrical Motors, Division 16.

2.	Mount the fan drive motor on an adjustable base and arrange for positive and easy adjustment of drive alinement and belt tension.

3.	Provide fan motors that will not overload when scheduled fan rpm is increased 10 percent.  Submit a fan curve for each scheduled unit showing operating points at scheduled conditions and at scheduled rpm increased 10 percent.

4.	Motors shall be 1750 rpm, TEFC, rated for 480 volts, 3 phase, 60 hertz.

H.	Axial Fans

1.	Constant volume units, air foil, In-line, axial flow, belt driven, fixed blade.

2.	Housing:  14-gauge steel with integral inlet bell and diffuser, painted finish of beige enamel.

3.	Inlet/Outlet Shells:  Tapered inlet/outlet shells over fan hub.

4.	Fan Wheel:  Aluminum casting with radially projected blades of air-foil cross section, factory dynamically balanced and keyed to fan shaft.

5.	Diffuser:  Cast aluminum with 29 radially projected straightening vanes of air-foil cross section.

6.	Shaft:  Solid AISI - C1040 hot rolled steel turned and polished.

7.	Bearings:  precision, flange mounted, self aligning ball bearings at inlet/discharge, grease lubricated with avg. life of 200,000.  Extended grease lines to exterior of shell.

8.	Motor:  High efficiency, ODP, outside of air stream.

9.	Accessories:  Inlet/outlet flanges, adjustable inlet vanes for pneumatic operations outlet flow stabilization screen (only on four smoke removal units).

10.	MFR:  Trane Company, Model "Q".

2.05	COILS

Provide coil section with coils and access to both sides of coils.  Enclose coils with headers and return bends exposed outside or fully contained within casing.  Slide coils into casing through removable end panel with blankoff sheets and sealing collars at connection penetrations.

A.	Standards.  Supply products of leading manufacturers with dependable published ratings, or equal.  Certify performance in accordance with latest edition ARI Standard 410.  Submit coil descriptive literature and rating information for review.

B.	Fabrication.  Construct coils of copper tubes with aluminum fins bonded to the tubes.

1.	Mount in a galvanized steel casing permitting removal of coil from unit. Coil sections shall have heavy-duty coil tracks extending the full width of the unit.

2.	Fins may be either plate type,with tubes mechanically bonded into the fins, or ribbon type, helically wound on individual tubes.  Provide a tight, mechanical bond between fins and tubes.  Use a minimum of six and a maximum of ten fins per linear inch (25 mm) of tube.

3.	Design coil section to prevent condensate carryover at face velocities 15 percent greater than design velocities.

C.	Water Coils.  Provide chilled water/coils.  Balance the circuits for equal pressure drop of no more than 10 feet on coils of six rows or fewer, nor more than 15 feet for coils with eight rows or more.

1.	Arrange each circuit for counterflow cooling with bottom supply connections.  Provide drain and vent connections at bottoms and top. Furnish access holes and covers.  Locate coil headers at the same end of the coil.

2.	Select water coil for approximately 3 to 4 feet per second velocity minimum, 5 fps (maximum).  Provide minimum .020-inch wall tubes and .010-inch fins.  Each coil shall be tested at the factory under water at not less than 250 psi air pressure and shall be suitable for 200 psi working pressure.

3.	Supply and return connections shall be clearly marked.

D.	Heating Coils

1.	Hot water (180°F).  Provide hot water coils, minimum two rows deep except where otherwise noted.  Design and construct hot water coils the same as cooling coils.

2.	Steam.

a.	Internal face and by-pass type with by-pass air flowing through vertical dampered openings in coil construction.  Casing:  14 ga. galvanized with baked enamel finish.

b.	Frame:  Rigid structural steel, galvanized with banked enamel finish.

c.	Coils:  Aluminum fin, replaceable seamless copper tubes brazed to headers.

Headers:  Heavy duty, Sch. 40 tubular steel.

d.	Dampers:  Preadjusted linkage, 16 ga. steel dampers, damper rods to rotate in nylon bearings, dampers with baked enamel finish.

e.	Face and by-pass channels:  16 ga. galvanized steel.

f.	MFR:  Wing Company, IFB Series.

2.06	MIXING BOX SECTION

Provide internally insulated, manufacturer's mixing box section with automatic dampers for mixing return air and outside air at top, bottom and rear as indicated on the drawing.

2.07	ACCESS MODULES

The access modules shall be provided by the air handling unit manufacturer, engineered to be used with the AHU unit.  All access modules shall be medium size unless otherwise noted.

2.08	FILTER (HOUSINGS)

A.	Slide Racks.  Provide and arrange suitable galvanized filter slide racks to permit easy removal of filters from the accessible side of unit.

PART 3 - EXECUTION

A.	Install in accordance with manufacturer's written instructions and in conformance with ARI 435.

B.	Install unit on vibration isolators.

C.	Do not operate units for any purpose, temporary or permanent, until ductwork is clean, filters are in place, bearings lubricated, and fan has been test run under observation.

END OF SECTION