November 21, 1997

Contract # TW-0928

SPECIAL SPECIFICATION

SECTION 15860-S

CENTRIFUGAL FANS

Page

PART 1 - GENERAL

1.01 	Description..	2

1.02	Related Work..	2

1.03	Quality Assurance..	2

1.04	References..	3

1.05	Submittals...	3

1.06 	Delivery, Storage, and Handling..	4

1.07	Sequencing..	4

1.08 	Extra Material..	4

PART 2 - PRODUCTS

2.01	Acceptable Manufacturers..	5

2.02 	General Fan Requirements..	5

2.03 	Centrifugal and Tubular Centrifugal Fans..	6

2.04 	Motors..	7

PART 3 - EXECUTION

3.01 	Inspection..	10

3.02 	Installation/Application/Erection...	10

3.03 	Field Quality Control..	11

3.04 	Adjusting and Cleaning..	11

3.05 	Commissioning....	11

3.06 	Demonstration...	12

SPECIAL SPECIFICATION

SECTION 15860-S

CENTRIFUGAL FANS

PART 1 - GENERAL

1.01	DESCRIPTION

A.  	This Section is for EF-1/-2 and RF-1/-2includes the following types of centrifugal fans:

Centrifugal (EF-1/-2) fans with inertia pads (See attached drawings for maximum dimensions of the inertia pad.) with their variable frequency drives (VFD) for indoor installations.

Tubular centrifugal (RF-1/-2) fans for horizontal indoor installations.

1.02	RELATED WORK

A.  	Section 01300-S

B.  	Section 13943-S

C.  	Section 15010-S

D.  	Section 15200-S

Section 15901-S

Division 16 Section "Circuit and Motor Disconnects" for disconnect switches.

G.  	Division 16 Section "Motor Controllers" for motor starters.

H.  	Division 16 Section "Motor Control Centers" for starters and fusible switches.

1.03	QUALITY ASSURANCE

A.  	Provide motors and electrical accessories that comply with National Electrical Manufacturers Association (NEMA) standards.

B.  	Provide components according to National Fire Protection Association (NFPA) 70 "National Electrical Code."

1.04	REFERENCES

A.  	Anti-Friction Bearing Manufacturers Association (AFBMA) Standard 9 for ball bearings

B.  	AFBMA Standard 11 for roller bearings

C.  	Air Movement Contractors Association (AMCA) Standard 210/American Society of Heating, Refrigerating, and Air-Conditioning Engineers (ASHRAE) Standard 51, Laboratory Methods of Testing Fans for Rating

D.  	AMCA Standard 300, Test Code for Sound Rating

E.  	AMCA Standard 301, Method for Calculating Fan Sound Ratings From Laboratory Test Data

F.  	American Society for Testing and Materials (ASTM) A36

G.  	ASTM A150

H.  	Institute of Electrical and Electronic Engineers (IEEE) Standard 112, Test Method B

I.  	NEMA 1

J.  	NEMA Standard MG 1

K.  	NFPA 70, National Electrical Code

L.  	Steel Structures Painting Council (SSPC) Surface Preparation Specifications SP 2 or SP 3

1.05	SUBMITTALS

A.  	Make submittals according to this Section, Section 15010-S, and Section 01300-S.

B.  	Submit product data for selected models, including specialties, accessories, and the following:

1.  	Certified fan performance curves with system operating conditions indicated.  All performance curves shall be corrected for an altitude of 5,500 ft.

2.  	Certified fan sound power ratings.

3.  	Motor ratings and electrical characteristics plus motor and fan accessories.

4.  	Materials gages and finishes, including color charts.

5.  	Dampers, including housings, linkages, and operators.

C.  	Submit shop drawings from manufacturer detailing equipment assemblies and indicating dimensions, weights, required clearances, components, and location and size of field connections.

D.  	Submit coordination drawings, in accordance with Division 15 Section "Basic Mechanical Requirements, "for fan room layouts."

E.  	Submit wiring diagrams that detail power, signal, and control wiring. Differentiate between manufacturer-installed wiring and field-installed wiring.

F.  	Submit maintenance data in the operating and maintenance manual as specified in Section 01300-S.

1.06	DELIVERY, STORAGE, AND HANDLING

A.  	Deliver fan units as a factory-assembled unit to the extent allowable by shipping limitations, with protective crating and covering.

B.  	See Section 15010-S.

1.07	SEQUENCING

A.  	Coordinate the size and location of concrete equipment pads.

B.  	Coordinate the size and location of structural steel support members.

1.08	EXTRA MATERIAL

A.  	Furnish one additional complete set of belts for each belt-driven fan.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

A.  	Provide products by one of the following:

1. 	Centrifugal Fans:

a. 	Barry Blower

b. 	Champion Fan

Buffalo Forge Co.

Greenheck

Twin City

B.	Substitutions: only under provisions of Section 1600-S.

2.02	GENERAL FAN REQUIREMENTS

A.  	Provide fans that are factory fabricated and assembled, factory tested, and factory finished, with indicated capacities and characteristics.

B.  	Fans and Shafts:  Statically and dynamically balanced and designed for continuous operation at the maximum rated fan speed and motor horsepower.

1.  	Fan Shaft:  Turned, ground, and polished steel, designed to operate at no more than 70 percent of the first critical speed at the top of the speed range of the fan's class.

C.  	Belt Drives:  Factory mounted, with final alignment and belt adjustment made after installation.

1.  	Service Factor:  1.4.

D.  	Belts:  Oil-resistant, nonsparking, and nonstatic.

E.  	Motors and Fan Wheel Pulleys:  Adjustable pitch for use with motors through 15 horsepower (hp); fixed pitch for use with motors larger than 15 hp. Select pulley so that pitch adjustment is at the middle of the adjustment range at fan design conditions.

1.  	Belt Guards:  Provide steel belt guards for motors mounted on the outside of the fan cabinet.

F.  	Shaft Bearings:  Provide type indicated, having a median life "Rating Life" (AFBMA (L10)) of 120,000, calculated in accordance with AFBMA Standard 9 for ball bearings and AFBMA Standard 11 for roller bearings.

G.  	Factory Finish:  The following finishes are required:

1.  	Sheet Metal Parts:  Prime coating prior to final assembly.

2.  	Exterior Surfaces:  Baked-enamel finish coat after assembly.

H.  	The following factory tests are required:

1.  	Sound Power Level Ratings:  Comply with AMCA Standard 301 "Method for Calculating Fan Sound Ratings From Laboratory Test Data." Test fans in accordance with AMCA Standard 300 "Test Code for Sound Rating." Fans shall be licensed to bear the AMCA Certified Sound Ratings Seal.

2.  	Fan Performance Ratings:  Establish flow rate, pressure, power, air density, speed of rotation, and efficiency by factory tests and ratings in accordance with AMCA Standard 210/ASHRAE Standard 51 - Laboratory Methods of Testing Fans for Rating.

2.03	CENTRIFUGAL AND TUBULAR CENTRIFUGAL FANS

A.  	General Description:  Belt-driven centrifugal fans consisting of housing, wheel, fan shaft, bearings, motor, drive assembly, and support structure.  Centrifugal fan shall be Class III construction.

Housings:

1.	Centrifugal  Fans - Fabricated from formed and reinforced galvanized steel panels to form curved scroll housings with continuously welded flanged split housing and access doors or panels to allow access to internal parts and components.

a.     Duct Connections:  Flanged.

Panel Bracing:  Steel angle- or channel-iron member supports for  	mounting and supporting fan scroll, wheel, motor, and accessories.

2.	Tubular Centrifugal Fans - Fabricate tubular housing from formed - and reinforced-steel panels with welded seams and the following:

Outlet guide vanes

Motor disconnect switch.

Spun inlet cone with flange.

Outlet flange.

Brackets suitable for horizontal mounting.

C.  	Fan Wheels:  Single-width, single-inlet, welded to cast-iron or cast-steel hub and spun steel inlet cone, with hub keyed to the shaft.

1.  	Blade Materials:  Steel.

2.  	Blade Type:  Backward-curved, airfoil type.

D.  	Shaft Bearings:  Grease-lubricated, self-aligning, pillow-block type; tapered roller bearings with double-locking collars and two- piece, cast-iron housing.

E.  	Accessories:  The following accessories are required where indicated:

1.  	Scroll Housing Access Doors:  Latch-type handles; flush-mounted for uninsulated housings and raised-mounted for insulated housings.

2.  	Drain Connections for Centrifugal Fans:  Threaded, 3/4-inch NPS, capped nipple installed at lowest point of housing.

Shaft Seals:  Air-tight seals installed around shaft on drive side of single-width fans.

Discharge Backdraft Damper:  Basis of Design Ruskin CBS92 or Approved Substitute.

5.	Inertia Pad shall be provided for the centrifugal fans.

2.04	MOTORS

A.  	General

1.  	Apply requirements below to motors covered by this Section except as otherwise indicated.

2.  	Motors 1 horsepower (hp) and Larger:  Polyphase.

3.  	Frequency Rating:  60 Hz.

4.  	Voltage Rating:  Determined by voltage of circuit to which motor is connected for the following motor voltage ratings (utilization voltages):

a. 		Motors smaller than 1 hp: 120 V circuit, 115 V - motor rating.

b. 		Motors 1 hp and larger: 480 V circuit, 460 V - motor rating.

5.  	Service factors indicated for motors are minimum values and apply at frequency and utilization voltage at which motor is connected.  Provide motors which will not operate in service factor range when supply voltage is within 10 percent of motor voltage rating.

6.  	Provide permanent-split capacitor classification motors for shaft-mounted fans and capacitor start classification for belted fans.

7.  	Capacity:  Minimum size as indicated.  If not indicated, sufficient to start and operate connected loads at designated speeds in indicated environment, and with indicated operating sequence, without exceeding nameplate ratings.  Provide motors rated for continuous duty at 100 percent of rated capacity.

8.  	Temperature Rise:  50 degree (deg) Celsius (C) maximum temperature rise at 40 deg C ambient for continuous duty at full load (Class A Insulation).

9.  	Motor Speed:  Single, multiple, or variable as indicated.

10. 	Motor Construction:  NEMA Standard MG 1.

a. 	Bases:  Adjustable.

b. 	Bearings:  The following features are required:

1)  	Roller bearings with inner and outer shaft seals.

2)  	Grease lubricated.

3)  		Designed to resist thrust loading where belt drives or other drives produce lateral or axial thrust in motor.

c. 		Enclosure Type:  The following features are required:

1)  		Open drip-proof motors where satisfactorily housed or remotely located during operation.

2)  		Guarded drip-proof motors where exposed to contact by employees or building occupants.

d. 		Noise rating:  Quiet. Min. NC-35

e. 		Nameplate:  Indicate the full identification of manufacturer, ratings, characteristics, construction, and special features.

11. 	Starters, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 16.

B.  	Polyphase Motors

1.  	Squirrel-cage, induction-type, general-purpose conforming to the following requirements except as otherwise indicated.

2.  	NEMA Design Letter Designation:  "B," unless specifically designated "C" for high starting torque.

3.  	Service Factor:  1.15.

4.  	Premium Efficient Motors:  Guaranteed minimum efficiency equal to or greater than 94.1% for a 50 hp motor, and 94.5% for a 60 hp motor, and 95.4% for a 125 hp motor.  Guaranteed minimum efficiencies are established for 4 pole and 1800 rpm synchronous speed motors.

5.  	Variable Speed Motors for Use With Solid-State Drives:  Energy efficient, squirrel-cage induction, design B units with ratings, characteristics, and features coordinated with and approved by drive manufacturer.  See Division 16 for specifications on VFDs.

6.  	Internal Thermal Overload Protection For Motors:  For motors so indicated, protection automatically opens control circuit arranged for external connection.  Protection operates when winding temperature exceeds safe value calibrated to the temperature rating of the motor insulation.

7.  	Bearings:  Double-shielded, pre-lubricated ball bearings suitable for radial and thrust loading of the application, unless noted otherwise.

PART 3 - EXECUTION

3.01	INSPECTION

A.  	Inspect areas and conditions, with Installer present, for compliance with requirements for installation tolerances, housekeeping pads, and other conditions affecting performance of fans.

B.  	Do not proceed until unsatisfactory conditions have been corrected.

3.02	INSTALLATION/APPLICATION/ERECTION

A.  	General

1.  	Install fans level and plumb, in accordance with manufacturer's written instructions.  Support units as described below, using the vibration control devices and anchorage indicated in Section 15200.  Provide siesmic restraints according to Section 15201.

a. 		Support floor-mounted units on concrete inertia bases with approved vibration isolation and anchorage.

b. 		Support ceiling mounted units with supports for the fan separate from the ductwork with approved vibration isolation and anchorage.  Provide hanger rods according to loads allowed in SMACNA Round Industrial Duct Construction Standards, and support according to SMACNA.

2.  	Arrange installation of units to provide access space around units for service and maintenance.

B.  	Connections

1.  	Duct installations and connections are specified in other Division 15 sections.  Make final duct connections with flexible connections.

2.  	Electrical Connections:  The following requirements apply:

a. 	Electrical power wiring is specified in Division 16.

b. 		Temperature control wiring and interlock wiring is specified in Section 13943.

c. 		Grounding:  Connect unit components to ground in accordance with the National Electrical Code.

3.03	FIELD QUALITY CONTROL

A.  	Arrange and pay for a factory-authorized service representative to perform the following:

1.  	Inspect the field assembly of components and installation of fans including ductwork, and electrical connections.

2.  	Prepare a written report on findings and recommended corrective actions.

3.04	ADJUSTING AND CLEANING

A.  	Clean unit cabinet interiors to remove foreign material and construction dirt and dust.  Vacuum clean fan wheel and cabinet.

3.05	COMMISSIONING

Provide labor, material, equipment, etc., required to facilitate the commissioning process.  Perform tests and verification procedures required by the commissioning process when requested by SNL’s Commissioning Authority and directed by the General Contractor’s Test Engineer.

Final Checks before Startup:  Perform the following operations and checks before startup:

Verify that shipping, blocking, and bracing are removed.

Verify that unit is secure on mountings and supporting devices and that connections for piping, ducts, and electrical components are complete.  Verify that proper thermal-overload protection is installed in motors, starters, and disconnects.

Perform cleaning and adjusting specified in this Section.

Disconnect fan drive from motor, verify proper motor rotation direction, and verify fan wheel free rotation and smooth bearings operation.  Reconnect fan drive system, align and adjust belts, and install belt guards.

Verify lubrication for bearings and other moving parts.

Verify that manual and automatic volume control and fire and smoke dampers in connected ductwork systems are in the fully open position.

Starting procedures for fans are as follows:

1.	Energize motor; verify proper operation of motor, drive system and, fan wheel.  Adjust fan to indicated RPM.

2.	Measure and record motor voltage and amperage.

Refer to Section 15901-S for procedures for air-handling-system testing, adjusting, and balancing.

E.	Replace fan and motor pulleys as required to achieve design conditions.

3.06	DEMONSTRATION

Train Owner’s maintenance personnel on procedures and schedules related to startup and shutdown, troubleshooting, servicing, and preventive maintenance.

Review data in the operation and maintenance manuals.  Refer to Division 1.

Schedule training with SDR, with at least 7 days’ advance notice.

Demonstrate operation of fans.  Conduct walking tour of the Project. Briefly identify location and describe function, operation, and maintenance of each fan.

END OF SECTION

EXCEPT FOR

DWG F-10A10A