Date: 21 March 2001

Project: Intercryostat Detector Electronics

Subject: Low Voltage Distribution

This note and supplemental documents describe the low voltage distribution system designed to deliver power to the Intercryostat Detector (ICD) preamplifiers (preamps).

General Information

The preamps used by the ICD are the I-type version of those used in the rest of the calorimeter readout, differing only in the integrating capacitor value (22pF) and two resistors in the output shaping circuit, which “stretches” the ICD PMT signal to look like a calorimeter signal.  These preamps are mounted on circuit boards (six per board), and each board is housed in an ICD electronics “drawer”.   These drawers also contain the photomultiplier tubes (PMTs) and the high voltage bases for the PMTs.  The drawers are installed into ICD crates (16 per crate) which are mounted beneath the cable winders in each detector quadrant.  The ICD signal readout is part of the calorimeter BLS/ADC system.

The following electronics systems used by the ICD are identical with the calorimeter as a whole, and are described in their corresponding Operational Readiness Review documents:

- The preamps.

- The preamp power supply.

- The high voltage power supply. (In addition, a document detailing the safe usage of the ICD high voltage distribution system was submitted and accepted.)

- The preamp pulser and fan-out card.

- The pulser power supply.

- The BLS/ADC readout.

Those items unique to the ICD electronics are the low voltage fan-out system, electronics drawers, voltage supply cables, and the racks in which the power supplies are mounted. Figure 1 shows the general layout of the ICD tiles and crates.

The low voltage for the ICD preamps is supplied by a custom VME-controlled power supply, designed by Dave Huffman of FNAL.  It is identical in operation to a calorimeter low voltage power supply.  The ICD low voltage power supply is located on rack PW09 on the western side of the platform (Figures 2-4).  The power supply will provide three separate voltages: 8 V @ 10 Amps, 12 V @ 10 Amps and –6 V @ 10 Amps.  The power will be supplied to each of the 48 ICD electronics drawers.  The voltage and current can be monitored via a computer connection.  If any voltage or current exceeds a set level, all output voltages will be disabled.  This is done to prevent the application of partial power to the preamps.  The supplies are fused on the primary 208 V AC input and the DC output.   A solid state 3-phase relay is used to control the application of AC power to the supply.  There is a local On/Off, Reset and Local/Remote switch on the front panel.  There are LED indicators on the front panel showing the status of the supply.

Requirements

The design must meet all Fermilab electrical safety standards and all components must be rated for the maximum current and temperatures to which they will be exposed.  Voltages delivered to the preamplifiers must be within 0.1V of the nominal values.

Details of Implementation

The power path from the wall socket to the fan-out card is shown in Figures 5-9.  One power supply provides the three voltages to each of the four ICD crates.  Each voltage and associated ground is split 1:4 by Stinger gold plated power distribution blocks (SDB2 4 GA to 10 GA).  The splitters are mounted with nylon screws to a panel installed near the bottom of the PW09 rack (Figures 12-13).  Three pairs of conductors are required to distribute each of the three voltages and associated grounds to the four quadrants.  For each quadrant, one three-conductor (202-10-3503) and one four-conductor (202-10-3504) Okonite-FMR 10 AWG cable are used.  The insulated conductors are UL rated VW-1, and pass vertical tray flame test of UL 1277 for type TC power and control tray cable.  The 90ºC wet or dry ampacity of the Okonite cables is 30 Amps per conductor.  The calorimeter low voltage power supply provides a maximum 10 Amps at each voltage.  The large size cable was picked primarily to minimize the voltage drop between the supply and the preamplifiers.   One of the conductors in the three-conductor cable is not used.

The Okonite cables are routed to the ICD crates at each detector quadrant via the false platform floor, the vertical chutes and the cable winders.  The low voltages are distributed to the ICD drawers through a fan-out card mounted below the ICD crates.  The fan-out card is a long PC board with individual fuses for each voltage to each drawer.  Three pairs of conductors are fed into a terminal block (Divisible Europa Strip).  The block is a 6-pole strip rated at 40 Amps with a maximum thickness of a 10 AWG conductor.  The terminal block is connected to the fan-out card via short runs of hookup wire, soldered directly to the PC board.  The voltages for each drawer are fused with GMA 5 x 20 mm fast-acting glass fuses, rated to 500 mAmps.  The voltages are fed to the ICD drawers by short patch cables, which are Alpha brand, item 6428, multi-pair foil-shielded tray cable, 18 AWG, UL type CM/PLTC, CSA PCC ft4.  The patch cable with the foil shield and outer plastic jacket removed was also used to fashion the cable harness within the low voltage fan-out.  Similar 22 AWG wire is used for the jumpers from the fan-out PC board to the bulkhead connectors.  Figure 10 shows a photo of an assembled low voltage fan-out with the pulser fan-out and cables attached.  Figure 4 shows a schematic of the low voltage fan-out card and fuse layout.

Also housed with the low voltage fan-out card is the fan-out card for the ICD pulser system.  This pulser system is identical to the calorimeter pulser system, and has been reviewed as part of the calorimeter preamp pORC review.  The pulser and pulser power supply are mounted in the same rack (PW09) as the ICD low voltage power supply.

The low voltage fan-out is mounted in a custom-made aluminum box isolated by plastic washers.  The pulser fan-out is mounted to the back of the low voltage fan-out by plastic standoff posts.  The low voltage supply cables enter the low voltage fan-out housing via a rectangular aperture in the side.  The supply cables attach to a Divisible Europa Strip connection block mounted on the back of the housing.  A cable harness consisting of 18 AWG hookup wire is connected to the Europa strip at one end, and soldered to the low voltage fan-out PC board at the other end.  A similar hookup wire is used to connect each voltage, via a fuse, to a bulkhead connector mounted on the front of the low voltage fan-out housing.  The multi-pair patch cables connect to the bulkheads and the corresponding connectors on the ICD drawers.  The pulser current supply cables and the pulser com-mand cables which run from the PW09 rack enter through the other side aperture.  The pulser fan-out cables exit through a long narrow slit on the front of the housing and are

connected to the ICD drawers.  The low voltage housing is mounted below the ICD crate, with a large mounting screw at each side.  Figure 11 shows a mounted fan-out in place below one of the ICD crates.

Rack Monitor Interface

Each LED is green if conditions are normal and red if a fault has been triggered.  A fault will remain once triggered, and the associated LED will remain red until a computer gen-erated reset occurs or until the RESET button is pressed.  The control of the rack monitor interface is via a cable from the 1553 to a 37-pin D connector.  The only control function available is RESET.

The smoke detector sensor is connected into a wire harness that enters the rear of the

rack monitor interface.  A +20 V and ground are supplied to the smoke detector.  The

+20 V is interrupted when a RESET occurs to clear the detector condition.  The RESET

is supplied by a front panel push button or by an output bit from the 1553.  A fault occurs

if the detector smells smoke or if the cable is disconnected.  If a fault occurs, the front

panel Smoke Detector LED is lit, the annunciator is activated and the OK/Smoke bit supplied to the 1553 changes to indicate smoke.  A Fault Out signal is produced to disable the power supply.

Figure 1: Conceptual view of the ICD layout

# Fig. 2: Conceptual Layout of the ICD Low Voltage Distribution System

Figure 11: ICD low voltage fan-out mounted below an ICD crate.

Figure 12: Input cables from low voltage power supply to splitter.

Figure 13: Low voltage splitter panel.

Figure 14: Terminal block for low voltage fan-out.

Figure 15: Segment of low voltage fan-out board.

Figure 16:  Fan-out connectors for output of low voltage to ICD drawers.

# Text boxes

ICD scintillator tiles

LV fanout box

Bot. cable winder

Top cable

winder

ICD NE crate electronics

LV fanout box

Bot. cable winder

Top cable winder

ICD NW crate electronics

Notes:

- There are 16 ICD boxes for each endcap with  12 scintillator tiles in each  box.  This equates to 12x16=192 signal channels per endcap, or 96 per quadrant.

- The tiles are connected to the ICD crates by fiber cables, five meters in length.

- Each ICD electronics crates contains 16 ICD electronics drawers, 6 PMTs  per drawer.

Fiber cable (5 m length)

End-cap calorimeter face

D0 North End

ICD box

(Contains 12 tiles)

Figure 10: Photo of an assembled low voltage fan-out card and housing with the pulser fan-out cables attached.