#### Totally Enclosed Fan Cooled - Electric Motors

- The vendor will provide totally enclosed fan cooled electric induction motors that are labeled “NEMA Premium” or meet the latest Federal Energy Management Program (FEMP) designated performance levels. To find the latest performance levels, visit the FEMP Web site at www.eere.energy.gov/femp/procurement/

- As of March 2006, the FEMP performance requirement called for:

| Performance Requirement for Totally Enclosed Fan Cooled Induction Motors Rated 600 volts or Less (Random Wound) |
| --- |
| Motor Size (horsepower) | Nominal Full-Load Efficiency |
|  | 6-pole (1200 rpm) | 4-pole (1800 rpm) | 2-pole (3600 rpm) |
| 1 | 82.5 | 85.5 | 77.0 |
| 1.5 | 87.5 | 86.5 | 84.0 |
| 2 | 88.5 | 86.5 | 85.5 |
| 3 | 89.5 | 89.5 | 86.5 |
| 5 | 89.5 | 89.5 | 88.5 |
| 7.5 | 91.0 | 91.7 | 89.5 |
| 10 | 91.0 | 91.7 | 90.2 |
| 15 | 91.7 | 92.4 | 91.0 |
| 20 | 91.7 | 93.0 | 91.0 |
| 25 | 93.0 | 93.6 | 91.7 |
| 30 | 93.0 | 93.6 | 91.7 |
| 40 | 94.1 | 94.1 | 92.4 |
| 50 | 94.1 | 94.5 | 93.0 |
| 60 | 94.5 | 95.0 | 93.6 |
| 75 | 94.5 | 95.4 | 93.6 |
| 100 | 95.0 | 95.4 | 94.1 |
| 125 | 95.0 | 95.4 | 95.0 |
| 150 | 95.8 | 95.8 | 95.0 |
| 200 | 95.8 | 96.2 | 95.4 |
| 250 | 95.8 | 96.2 | 95.8 |
| 300 | 95.8 | 96.2 | 95.8 |
| 350 | 95.8 | 96.2 | 95.8 |
| 400 | 95.8 | 96.2 | 95.8 |
| 450 | 95.8 | 96.2 | 95.8 |
| 500 | 95.8 | 96.2 | 95.8 |
| Performance Requirement for Totally Enclosed Fan Cooled Induction Motors Rated Medium Voltage – 5 kV or less (Form Wound) |
| 250-500 | 95.0 | 95.0 | 95.0 |

# Footnotes

Premium efficiency electric motors usually have higher inrush current than equivalent models. In older buildings, make sure existing circuits and protection equipment are adequate to handle this higher initial current, especially when replacing “Design B” with “Design A” motors.

This recommendation applies to general-purpose, single speed, polyphase induction motors. Some applications require definite-purpose, special-purpose, special frame, or special mounted polyphase induction motors. A motor meeting this efficiency recommendation should be available for these other applications.

Motor efficiency is identified on the nameplate by “nominal” efficiency, which represents the average efficiency of a large population of the same design. It is measured in accordance with NEMA MG 1-1998, Motors and Generators, and IEEE 112 Test Method B.