## Inputs - base case
Fan Project |  | Base Case M&V Plan |  |  |  |  | indicates input parameter
Numerical inputs only | [6 empty] | indicates tool output
ECM Level
Project: A variable frequency drive is added at a constantly loaded 150HP fan motor.
Constant Load, Timed Schedule to Variable Load, Variable Schedule
Energy Rate: | 0.1 | per kWh
| Labor | Hours | Totals |  |  | Direct Costs: |  |  |  |  | Baseline | 509832 | kWh
Rate 1 | 65 | 32 | 2080 |  |  | Monitoring Equipment Cost | 114.5 |  |  |  | Post | 343465.25 | kWh
Rate 2 | 80 | 24 | 1920 |  |  | Other Equipment Costs | 12.5 | logger software |  |  | ECM Savings | 166366.75 | kWh
|  |  | 4000 |  |  | Travel and lodging | 100 | mileage, meals |  |  | Savings % | 32.63%
[6 empty] | Miscellaneous Costs | 0 |  |  |  | ECM Cost Savings | 16636.675
[7 empty] | 227 |  |  |  | ECM Savings Uncertainty (%) | 35.88%
M&V Method Level | [10 empty] | ECM Savings Uncertainty ($) | 5969.8761
Equation Selection |  | Esave = kWbaseHRSbase - SikWpost,iHRSpost,i | [8 empty] | M&V Plan Cost | 4227
[11 empty] | Fract. M&V Cost | 25.41%
Number Operation Stages |  | 10
Data Collection Method Level
kWbase |  |  |  | HRSbase |  |  |  | kWpost,i |  |  |  | HRSpost,i
value | 58.2 |  |  | value | 8760 |  |  | values | 18.65 | 18.65 | 1.865 | values | 100
single spot measurement |  |  |  | stipulation |  |  |  |  | 19.92 | 19.92 | 1.992 |  | 50
[9 empty] | 21.98 | 21.98 | 2.198 |  | 150
Variable Total Uncertainty Value |  |  | 5.51% | Variable Total Uncertainty Value |  |  | 10% |  | 24.81 | 24.81 | 2.481 |  | 425
[9 empty] | 28.43 | 28.43 | 2.843 |  | 785
[9 empty] | 32.82 | 32.82 | 3.282 |  | 1565
[9 empty] | 38 | 38 | 3.8 |  | 2250
[9 empty] | 43.95 | 43.95 | 4.395 |  | 1750
[9 empty] | 50.69 | 50.69 | 5.069 |  | 985
[9 empty] | 58.2 | 58.2 | 5.82 |  | 700
[8 empty] | ind. var. | Pressure |  |  | ind. var. | Pressure
[8 empty] | short-term monitoring |  |  |  | Short-term monitoring
[8 empty] | Variable Total Uncertainty Value |  |  | 9% | Variable Total Uncertainty Value |  |  | 2%
Data Collection Equipment Level
kWbase |  |  |  | HRSbase |  |  |  | kWpost,i |  |  |  | HRSpost,i
Selected Measurement Instrument |  |  |  | Selected Measurement Instrument |  |  |  | Selected Measurement Instrument |  |  |  | Selected Measurement Instrument
Fluke 39 |  |  |  | n/a |  |  |  | Veris Enspector E7003 |  |  |  | none | (using time-stamped Veris logger data)
Relevant Uncertainty Values |  |  |  | Relevant Uncertainty Values |  |  |  | Relevant Uncertainty Values |  |  |  | Relevant Uncertainty Values
Uinst,prec |  | 1% | 0.5102% | Ustip |  | 10% |  | Umeas,prec |  | 3% |  | Uinst,prec |  | 0% | 0%
Uinst,bias |  | 0% | 0% |  |  |  |  | Umeas,bias |  | 3% |  | Uinst,bias |  | 0% | 0%
Ueqp,prec |  | 5% | 5% |  |  |  |  | Umodel,prec |  | 3% |  | Ubias,bin i |  | 2% | 2%
Variable Uncertainty |  |  | 5.51% | Variable Uncertainty |  |  | 10% | Umodel,bias |  | 0%
[8 empty] | Variable Uncertainty |  |  | 9% | Variable Uncertainty |  |  | 2%
Equipment Purchase Cost |  |  | 590 | Equipment Purchase Cost |  |  | 0 | Equipment Purchase Cost |  |  | 306 | Equipment Cost |  |  | 0
Amortization Factor |  |  | 0.1 | Amortization Factor |  |  | 0.1 | Amortization Factor |  |  | 0.1 | Amortization Factor |  |  | 0.1
Equipment Cost |  |  | 59 | Equipment Cost |  |  | 0 | Equipment Cost |  |  | 30.6 | Equipment Cost |  |  | 0
[8 empty] | Independent Variable Instrument |  |  |  | Independent Variable Instrument
[8 empty] | Onset HOBO air pressure |  |  |  | Onset HOBO air pressure
[8 empty] | Equipment Purchase Cost |  |  | 249 | Equipment Cost |  |  | 249
[8 empty] | Amortization Factor |  |  | 0.1 | Amortization Factor |  |  | 0.1
[8 empty] | Equipment Cost |  |  | 24.9 | Equipment Cost |  |  | 24.9
Note on C45: David Jump: at 95% confidence interval
Note on D45: David Jump: at 68% confidence interval

## fan base case calcs
| Baseline |  |  |  | Uncertainty
| kW | HRS | kWh |  | kW | HRS
| 58.2 | 8760 | 509832 |  | 5.51% | 10%
squared
[5 empty] | 0.0030362 | 0.01
summed
0.013036
square root
0.11418
[5 empty] | abs uncert. | rel. uncert.
[5 empty] | 58210.7479 | 11.42%
| Post |  |  |  | Uncertainty
| kW_i | HRS_i | kWh_i | squared | kW | HRS
| 18.65 | 100 | 1865 | 3478225 | 9% | 2%
| 19.92 | 50 | 996 | 992016 | squared
| 21.98 | 150 | 3297 | 10870209 | 0.0081 | 0.0004
| 24.81 | 425 | 10544.25 | 111181208.0625 | sum
| 28.43 | 785 | 22317.55 | 498073038.0025 | 0.0085
| 32.82 | 1565 | 51363.3 | 2638188586.89 | sqrt
| 38 | 2250 | 85500 | 7310250000 | 0.092195
| 43.95 | 1750 | 76912.5 | 5915532656.25
| 50.69 | 985 | 49929.65 | 2492969949.1225
| 58.2 | 700 | 40740 | 1659747600 |  | abs uncert.
total |  | 8760 | 343465.25 | 20641283488.3275 | 175450909.6508 | 13245.7884
rel. uncert.
3.857%
savings
| base - post |  | abs. savings uncert.
| 166366.75 |  | 59698.7612
rel. savings uncert.
35.88%

## Inputs - plan #1
Fan Project |  | M&V Plan #1 |  |  |  |  | indicates input parameter
Numerical inputs only | [6 empty] | indicates tool output
ECM Level
Project: A variable frequency drive is added at a constantly loaded 15HP fan motor.
Constant Load, Timed Schedule to Variable Load, Variable Schedule
Energy Rate: | 0.1 | per kWh
| Labor | Hours | Totals |  |  | Direct Costs: |  |  | Baseline | 509832 | kWh
Rate 1 | 65 | 40 | 2600 |  |  | Monitoring Equipment Cost | 247.5 |  | Post | 343465.25 | kWh
Rate 2 | 80 | 24 | 1920 |  |  | Other Equipment Costs | 12.5 | logger software | ECM Savings | 166366.75 | kWh
|  |  | 4520 |  |  | Travel and lodging | 50 | mileage, meals | Savings % | 32.63%
[6 empty] | Miscellaneous Costs | 0 |  | ECM Cost Savings | 16636.675
[7 empty] | 310 |  | ECM Savings Uncertainty (%) | 30.65%
M&V Method Level | [8 empty] | ECM Savings Uncertainty ($) | 5099.0728
Equation Selection |  | Esave = kWhbase - kWhpost | [6 empty] | M&V Plan cost | 4830
[9 empty] | Fract. M&V Cost | 29.03%
Number Operation Stages |  | 1
[9 empty] | Benefit-Cost Plan 1: | 1.4441
Data Collection Method Level
kWhbase |  |  |  | kWhpost
value | 509832 |  |  | value | 343465
stipulation |  |  |  | continuous monitoring
Variable Total Uncertainty Value |  |  | 10% | Variable Total Uncertainty Value |  |  | 0.2551%
Data Collection Equipment Level
kWhbase |  |  |  | kWhpost
Selected Measurement Instrument |  |  |  | Selected Measurement Instrument
PST Ultralite
Relevant Uncertainty Values |  |  |  | Relevant Uncertainty Values
Ustip |  | 10% |  | Uinst,prec |  | 0.5% | 0.2551%
|  |  |  | Uinst,bias |  | 0% | 0%
Variable Uncertainty |  | 10% |  | Variable Uncertainty |  |  | 0.2551%
Equipment Purchase Cost |  | 0 |  | Equipment Cost |  |  | 495
Amortization Factor |  |  |  | Amortization Factor |  |  | 0.5
Equipment Cost |  | 0 |  | Equipment Cost |  |  | 247.5

## lighting - base case
Lighting Project |  | Base Case M&V Plan |  |  |  |  | indicates input parameter
Numerical inputs only | [6 empty] | indicates tool output
ECM Level
Project: A timed schedule lighting system will be retrofit with more efficient ballasts and occupancy sensors
Constant Load, Timed Schedule to change load and schedule
Energy Rate: | 0.1 | per kWh
Number of Usage Groups |  | 3
Usage Group Names |  | Population
| Offices | 1200
| Restrooms | 26
| Common Areas | 258
| Labor | Hours | Totals |  |  | Direct Costs: |  |  |  |  | Baseline | 714937.5 | kWh
Rate 1 | 65 | 80 | 5200 |  |  | Monitoring Equipment Cost | 2680.2934 |  |  |  | Post | 480511 | kWh
Rate 2 | 80 | 40 | 3200 |  |  | Other Equipment Costs | 5 | logger software |  |  | ECM Savings | 234426.5 | kWh
|  |  | 8400 |  |  | Travel and lodging | 200 | mileage, meals |  |  | Savings % | 32.79%
[6 empty] | Miscellaneous Costs | 175 |  |  |  | ECM Cost Savings | 23442.65
[7 empty] | 3060.2934 |  |  |  | ECM Savings Uncertainty (%) | 19.02%
M&V Method Level | [10 empty] | ECM Savings Uncertainty ($) | 4459.9581
Equation Selection |  | Esave = kWbaseHRSbase - kWpostHRSpost | [8 empty] | M&V Plan cost | 11460.2934
[11 empty] | Fract. M&V Cost | 48.89%
Number Operation Stages |  | 1
Data Collection Method Level
kWbase |  |  |  | HRSbase |  |  |  | kWpost |  |  |  | HRSpost
Offices | 0.123 | kW/fixture |  | Offices | 3840 | hours |  | Offices | 0.089 | kW/fixture |  | Offices | 3600 | hours
Restrooms | 0.123 | kW/fixture |  | Restrooms | 4650 | hours |  | Restrooms | 0.089 | kW/fixture |  | Restrooms | 2800 | hours
Common Areas | 0.123 | kW/fixture |  | Common Areas | 4200 | hours |  | Common Areas | 0.089 | kW/fixture |  | Common Areas | 3900 | hours
Data Collection Method: |  | Stipulation |  | Data Collection Method |  | Short-term monitoring |  | Data Collection Method |  | Stipulation |  | Data Collection Method |  | Continuous Monitoring
Variable Total Uncertainty Value |  |  | 3.061% | Number Samples per usage group |  |  |  | Variable Total Uncertainty Value |  |  | 3.061% | Number Samples per usage group
|  |  |  | CV | 0.5 | [6 empty] | CV | 0.5
|  |  |  | P | 10% | [6 empty] | P | 10%
|  |  |  | C.L. | 90% | [6 empty] | C.L. | 90%
|  |  |  | sample sizes: | n* | n | [5 empty] | sample sizes: | n* | n
|  |  |  | Offices | 67.6424 | 64.0329 | [5 empty] | Offices | 67.6424 | 64.0329
|  |  |  | Restrooms | 67.6424 | 18.781 | [5 empty] | Restrooms | 67.6424 | 18.781
|  |  |  | Common Areas | 67.6424 | 53.5917 | [5 empty] | Common Areas | 67.6424 | 53.5917
|  |  |  | Sampling Uncertainty |  | (68%) | Total U. |  |  |  |  | Sampling Uncertainty |  | (68%) | Total U.
|  |  |  | Offices | 6.079% | 5.102% | 5.704% |  |  |  |  | Offices | 6.079% | 5.102% | 5.102%
|  |  |  | Restrooms | 11.45% | 9.607% | 9.94% |  |  |  |  | Restrooms | 11.45% | 9.607% | 9.607%
|  |  |  | Common Areas | 6.676% | 5.603% | 6.156% |  |  |  |  | Common Areas | 6.676% | 5.603% | 5.603%
Data Collection Equipment Level
kWbase |  |  |  | HRSbase |  |  |  | kWpost |  |  |  | HRSpost
Selected Measurement Instrument |  |  |  | Selected Measurement Instrument |  |  |  | Selected Measurement Instrument |  |  |  | Selected Measurement Instrument
n/a |  |  |  | Onset HOBO light on/off |  |  |  | n/a |  |  |  | ACME K667
Relevant Uncertainty Values |  |  |  | Relevant Uncertainty Values |  |  |  | Relevant Uncertainty Values |  |  |  | Relevant Uncertainty Values
Ustip | (wattage table) | 6% |  | Uinst,prec |  | 0% |  | Ustip | (wattage table) | 6% |  | Uinst,prec |  | 0%
|  |  |  | Uinst,bias |  | 0% | [5 empty] | Uinst,bias |  | 0%
Variable Uncertainty (68%) |  | 3.061% |  | Usched,bias |  | 5% |  | Variable Uncertainty (68%) |  | 3.061% |  | Variable Uncertainty (68%) |  | 0%
Equipment Purchase Cost |  | 0 |  | Variable Uncertainty (68%) |  | 2.551%
Amortization Factor |  | 0 | [5 empty] | Equipment Purchase Cost |  | 0 |  | Equipment Purchase Cost |  | 210
Equipment Cost |  | 0 |  | Equipment Purchase Cost |  | 69 |  | Amortization Factor |  | 0 |  | Amortization Factor |  | 10%
|  |  |  | Amortization Factor |  | 10% |  | Equipment Cost |  | 0 |  | Equipment Cost (per point) |  | 21
|  |  |  | Equipment Cost (per point) |  | 6.9 | [5 empty] | Total Equipment Cost |  | 1739.0939
|  |  |  | Total Equipment Cost |  | 941.1995

## lighting calcs
lookup table of Z values
C.L. | Z
0.5 | 0.6745
0.68 | 1
0.8 | 1.2816
0.9 | 1.6449
0.95 | 1.96
0.98 | 2.5758
M&V Base Case
Baseline
Usage Group | Pop. | kW | DkW | HRS | DHRS | kWh | DkWh (%) | DkWh
Offices | 1200 | 0.123 | 0.0037653 | 3840 | 219.0434 | 566784 | 6.474% | 36692.2588
Restrooms | 26 | 0.123 | 0.0037653 | 4650 | 462.187 | 14870.7 | 10.4% | 1546.5877
Common Areas | 258 | 0.123 | 0.0037653 | 4200 | 258.5507 | 133282.8 | 6.875% | 9163.3311
[6 empty] | 714937.5 | total | 37850.7652
[7 empty] | rel. | 5.294%
Post
Usage Group | Pop. | kW | DkW | HRS | DHRS | kWh | DkWh (%) | DkWh
Offices | 1200 | 0.089 | 0.0027245 | 3600 | 183.6735 | 384480 | 5.95% | 22876.3713
Restrooms | 26 | 0.089 | 0.0027245 | 2800 | 268.9838 | 6479.2 | 10.08% | 653.2665
Common Areas | 258 | 0.089 | 0.0027245 | 3900 | 218.4984 | 89551.8 | 6.384% | 5717.26
[6 empty] | 480511 | total | 23589.0267
[7 empty] | rel. | 4.909%
M&V Plan 1
Baseline
Usage Group | Pop. | kW | DkW | HRS | DHRS | kWh | DkWh (%) | DkWh
Offices | 1200 | 0.123 | 0.0037653 | 3840 | 403.8961 | 566784 | 10.95% | 62088.6151
Restrooms | 26 | 0.123 | 0.0037653 | 4650 | 571.1203 | 14870.7 | 12.66% | 1882.3186
Common Areas | 258 | 0.123 | 0.0037653 | 4200 | 448.2076 | 133282.8 | 11.1% | 14797.0517
[6 empty] | 714937.5 | total | 78767.9854
[7 empty] | rel. | 11.02%
Post
Usage Group | Pop. | kW | DkW | HRS | DHRS | kWh | DkWh (%) | DkWh
Offices | 1200 | 0.089 | 0.0027245 | 3600 | 367.3469 | 384480 | 10.65% | 40960.0923
Restrooms | 26 | 0.089 | 0.0027245 | 2800 | 336.4007 | 6479.2 | 12.01% | 778.4313
Common Areas | 258 | 0.089 | 0.0027245 | 3900 | 404.1264 | 89551.8 | 10.36% | 9279.5511
[6 empty] | 480511 | total | 51018.0747
[7 empty] | rel. | 10.62%

## lighting - plan #1
Lighting Project |  | M&V Plan #1 |  |  |  |  | indicates input parameter
Numerical inputs only | [6 empty] | indicates tool output
ECM Level
Project: A timed schedule lighting system will be retrofit with more efficient ballasts and occupancy sensors
Constant Load, Timed Schedule to change load and schedule
Energy Rate: | 0.1 | per kWh
Number of Usage Groups |  | 3
Usage Group Names |  | Population
| Offices | 1200
| Restrooms | 26
| Common Areas | 258
| Labor | Hours | Totals |  |  | Direct Costs: |  |  |  |  | Baseline | 714937.5 | kWh
Rate 1 | 65 | 40 | 2600 |  |  | Monitoring Equipment Cost | 557.4407 |  |  |  | Post | 480511 | kWh
Rate 2 | 80 | 40 | 3200 |  |  | Other Equipment Costs | 5 | logger software |  |  | ECM Savings | 234426.5 | kWh
|  |  | 5800 |  |  | Travel and lodging | 100 | mileage, meals |  |  | Savings % | 32.79%
[6 empty] | Miscellaneous Costs | 175 |  |  |  | ECM Cost Savings | 23442.65
[7 empty] | 837.4407 |  |  |  | ECM Savings Uncertainty (%) | 40.03%
M&V Method Level | [10 empty] | ECM Savings Uncertainty ($) | 9384.6894
Equation Selection |  | Esave = kWbaseHRSbase - kWpostHRSpost | [8 empty] | M&V Plan cost | 6637.4407
[11 empty] | Fract. M&V Cost | 28.31%
Number Operation Stages |  | 1
[10 empty] | Benefit-Cost Ratio |  | -1.0211
Data Collection Method Level
kWbase |  |  |  | HRSbase |  |  |  | kWpost |  |  |  | HRSpost
Offices | 0.123 | kW/fixture |  | Offices | 3840 | hours |  | Offices | 0.089 | kW/fixture |  | Offices | 3600 | hours
Restrooms | 0.123 | kW/fixture |  | Restrooms | 4650 | hours |  | Restrooms | 0.089 | kW/fixture |  | Restrooms | 2800 | hours
Common Areas | 0.123 | kW/fixture |  | Common Areas | 4200 | hours |  | Common Areas | 0.089 | kW/fixture |  | Common Areas | 3900 | hours
Data Collection Method: |  | Stipulation |  | Data Collection Method |  | Short-term monitoring |  | Data Collection Method |  | Stipulation |  | Data Collection Method |  | Continuous Monitoring
Variable Total Uncertainty Value |  |  | 3.061% | Number Samples per usage group |  |  |  | Variable Total Uncertainty Value |  |  | 3.061% | Number Samples per usage group
|  |  |  | CV | 0.5 | [6 empty] | CV | 0.5
|  |  |  | P | 20% | [6 empty] | P | 20%
|  |  |  | C.L. | 80% | [6 empty] | C.L. | 80%
|  |  |  | sample sizes: | n* | n | [5 empty] | sample sizes: | n* | n
|  |  |  | Offices | 10.2656 | 10.1785 | [5 empty] | Offices | 10.2656 | 10.1785
|  |  |  | Restrooms | 10.2656 | 7.3598 | [5 empty] | Restrooms | 10.2656 | 7.3598
|  |  |  | Common Areas | 10.2656 | 9.8728 | [5 empty] | Common Areas | 10.2656 | 9.8728
|  |  |  | Sampling Uncertainty |  | (68%) | Total U. |  |  |  |  | Sampling Uncertainty |  | (68%) | Total U.
|  |  |  | Offices | 15.61% | 10.2% | 10.52% |  |  |  |  | Offices | 15.61% | 10.2% | 10.2%
|  |  |  | Restrooms | 18.37% | 12.01% | 12.28% |  |  |  |  | Restrooms | 18.37% | 12.01% | 12.01%
|  |  |  | Common Areas | 15.85% | 10.36% | 10.67% |  |  |  |  | Common Areas | 15.85% | 10.36% | 10.36%
Data Collection Equipment Level
kWbase |  |  |  | HRSbase |  |  |  | kWpost |  |  |  | HRSpost
Selected Measurement Instrument |  |  |  | Selected Measurement Instrument |  |  |  | Selected Measurement Instrument |  |  |  | Selected Measurement Instrument
n/a |  |  |  | Onset HOBO light on/off |  |  |  | n/a |  |  |  | ACME K667
Relevant Uncertainty Values |  |  |  | Relevant Uncertainty Values |  |  |  | Relevant Uncertainty Values |  |  |  | Relevant Uncertainty Values
Ustip | (wattage table) | 6% |  | Uinst,prec |  | 0% |  | Ustip | (wattage table) | 6% |  | Uinst,prec |  | 0%
|  |  |  | Uinst,bias |  | 0% | [5 empty] | Uinst,bias |  | 0%
Variable Uncertainty (68%) |  | 3.061% |  | Usched,bias |  | 5% |  | Variable Uncertainty (68%) |  | 3.061% |  | Variable Uncertainty (68%) |  | 0%
Equipment Purchase Cost |  | 0 |  | Variable Uncertainty (68%) |  | 2.551%
Amortization Factor |  | 0 | [5 empty] | Equipment Purchase Cost |  | 0 |  | Equipment Purchase Cost |  | 210
Equipment Cost |  | 0 |  | Equipment Purchase Cost |  | 69 |  | Amortization Factor |  | 0 |  | Amortization Factor |  | 10%
|  |  |  | Amortization Factor |  | 10% |  | Equipment Cost |  | 0 |  | Equipment Cost (per point) |  | 21
|  |  |  | Equipment Cost (per point) |  | 6.9 | [5 empty] | Total Equipment Cost |  | 368.3042
|  |  |  | Total Equipment Cost |  | 189.1365