Reference Drawing BOS-D-RTR-G102

- Change the second sentence in note 3 to read.  “The contractor shall determine size of circuit conductors fed from the EG van (see DWG E101) and identify to COTR”.

- Change Note 18 to read “not exceeding 6 inches…”

Reference Drawing BOS-D-RTR-C101

- See Site Plan: The contractor shall remove abandoned 2” Steel Conduit (abandoned), extending into proposed EG shelter placement, located at the 17’ x 28’-6” concrete pad

- See Site Plan, callout A8 is referring to entire site area.

- Change the second sentence in Note A13 to read “Asbestos may be present in the existing EG gaskets.

- Change Note A18 from “…¾ inch processed gravel…” to “…¾ inch minimum…”.

- Change Note A18 from “…98 percent maximum density…” to “…95 percent maximum density.

Reference Drawing BOS-D-RTR-C102

1	See Site Plan: The contractor shall remove the 2” Steel Conduit (abandoned) extending into proposed EG shelter placement area, located at the 17’ x 28’-6” concrete pad

- See Detail 2.  Contractor to remove safety bollards.

- See Detail A.  Pad to be 6” thick reinforced with wire mesh 6x6-W2.9xW2.9. 4000-PSI concrete.

- Change Note A2 to read, “Contractor shall replace the demolished concrete with bituminous paving to match existing”.

- Change the second sentence in Note A7 to read, “The 18” square, 12 “ deep stainless steel, lockable, hinged, watertight enclosure to transition fuel lines is GFM Installed.

- Change Note A9 to read “4” steel pipe hole thru the new shelter for fuel pipe exists.

- Change Note A18 to read.  “Contractor shall provide and install a new concrete apron at underground 600 gallon diesel fuel tank.  See drawing M104 for more information.  Coordinate with COTR.”

- Change NOTE A19 to read:  “Provide, install, maintain, service, and fill for the duration of the project, a temporary 300-gallon double-wall steel fuel tank.”

Reference Drawing BOS-D-RTR-C103

- See detail B; A vapor barrier is required under the 2” Rigid Insulation.

- Conduit trench work shown in detail 3 is required under this contract.

- Change notes A4 and A6 to 4000 PSI in accordance with Division 03300.

Reference Drawing BOS-D-RTR-C104

- Detail A, B, D: Air Terminal should read:  48” Blunt Tip, Air Terminal (TYP).  See sheet E105.

- See Detail C, Stainless steel transition for fuel lines to UST is GFM.

Reference Drawing BOS-D-RTR-E101

- NOT SHOWN – A Feeder presently exists from the MPA 75 KVA transformer to FAA CMU building.  Power shall be available at all times.

- NOTE C7 should read as the following: Contractor shall provide necessary secondary connections (conduit and cable) of the 7.5 KVA (GFM) transformer, single phase, 120/208-480Vac for the new PAPI feed (not shown).  (Transformer is GFM installed).  See Sheet E106.

Reference Drawing BOS-D-RTR-E102

- NOT SHOWN – A Feeder presently exists from the MPA 75 KVA transformer to FAA CMU building.  Power shall be available at all times.

- Change note B2 to read: Contractor shall provide and install a temporary fuel tank.  See Mechanical Drawings.  Delete reference of the 72 hours of temporary fuel.  See drawing BOS-D-RTR-C102.

- Change note B9 to read: Contractor shall see sheet M101 and sheet C102 for temporary fuel tank requirements.

Reference Drawing BOS-D-RTR-E103

- Change note A2 to read:  Contractor shall provide and install fuel lines to day tank.  (GFE INSTALLED)

- Change note A12 from ¾” to 1” in accordance with drawing M101 Note A14.

- Reference Note A22.  Contractor shall install the Veeder Root Fuel monitoring system (GFM).  The contractor shall hire the services of the Manufacturer’s Representative to start and setup.  See Note A14 on drawing M101.  Contractor is not required to purchase unit.

- Contractor shall provide work identified under Note A5.  Contactor shall provide and install a neutral bond to the earth electrode system (counterpoise).

- Delete note A8, not required.

Reference Drawing BOS-D-RTR-E106

- Change the last sentence in Note C2 to read as; See Note 3 on DWG BOS-D-RTR-G102 and Note C5 on DWG BOD-D-RTR-E101.

Reference Drawing BOS-D-RTR-M101

- Disregard the first sentence of Note A9 and change to read as Provide and install ¾” fuel supply and ¾” return lines inside 4” secondary containment pipe to underground storage tank.  See DWG BOS-D-RTR-C102 for tank pipe location.  Stainless Steel Transition Box is “GFM Installed”.

- Change first sentence of Note A11 to read, “Contractor to provide and install new vent from underground fuel storage tank.”

Reference Drawing BOS-D-RTR-M104

- Change Note 1 to read as: ¾” supply and return fuel lines (OPW Pisces type or approved equal) in 4” FRP secondary containment.  Supply elbows and fittings of schedule 40 black iron, as necessary.  Fuel lines shall be continuous from underground sump to building entry.