Prepared by the United States Bureau of Land ManagementCentral Yukon Field Office

STATE OF ALASKA

Approved: _______________________________________   _________________

Central Yukon Field Manager			  Date

LIVENGOOD COMMUNICATIONS

SITE PLAN

I.	INTRODUCTION	2

A.	Terms and Definitions	2

B.	Purpose	3

C.	Site Description	3

D.	Area Served	3

E.	Access	3

F.	Site History and Development	4

G.	Goals and Objectives of Site Management Plan	4

II.	AUTHORITY AND DIRECTION	4

A.	Authority	4

B.	Relationship to Communications Site Lease	5

III.	GENERAL RESPONSIBILITIES	5

A.	The Bureau of Land Management retains the responsibility for:	5

B.	Facility Owners and Facility Managers (or their designated representatives)                                	are responsible for:	5

C.	FCC and NTIA are responsible for:	6

IV.	AUTHORIZED USES AND USERS WITHIN A FACILITY	7

A.	Use by Multiple Users	7

V.	    RENTAL	7

VI.	General Operation and Maintenance Direction	7

A.	Unique Resource Considerations at this Communication Site	7

B.	Wiring and Grounding	8

C.	Equipment	8

D.	Cables and Transmission Line (Wave Guides)	10

E.	Radiation	11

F.	Utilities-Availability of and Requirements for:	11

G.	Sanitary Facilities	…………………………………12

H.	Security And Law Enforcement	12

I.	Site Maintenance	13

J.	Inspections	13

K.	Fire Prevention and Hazard Reduction Requirements	14

L.	Access Maintenance and Restrictions	14

VII.	CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION	15

A.	Responsibilities	15

B.	Construction Methods and Resource Protection	16

C.	Construction Inspection	16

D.	New or Remodeled/Expanded Buildings	17

E.	New or Remodeled/Expanded Towers	19

VIII.	SITE ASSOCIATION/ADVISORY GROUP	19

IX.	APPENDICES	20

INTRODUCTION

## Terms and Definitions

The terms used in this communication site plan conform to the definitions in 43 CFR 2801.5 and clarifications provided in Bureau of Land Management Handbook 2860-1.  In the event of a conflict, between the plan and these sources, the CFR and the Bureau of Land Management Handbook will govern.

The words “lease” and “lessee” as used in this plan refer to the relationship between the Bureau of Land Management and the communications use leaseholder, the lessee.  The words “customer” and “tenant” refer to the relationship between the lessee and the occupants in the lessee’s facilities.

LEASE – An authorization issued to a communication facility owner or facility manager, allowing for the use of public lands to construct and or operate a communications facility and unless specifically prohibited, to sublease to occupants in that facility.

LEASEHOLDER OR LESSEE – Facility Owner/Facility Manager

CUSTOMER – Entity that pays a facility owner, facility manager or tenant for communications services and are not re-selling or broadcasting communications services to others

TENANT – A communications user who rents space in a communications facility and operates communication equipment for the purpose of re-selling, or broadcasting communications services to others for profit.

COMMUNICATIONS SITE – An area of Bureau of Land Management administered public land designated through the land and resource management planning process.  A communications site may be limited to a single communications facility, but most often encompasses more than one.  Each site is identified by name; usually a local prominent landmark, such as Livengood Communications Site.

FACILITY MANAGER – The holder of a Bureau of Land Management communications use authorization who leases space for other communication users.  A facility manager does not directly provide communications services to third parties.

FACILITY OWNER – Individual, commercial activity, organization, or agency that owns a communication facility on Federal land; own and operate their own communications equipment; and hold a communication use authorization.

NON-BROADCAST – This category includes Commercial Mobile Radio Service (CMRS), Facility Managers, Cellular Telephone, Private Mobile Radio Service (PMRS), Microwave, Local Exchange Network, and Passive Reflector.

BROADCAST – This category includes Television Broadcast, AM and FM Radio Broadcast, Cable Television, Broadcast Translator, Low Power Television, and Low Power FM Radio.

## Purpose

This plan is intended to be used by Bureau of Land Management officials administering communication uses at Bender Mountain, existing lessees, and applicants desiring a lease or a lease amendment.  The plan will be kept updated by amending pages or sections of the plan rather than issuing a revised edition of the plan.  When a revision is necessary, the plan will be amended by letter from the Central Yukon Field Office Manager enclosing a copy of revised pages or sections.  The amendments will be consecutively numbered.

General management direction for all land use is outlined in the Fairbanks North Star Borough Regional Comprehensive Plan on September 13, 2005 (Ordinance No.2005-56), the Code of Federal Regulations (CFR), the BLM Handbook, and applicable Instruction Memoranda.  Specific direction for site management planning on designated communications site is contained in BLM Handbook 2860-1.  Primary regulations and policy pertaining to issuance of rights-of-way and leases by the Bureau of Land Management are found in 43 CFR Sections 2801-2809 and BLM Handbook 2860-1.

Primary management of the current site is to assure integrity of the historical broadcast uses.  Non-broadcast uses may be authorized as tenants or customers with the provision that they can be designed and filtered to operate on a non-interference basis within the broadcast environment.

A communications site management plan was approved for this site in 1985.  This plan has technical standards for better management of the Bender Mountain communications site as well as updated references to current policy, rules, and regulations.  This plan governs development and management of Bender Mountain and will be modified in the future as needs and conditions warrant.  Any future such uses must be designed, installed, operated, and maintained to be compatible and not interfere with the primary uses.  This site-specific plan is administrative in nature and is Categorically Excluded from further review under the National Environmental Policy Act (NEPA) (516.DM2, Appendix 1,1.7).  Any additional development of the site will be addressed in a site-specific NEPA document.

## Site Description

The site is located on a ridge point northeast of Money Knob and southeast of Livengood on lands administered by the Central Yukon Field Office.  It is located in portions of excluded mining claims in Section 23, Township 8 North, Range 5 West Fairbanks Meridian, at approximately 65º 30’42” North Latitude and 148º 30’ 32” West Longitude.  The elevation of the Livengood Communication Site is approximately 1850 feet above mean sea level. A site map is provided as Appendix A.

## Area Served

This site does not serve a Ranally Metro Area (RMA).  The population of this unincorporated area is less than 25,000, which may be adjusted annually based upon changes in population and growth.  This information will be used for rental determination.

## Access

Access to the site is via an unnamed road which intersects the Old Elliott Highway just west of Olive Creek, then north at the Hudson mining claim and over Money Knob to the site.  The communication grant includes a 20’ x 4,500’ foot road right-of-way grant for this access road and its maintenance.

## Site History and Development

Livengood communications site was developed by the Alaska Department of Transportation and public facilities and a grant was issued to them in 1995.  The grant also includes a 5,000’ power and communication line running from the Highway maintenance station in Livengood to the communications site.  The site also has a 200’ diameter helicopter pad located south of the building.

Additional space is available for other facilities at this site.  Any new facilities or modification of existing facilities must be done according to the application and appropriate NEPA process preferred to later in this plan.

## Goals and Objectives of Site Management Plan

1.	Livengood Site will be managed as a low-power radio and microwave site.  No broadcast uses will be allowed.  Other low power non-broadcast uses may be considered if deemed to be compatible with the senior uses.

2.	Communication equipment on Livengood Site will be managed to be consistent with the Comprehensive Plan guidelines as viewed from the Elliott Highway.  The maximum tower height to meet visual objectives is 85 feet.

3.	The overall appearance of the site and the integrity of the natural environment will be improved through stringent maintenance requirements and selection of authorized paint colors.

- The site will be systematically developed to maximize the number of compatible uses while ensuring safety and protection of resources.  New development is not anticipated until existing facilities are utilized to their optimum capacity.

- Encourage a Livengood Users Association which includes all uses on BLM, private, and State lands.

- New facilities will be developed only after appropriate site-specific NEPA analysis and coordination with current lease holders and users.

AUTHORITY AND DIRECTION

## Authority

Bureau of Land Management authority to authorize communications uses on public (BLM) land is granted by the Federal Land Policy and Management Act of 1976, 90 Stat. 2776 (43 U.S. C. 1761-1771) and is reflected in Title 43, Code of Federal Regulations (CFR), Sections 2801- 2803

and WO IB 98-23.

Bureau of Land Management authority for communications site management planning is contained in Bureau of Land Management Handbook 2801-1, Plan of Development.  Direction on and policy for communication use authorizations is contained in Bureau of Land Management Manual (BLM Manual) section 2860.

Authority for the issuance of authorizations and/or licenses for the transmission and reception of electronic radiation for communication purposes is granted by Congress and administered by the Federal Communications Commission (FCC) and/or the National Telecommunication and Information Administration (NTIA).

## Relationship to Communications Site Lease

This site plan will be incorporated into all leases now and in the future issued for this communications site and must be used in conjunction with the lease. PROVISIONS OF THE SITE PLAN ARE ENFORCED THROUGH THE LEASE. Each lessee is expected to include the requirements of the lease and the site plan into any documents, which describe the business relationship between the lessee and the lessee's tenants and customers. The lessee is responsible for enforcing those provisions.

GENERAL RESPONSIBILITIES

## The Bureau of Land Management retains the responsibility for:

Issuing and amending leases and existing rights-of-way to facility owners and facility managers, only for the areas actually occupied by the authorized improvements.  Granting occupancy and use of public lands rest exclusively with the Bureau of Land Management (43CFR Sections 2801-2803)

- .  The issuance of a FCC license (authorization), or frequency assignment, does not authorize occupancy of public lands.

1.   Approving any new/modified facility(ies) at the site.

- Approving amendments to leases to qualified buyers of facilities on the site.

## Facility Owners and Facility Managers (or their designated representatives) are responsible for:

- Complying with their authorization and all sections of this Site Management Plan.

- Ensuring that all new facilities, expansions, or improvements are consistent with future Resource Management Plans, RMP; any environmental document(s)/decisions for the site; and this Site Plan.

- Ensuring facilities/equipment not complying with Federal/State/local laws/regulations/ ordinances will be removed or modified within one year of the approval of this plan.  Any modification needs pre-approval by the Bureau of Land Management.

- Keeping all facilities within the established limits of their authorized area.

- Providing the Bureau of Land Management, with the name, address and phone number for a local contact person.  The Facility Owner and Facility Manager and the contact person may be the same individual.  The contact person will be available for emergencies and will have the authority to make decisions about construction issues, facility maintenance and all equipment within the facility.

- Adhering to the terms of the Facility Owner/Manager Lease or Right-of-Way:

  - Facility Owners and Facility Managers are authorized to rent building/tower space to tenants and/or customers without prior written approval from the Bureau of Land Management.

  - Tenants and/or customers may not construct their own equipment shelter (building, shelter or cabinet) or antenna support structure (tower or mast).  The facility owner/manager must own all communication shelters and towers under their lease. [If that is not possible, a separate SF-299 application, cost-recovery deposit, analysis, and authorization are required.  This will also result in the use being a tenant/customer of the original lease holder in additional to being a separate facility for billing purposes.]

  - Tenants and/or customers using a facility covered by a Facility Lease/right-of-way will not have separate Bureau of Land Management permits to authorize the use.

  - Facility Owners and Facility Managers are responsible for complying with the terms and conditions of the Facility Lease or their valid right-of-way.  Facility Owner/Managers are also responsible for ensuring that their tenants and customers are in compliance with the terms and conditions of the Lease or right-of-way, and applicable FCC or NTIA license terms and conditions.

  - The Facility Owner and Facility Manager may not place any unreasonable restrictions nor any restriction restraining competition or trade practices on tenants and/or customers, or potential tenants and/or customers.

- Ensuring that all communications equipment is properly installed, operated, and maintained.

- Ensuring that all communication equipment meets ANSI, FCC and Bureau of Land Management regulations, guidelines and standards concerning radiation limitations.

  - Monitoring radiation levels at their facility and;

  - Immediately correcting any radiation levels that are, or could be a hazard to human health. (FCC 47CFR sections 1.1307(b), 1.1310 and 2.1093) and FCC OET Bulletin 54, August 1999.

- Providing a certified copy of their use and the category of use along with the current phone numbers and addresses of all tenants and customers as of September 30 each year.  This report is due by October 15th.

- Keeping the premises around their buildings free of trash and debris.

- Placing the lessee/right-of-way holder’s name, address, phone number, and authorization number on the door of their communication site building.

## FCC and NTIA are responsible for:

The responsibilities of the FCC and NTIA are frequency management.  Correcting interference problems is the responsibility of the affected licensees.  The FCC and NTIA are not normally responsible for the resolution of conflicts when the licensees or agencies are operating within the limits of the authorizations.

AUTHORIZED USES AND USERS WITHIN A FACILITY

## Use by Multiple Users

Development of any new facilities which are proposed after existing facilities are fully utilized must be designed for more than one user. This includes multiple use of buildings, towers, back-up generators, grounding systems, fuel containers, access ways and parking areas.

Facility Owners and Facility Managers are not required to lease facility space to others if they can prove to the authorized Bureau of Land Management officer that:

- Space is not available;

- The use is incompatible with the existing facilities;

- Additional space is needed by the facility owner/manager;

- Additional users would violate system security needs; or,

- Potential interference is not resolvable.

RENTAL

Pursuant to 43 CFR 2806.30, Facility Owners and Facility Managers shall pay annual rental based on the Rent Schedule for Communications Uses on Public Lands as adjusted annually.  Since this site is not within an established RMA, the population zone less than 25,000, will be used for these calculations until the RMP designation changes.

Fees that Facility Owners and Facility Managers may charge their tenants and “customers” are to be: reasonable (consistent with, and not in excess of, other fees for similar facilities) and commensurate with the uses and occupancy of the facilities and services provided to tenants and “customers” and

General Operation and Maintenance Direction

## Unique Resource Considerations at this Communication Site

- There are no currently identified special resource coordination considerations with on-site or adjacent resource values.  Should special conditions arise through the revision process of the RMP, this plan will be amended accordingly.

## Wiring and Grounding

1.	All equipment is to be installed within existing buildings and on equipment racks that are grounded and shielded.  Grounding is to be installed in accordance with accepted standards.

2.	All electrical wiring and grounding must meet the ‘National Electrical Code” and applicable estate codes.  All permanent wiring shall be installed in metallic conduit.  Surge protection shall be installed on all power distribution panels.

3.	Lightening protection “down” conductors installed upon communications towers shall be treated as “Transmission lines”.  Therefore, they shall have an insulating jacket.  Periodic bonding of the down conductor to the tower (Galvanized) steel shall be made with proper bonding connectors that are tin plated or made of brass.

4.	Each building is to have its own separate grounding system for all users in that structure.  Wherever practical, interconnection of individual grids and/or the simultaneous placement of a large sized copper ground wire with any new grounding systems that are buried on the site will be required.

5.	Site or facility grounding must be constructed of copper, with #2 AWG or larger wire or 2” or larger solid copper strap, connected to an adequate site/facility ground electrode system.  The site/facility ground electrode system shall be bonded to the power service entrance grounding electrode conductor.  Guy wires should also be grounded using manufacturers approved methods to preclude bi-metallic junction and corrosion.  All equipment on the site (buildings, towers, power units, transmitters, receivers, antennas, combiners, telephone systems, power cabinets, HVAC units, etc) must be connected to the site/facility ground by direct connection.  Electrical system ground wiring is required for electrical ground fault protection and circuit breaker coordination.  The grounding systems shall comply with applicable laws, codes and in accordance with standard engineering practice.  Below ground connections must use either an exothermic welding process (i.e. Cadweld, Thermoweld, etc.), copper wedge pressure devices (i.e. Ampact, Wrench-lock, etc.), or brazed copper connections in conjunction with a mechanical UL listed connector (to be used as a physical strength enhancement component).  Brazing by itself is not an acceptable method of bonding below earth grade (buried).

## Equipment

Equipment Ownership

All equipment shall be labeled with:

- The owner’s name;

- Transmitter frequency(ies);

- A valid FCC, or NTIA authorization;

- Transmitting power output(s); and

- A current 24-hour phone contact number.

Transmitting Equipment

All transmitters will have protective devices (shields, filters, isolation components), designed into or externally installed, to prevent interference with other users.  All transmitters will meet FCC licensing requirements.

The re-radiation of intercepted signals from any unprotected transmitter and its associated antenna system will be prevented by the use of appropriate filters (wide band and narrow band broadcast transmitters).

The direct radiation of out-of-band emissions (i.e. noise or spurious harmonics) will be reduced to a level such that they may not be identified as a source of interference as defined in the FCC Rules and Regulations (e.g. Part 90.209(e)).  If site noise (electromagnetic noise) becomes an issue, noise threshold limits will be established, and amended into the Site Plan.

All transmitters not in immediate use and not specifically designated as standby equipment shall be removed.  Loads connected to circulators are to be capable of dissipating the total power output of the transmitter.

Receiving Equipment

A bandpass device (cavity, crystal filter, etc.) is recommended at the input of all receiving devices.  Cavity filters, or other protective device, may be used at receiver inputs to reduce interference.

Where duplexing is used, use of the notch type device should be avoided.  In situations where a notch type device is used, a bandpass filter must be used with the transmitter.

Tower

- Generally only one tower is authorized for each facility owner.  Facility Owners and Facility Managers may obtain permission to construct the second tower only after submitting evidence that demonstrates that their existing tower(s) is/are completely filled and full use has been made of combining systems.  When a single equipment building is required, multiple antenna support structures may need to be designed and authorized to accommodate all uses without interference.

- All towers will be left unpainted, if they are dull, galvanized steel.  Paint is required, only if they have a shiny (i.e. reflective) surface.  Only non-reflective, Bureau of Land Management approved dark gray to green colors will be approved unless FCC requires red/white striping.  All towers will be treated for low to non-reflectance.

- Only lights, beacons or strobes specifically required by the FCC will be allowed on towers (including antennas).

- The maximum tower height for this site is 85 feet.

Antennas

            - Microwave (dish) antennas (other than ground mounted satellite dishes) will be limited to a maximum of ten (10) feet in diameter.  Smallest diameter dishes are preferred if technically feasible.

            - All antennas must meet all OSHA safety standards.  If an antenna exceeds FCC public or occupation standards (see FSS OET Bulletin 57), it will be remedied within 24 hours after measures are taken or isolated (e.g., fencing, signing, relocation, lowering power levels are all possible remedies).  Ground measurements of Radio Frequency Radiation, RFR, levels will be taken before mitigation measures are implemented.

            - Color(s) for dish antennas, or covers, must be pre-approved by the Bureau of Land Management.  White dish antennas and/or covers will not be approved.  Existing white dishes and covers must be repainted or replaced with grey as repairs or replacement become necessary.

Interference

The responsibility for correcting interference problems is a matter for resolution between the permit/lease holder of the facility(ies), the user causing the interference, and the affected party(ies).  Generally, the first users on a site have seniority with respect to the resolution of interference complaints.  Senior holders have an obligation to maintain their equipment to industry standards, to operate their systems in accordance with the terms of both the FCC license and NTIA frequency authorization, and to comply with the Bureau of Land Management authorization.  New users on a site must correct, at their expense, interference problems that they create.  They must cease operation of the suspect equipment until the problem is corrected.  If interference problems cannot be resolved or corrected within a reasonable time, the new use that is causing the interference may be terminated and the equipment removed.

The Bureau of Land Management does not have authority for correcting interference problems, but can act as a mediator to help all affected parties.  Interference problems must be coordinated with the FCC or NTIA, whichever is appropriate.

Interference with law enforcement and/or emergency communications must be corrected immediately.  The operation of equipment covered by this Site Plan shall not interfere with United States Government radio or electronic operations already in existence on public land within two (2) miles of the site to which this authorization refers.  The user causing this interference, shall, at its own expense, take all action necessary to prevent or eliminate such interferences.  If it does not eliminate such interference within ten (10) days after receipt of notice from the Bureau of Land Management to do so, this use will be terminated.

If electromagnetic noise becomes an issue, noise thresholds will be established and appended to this Plan.

## Cables and Transmission Line (Wave Guides)

All new cabling will be jacketed and shielded and shall either be flexible or semi-rigid type.  Existing substandard cables will be upgraded as repairs or replacement become necessary.

Cables will be properly installed and will be strapped and fastened down.

All transmission lines (wave guides) are to be supported in accordance with manufacturer’s specifications.

Unjacketed transmission line of any type is prohibited. No transmission lines shall be left unterminated.

Double shielded braided, or solid shielded cable will be used.  No RG-8 type cable is permitted.  No connector-type adapters will be used on transmission lines.  Only correct connectors that will mate to connected devices are to be used.

## Radiation

All communications uses must meet ANSI, FCC and Bureau of Land Management regulations guidelines and standards concerning radiation limitations.

Monitoring radiation levels at the site is the responsibility of all site users and will occur at intervals to comply with FCC regulations and guidelines.  A copy of the monitoring report will be provided to the Bureau of Land Management within 30 days of its completion.

Onsite RFR measurements will be taken using appropriate equipment that can adequately measure both on-tower and on the ground levels before mitigation measures related to RFR are implemented.

Security fences with RFR notice signs are required around areas that exceed public use levels.  All fencing location and design will be pre-approved by the Bureau of Land Management.

Warning signs will comply with ANSI C95.2 color, symbol, and content conventions.  Contact information including name and telephone number will also be included on warning signs.

Lowering power levels for on-tower access during maintenance will be coordinated between affected users.

Any identified RFR radiation problems that are, or could be, a human health hazard must be corrected within 24 hours after measurement tests have been completed or be removed from the site by the site user(s).  If the proposed corrective action involves any new ground disturbance, it must be pre-approved by the BLM.

## Utilities-Availability of and Requirements for:

Commercial Electrical Power

Power is provided to the site under the grant issued to AKDOT&PF.  The distribution line and portions of the service drops are on the ground surface.  These lines must meet the appropriate applicable electrical code for it installation, operation, and maintenance.  Future service drops or modifications will be buried.

Telephone Service

No commercial telephone service is available; cell phone coverage does not extend to this area.  AKDOT&PF provides telephone service to itself by this site under the communications ROW grant.

Fuel Tanks

All facility owners are responsible for providing fuel storage (propane and diesel) and emergency power for their tenants.  No tenants will be authorized their own fuel tank and/or generator.  Fuel storage will preferably be consolidated into a tank large enough in size to accommodate all tenants by each facility owner.  At a minimum, tanks will be grouped together in a consolidated area adjacent to their facilities.  All fuel, storage tanks (e.g. LPG, propane and diesel) must meet current fire department, Federal, State and Borough safety and hazardous materials requirements.

- All tanks will be:

a.	Signed in red letters, “SMOKING OR OPEN FLAME PROHIBITED WITHIN 20 FEET”;

b.	In conformance with National Fire Protection Association (NFPA) requirements; and,

c.	Painted an approved color, or screened by an enclosure to blend in with the natural environment.  (If an enclosure is used, it must be pre-approved and painted an approved color).

2.	Diesel tanks will also be:

a.	Enclosed in Bureau of Land Management and fire department approved secondary containment vaults that are painted a Bureau of Land Management approved color.

b.	Constructed with underground fuel lines.  Fuel line must be constructed of black, treated pipe and fittings, and must be posted.

## Sanitary Facilities

1.	Plans for any new sanitary facilities must be pre-approved by the Bureau of Land Management.  If it is determined by the Bureau of Land Management that the user needs such facilities, they will be provided by the applicant/holder in a manner and location satisfactory to the Bureau of Land Management and within the requirements of the Occupational Safety and Health Administration (OSHA).

## Security and Law Enforcement

The Alaska State Troopers are the key law enforcement agency for the area.  They are responsible for most civil and criminal matters.  The Bureau of Land Management will be responsible for enforcing matters related to uses of BLM lands (e.g. resource protection issues).

Patrol and policing for security purposes is the holder’s responsibility.  If holders desire to have the protection of extra fencing, Bureau of Land Management approval must be obtained first.  To reduce visual clutter and efficiently utilize existing space, fencing groups of buildings will be encouraged.

Gates must be adequate for Bureau of Land Management and firefighting access needs.

Fencing

No facilities currently have perimeter fencing.  If future facilities determine that fencing is desirable, they must meet the following criteria:

1.	All fences must meet health and safety requirements.

2.	All fence locations and design require Bureau of Land Management pre-approval.  The standard fencing type will be chain-link (i.e. cyclone).

3.	The standard fence height will be eight (8) feet.

4.	Fencing will be designed and of a type to minimize interference issues.

5.	Fences will be signed with RFR notices if RFR is above public levels.

## Site Maintenance

The objective of maintenance activities is to present a clean, neat, and orderly appearance at the site and have all of the authorized improvements safe for workers and the public.  All users will keep up the overall appearance of the site.

Miscellaneous debris remaining after any construction and/or equipment installation, removal or modification, is not only a hazard, but can cause interference or intermodulation problems.  In particular, all loose wire or metal objects are to be removed from the site.

The users of the Site will remove all graffiti within 10 working days of finding it.  If graffiti is on natural features (e.g. rocks), the graffiti will be removed in a method approved by the Bureau of Land Management Authorized Officer.

Holders will not be permitted to leave or dispose of trash, garbage or cut brush on public lands.  No outside trash or litter containers will be provided.  Site users (i.e. holders) will remove litter from the site as it is produced.

Policing of litter in common areas (i.e. areas between buildings and developed sites) is the shared responsibility of those holders bordering these areas.

During construction and/or maintenance, paintbrushes will not be cleaned off on the rocks around the site and excess materials (e.g. cement) will be removed from public lands.

Peeling paint on buildings and/or towers will be re-painted within ten (10) days of notification of the holder by the BLM.

## Inspections

Unless waived in writing by the Bureau of Land Management, the holder is to provide, annually, a certified inspection of the facilities and equipment covered by the authorization.  The inspection will include technical review that assures that authorized equipment is operating within the specifics of this Site Plan, the FCC authorization, ANSI Standards, and the manufacturer’s specifications.  In addition, the inspection must assure that the authorized equipment is secure, free of rust, properly grounded, and otherwise properly operated and maintained.  This inspection should also review general good "housekeeping". A copy of the inspection report, certified by a telecommunication specialist, is to be provided to the Bureau of Land Management within 30 days of completion.  Appendix D provides an example of the inspection checklist.

The Bureau of Land Management may also conduct un-announced periodic reviews to monitor for authorization compliance.

## Fire Prevention and Hazard Reduction Requirements

Facility owners and managers will be required to maintain to mineral soil, a minimum of thirty (30) feet clearance around their buildings and a minimum of ten (10) feet clearance around any propane tanks.  Identified threatened, endangered, or sensitive plant species must remain within the minimum clearance areas.

Smoking is prohibited while walking in flammable vegetation.

The roof structure shall be kept reasonably clear of leaves, twigs, and other debris at all times.

No explosive will be stored at this site.  Flammable materials shall be stored in conformance with the requirements of local fire regulations.  Flammables will be placed in closed containers and stored away from sources of ignition and combustible materials.  If flammables are stored within a building, the building will be locked, properly signed and well ventilated.

Approved spark arresters will be required and maintained on all internal combustion engines.

At least one (1) U.L. rated 40 B:C dry chemical fire extinguisher is required inside each building.  Prior to each June, fire extinguisher(s) shall be inspected and refilled by holders, if necessary.

Any fire will be immediately reported to 911 or the Alaska Interagency Fire Coordination Center at 1-800-237-3633.

Fire prevention inspections are made by Bureau of Land Management Officers.  They will call to your attention any lack of compliance with the above regulations, plus any other existing hazards.  Compliance with these inspections is required within the time limits specified.

All fire protection standards must be accomplished by the beginning of fire season unless otherwise agreed to, and then maintained throughout the fire season.

For new construction, the Bureau of Land Management will provide the Holder with a separate Construction Fire Plan which will be prepared at that time as applicable.

## Access Maintenance and Restrictions

Roads

The holder is responsible for the access road from the Hudson mining claim to the site.  Holders who damage or disturb the access road, or any associated structures, such as ditches, culverts, roadside vegetation, signs and/or underground utilities or facilities, will be required to repair the road or associated structures to conditions equal to or superior to those prior to any damage or disturbance.  These actions may require a new NEPA analysis.

Interior Site Driveways/ Parking Areas

Roads within the communications site will be maintained by the site users.  Interior roads will be planned and approved during establishment of new facilities.  Interior roads will be maintained in a manner to allow only one entrance to the site.  The intent is to discourage off-road vehicle use in and around the site.

Road Closures

Native surface roads are subject to periodic closures to entry during periods of extreme fire danger, inclement weather, or wet conditions.  Authorized site users may use the site during these periods, but should use judgment and may need to seek advance approval from the Bureau of Land Management.

CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION

## Responsibilities

In addition to the responsibilities listed in Section III, New Facility Owners and Facility Managers are responsible for:

1.	Submitting a complete application to the Central Yukon Field Office prior to any new construction, or modifications to existing improvements (ATTN: “Realty Specialist”).  The application must include:

a.	The appropriate Cost Recovery fees in connection with the application.

b.	A copy of the approved Site Plan Base Map showing all of the proposed (new) facilities including structures, towers, and auxiliary equipment;

c.	Completed drawings/plans prepared by a registered engineer and approved by the Bureau of Land Management;

d.	Identification of any microwave beam paths, a plot of their azimuth(s), and their proposed elevation(s) on the tower;

e.	All proposals must include documentation that shows that proposed facilities will not be obstructing, or interfering with, any existing fixed point to point antennas, omni directional broadcast antennas, or microwave beam paths in the directions of primary population targets.  Proposed beam path needs must be shown on Site Plan Base Map;

f.	Any needed recommendations, changes or modifications to their original proposal, based on any required resource surveys and/or reports.

2.	Demonstrating that their proposals for new facilities will not cause undue interference with any existing uses. The applicant has the burden of proof to demonstrate that they will not cause undue interference with any existing uses.  In addition, it is the applicant’s responsibility to show that any new facilities will make the most efficient use of the limited amount of space at the site.

3.	Evidence that their proposals will provide for future users without additional construction, if possible.

4.	Providing engineering and geotechnical investigations for development of specific foundation designs and grading plans.

5.	Providing an Erosion Control Plan prior to construction activities.  At a minimum, the Erosion Control Plan must include: sediment control, stipulations that cut/fill slopes will be graded and contoured to prevent erosion and/or excessive runoff, and recommendations for temporary erosion control measures, (e.g. netting, silt fences, swales, and/or sediment collection areas).

6.	Coordinating with other Federal (e.g., FCC and FAA), State and Borough agencies and obtainment of all required approvals and/or permits.

7.	Providing 30-day notice to all facility owners/managers at the site, as well as the Bureau of Land Management, of all new frequencies proposed for the site.  A completed BLM technical data sheet or equivalent must be sent with the 30-day notice to allow for comment of potential interference.  This would be for new frequencies for themselves and their tenants.

8.	Insuring that all written approvals have been obtained from the Bureau of Land Management prior to construction.

## Construction Methods and Resource Protection

Plans submitted by an applicant for any new construction or modifications shall specify provisions for soil rehabilitation measures including, but not limited to, soil replacement and stabilization and for proper handling of runoff from buildings, parking area, access roads, and undeveloped common areas.

The following methods and resource protection measures will be required to minimize impacts during construction:

1.	Avoid and protect sensitive resource areas, as identified by the Bureau of Land Management.

2.	Compliance with the Erosion Control Plan.

3.	During construction and/or maintenance, paintbrushes will not be cleaned off on rocks around site and no marks of any kind (including survey marks) will be permitted on rocks.

4.	Minimize ground disturbance and vegetation removal as much as possible during construction activities.  All ground-disturbing activities require Bureau of Land Management pre-approval.

5.	Any extensive cut and fill slopes will be re-vegetated with vegetation species approved by BLM as soon as possible after construction.  All re-vegetation requires Bureau of Land Management pre-approval. If necessary, reseeding will be required until vegetation is successfully established as determined by the Bureau of Land Management.

6.	No grading material will be cast off during construction/reconstruction activities. Excess soil can be used for fill material on road and/or building/tower pads.

7.	Temporary, on-site storage of construction materials will require pre-approval by the Bureau of Land Management.

8.	Construction materials and supplies, except for hazardous materials (see number 10. below) may be left unattended at the construction site at the end of each workday, but at the owner’s risk.

9.	Hazardous materials, including, but not limited to all fuels, oils, and lubricants are not to be left unattended at the site at any time.  During construction, these materials are to be removed from the site at the end of each workday, or temporarily stored inside a locked and signed building until the following workday.

10.	All surplus construction materials and/or waste debris must be removed from the site no later than thirty (30) days after construction has been completed.

11.	Any earth moving or heavy equipment (e.g. dozers, graders, cranes, backhoes, etc.) leaving the designated roadway and/or approved parking area(s) to perform authorized activities at the site, will be washed off prior to being brought onto public land to prevent the introduction and spread of noxious weeds into the area.

## Construction Inspection

1.	All new construction, reconstruction, or major modification shall conform to the established technical standards and accepted engineering practices (e.g., the Uniform Building Code).

2.	Any construction inspections required by other applicable agencies are the responsibility of the holder.  Copies of completed inspections are to be provided to the Field Manager, either as they occur or as part of the final as-built plan.  Inspection information shall become a permanent part of the holder’s case file.

3.	The Holder agrees that corrective work detailed in Bureau of Land Management, or other agency required compliance inspections, would be completed by the scheduled completion date.  If the Holder disagrees or has questions about specific items, the Holder must contact the Bureau of Land Management in order that the disagreement or item may be resolved.

4.	A final set of as-built plans will be submitted to the Field Manager within 90 days of acceptance of structure (if contracted) or of completion date.

## New or Remodeled/Expanded Buildings

1.	Any new buildings must be designed to accommodate multiple users along with fitting into the physical environment as defined in a site-specific environmental analysis developed at the time of the proposal.

2.	Buildings are required to be one-story.  The roof must be metal or covered with metal to be fire resistant.  Roofs can be equipped with antenna support structures, such as poles and railings that can extend up to 25-feet above ground level.

3.	Facility Owners and Facility Managers are encouraged to construct the interior of their buildings in a modular fashion, so that they can:

a.	Sublease sections to others;

b.	Provide tenants and customers with internal separation and security;

c.	Reduce physical interference; and

d.	Increase management effectiveness.

4.	The following materials are approved for construction of new facilities (i.e. buildings)

#### a.	Floors – Concrete slab with drainage.

b.	Walls – Concrete block, pre-fabricated concrete, or other pre-approved fire resistant materials.

c.	Roof – Metal, or concrete, if painted to eliminate shiny surfaces, or other fireproof material as approved by the Bureau of Land Management.  Proposals for wooden roofs will not be approved.

d.	Partitions – If it is felt partitions are necessary in buildings, ensure they are constructed with fire resistant material (e.g., concrete block, reinforced concrete, or properly grounded expanded metal.

e.	Color – Proposed color for use on all exterior building surfaces must be pre-approved by the Bureau of Land Management. The goal of the color selection for the facilities is to make the building as inconspicuous as possible and make buildings located on the skyline look inconspicuous when viewed from a distance.  The intent is to reduce or eliminate glare from reflective and/or illuminated surfaces such as windowpanes, sheeting and reflective paints.  Non-reflective, Bureau of Land Management approved dark gray to green colors will be used on equipment buildings.

f.	Pre-fabricated equipment shelters which meet the above requirements may be approved.

5.	Building entry lights must:

a.	Only light the immediate area in the vicinity of the door;

b.	Be motion activated and have a limited time duration (e.g., 3-5 minutes); and

c.	Have a shielded beam that is pointed at the building door.

Requests for all-night (i.e. “dusk-to-dawn”) lighting, or entry lighting that would be visible from outside of the site will not be approved.

## New or Remodeled/Expanded Towers

- All new construction, reconstruction, and modifications to towers will be pre-approved by the Bureau of Land Management prior to implementation.

- It is the applicant/holder’s responsibility to assure that a new, or modified, structure will not unduly interfere electronically or physically with any existing equipment at the site.  Towers must be spaced, so as to prevent ground level radiation and/or interference problems.  This must be clearly demonstrated in writing to the Bureau of Land Management prior to issuance of a lease, permit, or amendment.

- All new towers will comply with current structural and safety specifications and design standards, including safety-climbing devices.  Towers should be as narrow and “open” as safety and structural integrity allow.  New towers will be designed using maximum wind, snow, and/or tower loading anticipated for the site.

- To avoid possible impacts to birds or bats, follow the most current version of the U.S. Fish & Wildlife Service’s Interim Guidelines on the Siting, Construction, Operation and Decommissioning of Communication Towers (available at http://migratorybirds.fws.gov/issues/towers/comtow.html).

SITE ASSOCIATION/ADVISORY GROUP

A Site Association is not recommended for the Livengood Communication Site since there is only one authorized user.  However, if the number of users increases, a Site Association should be developed and should extend to all users on BLM and State lands.  If formed in the future, the Site Association would be responsible for obtaining and maintenance of an administrative access and upkeep of internal roads and parking areas.  The Site Association would also be responsible for ensuring cooperation between users for on-tower access.  A Site Safety officer would be identified within the Site Association. The Site Association would be expected to develop a Radiofrequency Radiation Plan/Agreement and recommend measures to reduce interference issues (e.g., through use of filters).

The goal of the Site Association would also be to maximize the effective use of the site.  The objective of a sanctioned association will be to represent all site users as a group when dealing with the Northern Field Office on matters relating to the Site administration.  The association would be able to work in cooperation with the Bureau of Land Management (BLM) to identify problems or opportunities and make recommendations to these agencies for any changes in management strategies at the site.  The association could also provide input to these agencies regarding the future addition of equipment and facilities at the site. While the advice and recommendations of the association would not be binding on these agencies, they could use the input for administration of the site.  The BLM would be a member of such a group and would help jointly develop the charter (i.e., the ground rules).

In the absence of a formal Site Association, the BLM may utilize a Site Advisory Group that can make suggestions and/or recommendations to specific problems associated with the administration of the site.

APPENDICES

## Site Map

## Authorized Facilities

## Site Photographs

## Inspection Checklist

APPENDIX A SITE MAP

APPENDIX B  LEASEE FACILITY TABLE

|  | Auth # | Use | Building | Tower | Access/Parking | Other |
| --- | --- | --- | --- | --- | --- | --- |
| Facility 1 Alaska Department of Transportation and Public Facilities | AKFF 88076 | MIC | 8’x 12’ metal | 65’ guyed | Access 20’x 4500’ and parking | 5000’ power and comm lines |

APPENDIX C  SITE PHOTOGRAPHS

Cover photo  ADOT&PF site (F-88076)

ADOT&PF building

Appendix D

“Livengood Annual Technical Inspection”

Date Inspected: _____________________________   	Time Inspection: ________________________________

Permit Holder: ______________________________  	Authorization # _________________________________

Site Technician : ____________________________   	 Phone # _______________________________________

Number of Transmitters ______________________   	 License Posted _________________________________

Please mark the following Items as Acceptable (A) or Unacceptable (U).

Electrical Wiring ------------------- (A)     (U)        	Grounding --------------------- (A)     (U)

Equipment Installation ------------ (A)     (U)	Housekeeping ----------------- (A)     (U)

Building Repair -------------------- (A)     (U)	Tower Repair ------------------ (A)     (U)

Please mark the following Items as Yes (Y) or NO (N) or (NA)

Isolators ---------------------------- (Y)     (N)     (NA)	Circulators --------------------- (Y)     (N)     (NA)

Cavities ----------------------------- (Y)     (N)     (NA)	Terminators -------------------- (Y)     (N)     (NA)

Filters ------------------------------- (Y)     (N)     (NA)	Lightning Protection ---------- (Y)     (N)     (NA)

Comments: __________________________________________________________________________________

____________________________________________________________________________________________

Recommended Corrective Action:  ________________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

Required Corrective Action To Be Taken:  __________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

Committee Representatives:  _____________________________________________________________________

Bureau of Land Management Representatives: _______________________________________________________

Please make the required corrective action within the next 120 days.

Please make a written report of corrective action taken and submit to the BLM in Fairbanks.  If you should have any questions, please call the BLM office