5.14  	Facilities and Siting Requirements

5.14.1	Introduction

FIRE will utilize a significant on-site tritium inventory, and will be a major consumer of electrical power and liquid nitrogen.  As a burning plasma experiment, FIRE will cause both direct radiation and induced radioactivity in its materials, resulting in a need to design for the safe handling of radioactive material.  FIRE will therefore need to be licensed by the Nuclear Regulatory Commission, although it is expected that it will qualify as a “low hazard facility”.  The design of facilities and discussion of siting requirements have been approached assuming that FIRE might be constructed at a new, undeveloped site, where there are no constraints on the orientation and interaction between buildings and systems.

5.14.2  Functional Requirements

Generally, the various buildings and site infrastructure comprising the FIRE facilities must be designed to enclose, protect, support, and provide key services to the systems and components which are located within each building or structure.  The facilities are also assigned the functional requirements to protect workers and the public from radiation or toxic hazards associated with FIRE operation.  Spatial and geometric requirements include space for the tokamak itself, and space to perform assembly, operation, maintenance, and future decommissioning functions.  Because of containment and shielding needs, some FIRE maintenance activities will involve the use of robotic remote handling equipment.  The FIRE test cell, hot cells, and remote maintenance systems facilities must be large enough to house and shield the remote handling equipment that performs these functions.

FIRE is designed to provide sufficient self-shielding so that the exposed parts of the machine can be approached during shutdown by maintenance workers.  However, when operating, the tokamak cannot be approached, and a suitable shielding boundary must be established around the machine.  This boundary must include labyrinths and access control features to prevent unplanned worker exposure.  In addition, FIRE must be designed against certain accident events (see Section 5.15).  To prevent the uncontrolled spread of radioactive material, the tokamak building must include a confinement boundary.  This boundary must include features such as airlocks, depressurization, exhaust filters, and perhaps water removal systems to capture tritium, so as to mitigate the consequence of any accidental releases.   When radiation sources are enclosed inside the tokamak vacuum vessel, it provides their containment.  Whenever objects or materials are removed from the tokamak, the confinement function must be maintained.  However, it is not desirable to permit radioactive materials to contaminate the test cell.  To deal with radioactive materials and components, the facilities must include one or more hot cells where objects can be maintained or processed as waste.  The remote handling system must be configured so that it can transport objects between the tokamak and the hot cell without losing the containment function.

The buildings and structures must be designed to resist all appropriate forces, including gravity, seismic events, wind and extreme weather loads, maintenance loads, and any dynamic loads imposed by operating systems.  The various buildings are categorized as either safety related, or non-safety related, depending on the systems and materials they contain, and the functions they are assigned.  Safety related buildings are designed and constructed so that they will not lose their functionality during any event included within the design basis.  Non-safety-related buildings are designed so that they might fail to perform all their functions during extreme events, however, they are always designed to protect the health and safety of workers.

Figure 5.14.2-1 shows a generic site plan and includes a legend indicating conceptual buildings and structures.

5.14.3 Design Descriptions

5.14.3.1  Tokamak and Hot Cell Building

The tokamak and hot cell building is a two-level reinforced concrete structure.  The building outside dimensions are 39 m wide at the south end, 59 m wide at the north end, and 98 m long.  An overhead bridge crane serves the tokamak test cell and an adjacent space on the north side of the test cell (used for remote handling cask operations).

Figure 5.14.2-1 – FIRE Conceptual Site Plan

The rails for this crane also continue over the assembly and mockup building at the south end of the test cell. The tokamak test cell and remote maintenance area are enclosed by 1 m thick concrete walls and a 60 cm thick roof.  These structural elements form a shielding and confinement envelope around the tokamak and some of the remote handling operations.  The crane bay is approximately 20 m high.  Other parts of the building, which wrap around the remote handling area, contain hot cells and remote handling tools service areas.  These parts of the building are approximately 10 m high. The below grade basement level of the building has an internal height of 5 m, and the basemat is 3 m thick.  The building is arbitrarily oriented on the site with the longest side of the building in the north-south direction.

The wall at the south end of the test cell is equipped with a large movable section that can be raised to allow the crane to also serve the assembly and mockup building.  A similar movable shield wall is provided at the north wall of the test cell.  Both the north and south walls of the test cell also have large door sections that can be moved horizontally to allow the crane to carry loads from the assembly and mockup area to any point in the test cell or remote maintenance operating area.  The horizontal and vertical shield wall sections at the south end of the test cell are also equipped with inflatable seals, since they form part of the confinement boundary.

Figure 5.14.3-1 shows an east-west elevation view, or cross-section of the tokamak building.  The tokamak is located so that its vertical centerline is in the center of the test cell, and its horizontal centerline is 4.2 m above the operating floor.  This elevation is chosen to allow space around the tokamak for the operation of remote handling casks.  This view also shows the approximate location of waveguides for the ICRF system, magnet busbars, and the minor structures located east and west of the test cell to facilitate horizontal entry to the test cell basement from the adjacent buildings.  Services such as ICRF waveguides, cryopumping, diagnostics, and divertor cooling will connect to the tokamak via vacuum vessel ports.  The current test cell layout strategy calls for services that will connect to ports to be routed through the test cell basement and penetrate the test cell through the operating floor.  Because port closure assemblies (except one blocked by a diagnostic neutral beam) are designed to be replaceable, the space immediately in front of each port must be kept clear of permanent installations.  Penetrations through the floor must be located in areas aligned with the magnet centerlines, and de-mountable sections of piping, waveguides, or other systems used to complete the connection to the ports.

Other services, such as magnet power leads, magnet pre-cooling and vacuum vessel cooling, will connect to the tokamak at locations other than the ports.  The current layout strategy calls for these connections to be made through the test cell basement and to penetrate the tokamak pedestal or test cell floor in the space below the cryostat.  This area will be congested because of the tokamak support system.  The current concept for these supports is a ring of flexing columns located below each TF coil.  Because of space constraints, the tokamak support system must be integrated with the clamps for PF coil 3L.

Figure 5.14.3-2 shows an above grade plan view and North-South elevation view of the assembly, tokamak and hot cell buildings.  The test cell size is determined by the space required to maneuver and dock remote handling casks at ports.  Because of the length of the port closure assemblies, remote handling casks are expected to be approximately 8 m in length and about 1.9 m in width.  There are several strategies under consideration for the design of remote handling cask vehicles.  Casks could be transported between the tokamak and the hot cell using the building overhead crane, or they could be designed to move on the building floor using either wheels or air cushion supports.  Because of the expected weight of these objects, it is likely that air cushions will be superior to wheels.  A strategy for cask access to the inclined upper and lower horizontal ports has not yet been determined, however, the facilities layout assumes that casks for each of the three horizontal locations will be mated with a vehicle designed to support the cask at the correct level from the floor.  A floor-supported vehicle will move the cask to a pre-determined position in front of the port established by guide pins or stops.  The vehicle frame system will provide the final motion along the axis of the port.

When port inserts are removed from the tokamak they need to be transported to and transferred into one of the hot cells.  It is expected that the radioactivity level of these components will require enough dose attenuation to make it impractical for the casks and remote handling vehicles to include shielding.  Therefore, object transfer operations are planned as remote handling activities. When radioactive sources are being moved between the tokamak and the hot cells, the test cell and remote handling vehicle areas must be made inaccessible to workers.  The test cell will also be inaccessible whenever a port insert is removed and not replaced by a new insert or a dummy shield.  It should be possible to restrict all transfer operations to night shifts.

It will also be necessary to maintain the divertor and first wall.  To access these components, an in-vessel manipulator is proposed.  This device should be capable of being inserted through any port (except the port blocked by the DNBI cell) and able to reach one eighth of the vessel in either direction.  The in-vessel manipulator may be mounted at a port for an extended time, and there are several potential strategies for re-closing the tokamak shield to make the test cell accessible.  These include movable shield walls that could be erected around the manipulator cask, or shielding within the manipulator or cask that prevent radiation streaming from reaching unacceptable levels.  Figure 5.14.3-3 is a plan view in the basement of the complete building. Space is available for the roughing vacuum pumping system and for the tritium processing systems.  In earlier FIRE reports, these systems were located in a dedicated Vacuum Pumping and Tritium Building, which has now been eliminated.

Figure 5.14.3-2.  It is expected that cryopumps located in upper and lower horizontal ports will operate during tokamak pulsing.  Between pulses (three hours), cryopumps will be warmed and regenerated back to the vacuum vessel, which will be pumped using mechanical vacuum pumps located in the outer part of some of the mid-plane ports.  Because of the high magnetic field, these mechanical pumps will only operate between pulses.  The mechanical pumps will exhaust to roughing pumps located in the tokamak building basement.  This area will also contain fuel gas purification systems and isotopic separation systems.  Tritium and D-T mixtures recovered from the fuel gas will be stored on hydride beds in a secure vault.  All tritium processing equipment will be housed in glove boxes.  The hot cell concept is based on the expectation that some port mounted objects can be repaired and returned to the tokamak.  To facilitate this, part of the hot cell system will allow port objects to be placed into a cell wall penetration that is physically identical to the tokamak port.  Inside the cell, which provides shielding and containment, a remotely controlled work center will be provided, which can perform repair operations on plasma facing components.  Meanwhile, the outboard end of the port assembly remains accessible for hands-on work.  Divertors and plasma facing objects that cannot be repaired will be transferred through a docking port into a second, larger hot cell.  This hot cell will house remotely controlled equipment and workstations used to remove and replace the

finger elements on divertor modules, which will then be returned to service in the tokamak.  Discarded divertor fingers and other irradiated components will be stored and eventually processed for disposal.  The extent and nature of

these hot cell processes are not yet well developed, but it is expected that they will include divertor repair (replacement of individual finger-tiles), tritium recovery from beryllium, size reduction by sawing or cutting, and encapsulation of radioactive material for subsequent shipment to a waste repository.

The tools that operate within the remote handling casks are likely to become contaminated with tritium or radioactive dust, but are unlikely to become radioactive sources.  They will need development and periodic maintenance and testing.  To serve these functions, facilities are provided where remote handling casks can dock and discharge tools to a decontamination facility.  Tools are subsequently moved to a storage and repair facility.

5.14.3.2   Other Safety Related Buildings

The tokamak and hot cell building, and other safety related buildings will generally be constructed using cast-in-place reinforced concrete.  They will be designed to resist seismic forces and extreme weather hazards such as tornado missiles.  For the tokamak and hot cell building, which is also assigned a shielding function; the thickness required for shielding is generally more than the thickness required to resist tornado missiles.

The radioactive system support building (Building 12) will be used to provide locker and change facilities for workers entering radiation controlled areas and to support systems used in remote repair and processing in the hot cell.  This building will also provide space to store materials and supplies used by radwaste encapsulation systems, tritium recovery systems, and waste shipping to offsite disposal locations.

The radwaste systems building (Building 14) will be used to house treatment systems for water which has become contaminated with tritium or activated corrosion products.  All floor drains and other intentional drainage from cooling systems which could be contaminated will be processed in this building to remove particulate and ionic activity.  Water which is contaminated with tritium or which is recovered from atmospheric detritiation units in the plant HVAC systems will be treated in a water detritiation system.  This system will use established technology including vapor phase catalytic exchangers and a tall distillation column.

The emergency power supply building (Building 15) will be used to house a backup power generating system.  Presently, the need for safety related backup power is not well known, but the loads are likely to include the HVAC systems and any other loads associated with maintenance of the confinement function.  If these loads are small, the safety related power supply system could consist of two small auto-start diesel generators.  Some systems will require battery powered un-interruptable power supplies, which could also be located in this building, or which could be distributed on the site.

5.14.3.3   Non-Safety Related Buildings

Non-safety related buildings will generally be constructed using the lowest cost building technology that is suitable for their purpose.  This usually means a steel-framed structure built on a concrete slab foundation at grade.  The assembly and mock-up hall (Building 21) is provided to facilitate assembly and maintenance functions.  The width of this building is set so that the overhead crane used in the test cell and remote handling staging area can also operate here.  The assembly and mockup hall will have a below grade level dedicated to diagnostic signal acquisition and processing, and will be built from reinforced concrete below grade. The floor loading capability of the assembly hall will be the same as the tokamak and hot cell building, tentatively 20 tons/m2. The above grade portions of the building will be steel framing with architectural siding and roofing.

The magnet power conversion building (Building 22) will be used to house the indoor portions of the magnet power supplies.  Transformers will be kept outdoors as a safety measure, and rectifier sets and power conditioning and switching apparatus located indoors.  This building will be a single floor, steel frame on concrete slab structure.  To minimize the length of busbars and cables, the shape proposed for this building uses a main corridor and three transformer-rectifier bays.

The cooling system building (Building 23) will be used to house the indoor parts of the heat rejection system, which provides secondary coolant to the divertor and vacuum vessel cooling systems.  Under present site assumptions, secondary coolant is pumped to cooling towers and rejects heat to the atmosphere.  This building will also house the plant component cooling water system, which provides water cooling to many of the plant’s power supply and plasma heating systems.

The cryogenics systems building (Building 24) is used to house indoor parts of the liquid nitrogen system used to pre-cool FIRE magnets.  Liquid nitrogen storage tanks are located outdoors.  Because FIRE will consume large amounts of liquid nitrogen for magnet pre-cooling, it has been proposed that FIRE should be co-located with a commercial air liquefaction plant.  Under ideal circumstances, the liquid nitrogen system could be filled by pipeline.  Building 24 also houses a liquid helium refrigerator that provides liquid helium to the vacuum vessel cryopumps.  Other liquid helium users will be the diagnostic neutral beam, and the isotopic separation system in the fuel process.  These systems are not yet well developed, and the size of the system components and building are very preliminary.

The ion cyclotron heating system power supply building (Building 25) will be similar in design and construction to the magnet power supply building.  It will house the indoor portions of the ICRH system, including power supply cubicles, and tetrode signal generator modules.  The ICRH system will deliver 30 MW to the plasma via 16 trains; hence each train will be sized for about 2 MW.  Waveguides from the ICRH building and busbars from the power supply building will be routed through access structures on the east and west sides of the tokamak building, so that they can enter the tokamak building below grade.

The laboratory office building (Building 26) and the control and operations building (Building 27) will be designed and constructed to conventional office building standards.  The laboratory office building will be sized for 500 to 700 scientists, engineers, administrators, and other site workers.  The LOB will be located near the perimeter of the FIRE site, to permit relative freedom of public access.  The control and operations building, on the other hand, will be located as close to the tokamak buildings as reasonably possible, to facilitate easy physical access to FIRE facilities.  The control and operations building will include facilities for operator interface with all FIRE control systems, and will include space dedicated to management of abnormal events.

The utility systems building (Building 28) will be dedicated to necessary site infrastructure, and will house compressed air systems, potable and demineralized water treatment systems, site central heating and chilled water systems, and storage of clean parts and supplies.

5.14.3.4 Site Improvements and General Arrangement

In addition to safety and non-safety-related buildings, the FIRE site will include improvement needed to meet the functional requirements of outdoor equipment.  The switchyard to receive grid power and step it down to voltages suitable for FIRE systems must be capable of handling approximately 1000 MW.   Cooling towers will be required to reject heat from the divertor and vacuum vessel cooling systems.  If the heat rejection system is able to average the heat load, the total capacity of the cooling towers could be quite small.  Magnet pre-cooling will use liquid nitrogen, supplied by pipeline from a commercial on-site plant or a nearby offsite plant.  Because FIRE will be a licensed nuclear facility, perimeter fencing and multiple levels of access control will be required.  These features will be further developed in future work.

5.14.5 Site Selection Process

The FIRE design process has been based on the assumption that the experiment will be sited at a new, undeveloped location  - a “greenfield” site.  This assumption presents the minimum set of design constraints.  However, it is likely that several current experimental sites could also provide a good basis for design.  The following key criteria are expected to be important to the process of selecting a site for FIRE:

- Availability of land.  Since FIRE will be a licensed nuclear facility, it will be necessary for the operating organization to be able to control land use within a distance of 500 to 1000 meters from the tokamak building.  This exclusion distance is related to the analysis of radiation release events, and suitability of the site for a nuclear facility.

- Access to electrical power   FIRE will require input power on the order of 1000 megawatts for periods at least as long as the plasma pulse plus the ramp-up time.  If an otherwise good site does not have a sufficient electrical supply, some form of energy storage could be considered.  However, the high power demand and relatively long pulse could require total energy storage on the order of 20 gigajoules.

- Access to industrial infrastructure.   Supply of construction labor and material, transportation for the delivery of tokamak and other large components, and the availability of industrial commodities such as liquid nitrogen will be factors which could effect the cost and schedule.

- Ability to transport radioactive materials. It must be acceptable to the surrounding community that the FIRE facility receives shipments of tritium and issue shipments of encapsulated radioactive waste.

- Access to amenities for FIRE staff .  The scientists, engineers, and technicians who build and operate FIRE will require adequate schools, health care, and community infrastructure.

In the future, candidate sites will be identified and evaluated for their technical acceptability and their influence on the cost and schedule of the project.

# Text boxes

Fig. 5.14.3-1.

Fig. 5.14.3-2

Figure 5.14.3-3