PET RFQ Phase I

Project Report

Volume I: RFQ Accelerator

Edited by Ralph J. Pasquinelli

4/9/98

Contents

Chapter									Page

Preface......................................................................	3

Executive Summary.........................................................	4

Introduction  ...............................................................	5

Chapter Summaries........................................................	17

1.  	Pre 1995 Project History..................................................	20

2.  	Ion Optical Design of the RFQ PET Accelerator.......................	26

3. 	RFQ Tuning Systems	...................................................	54

4.	Low Level RF (LLRF)...................................................	63

5.	High Level RF (HLRF)...................................................	68

6.	Charge Doubler...........................................................	73

7.	Machine Operatons and Performance....................................	82

8.	Beam Instrumentation and Diagnostic Systems........................	92

9.	Equipment Interlocks......................................................	101

10.	Radiation Safety & Shielding.............................................	107

11.	Magnet Power Supply Systems .........................................	130

12.	Vacuum & Mechanical Systems.........................................	135

13.	Water Cooling Systems..................................................	155

14.	Control System Hardware...............................................	161

15.	Control Software.........................................................	163

Phase I Acclerator Performance Parameters.............................	173

Preface

The PET RFQ project is nearing the end of the first phase of what was envisioned to be a three phase project.  This document is a full report on the accomplishments and difficulties encountered during this phase.  As such it is important in the assessment of whether or not to proceed to the succeeding phases and, if so, is how to proceed.

This report contains documentation from the efforts of building the RFQ accelerator for production of PET isotopes.  It is meant as a summary of design, construction, performance and improvements.  Each chapter contains references to more detailed resources when appropriate.  The contributors listed below are part of a staff approaching one hundred individuals that have worked on this project for over two years.  Their efforts and dedication have created a functional 3He++ accelerator.

Contributors to this report include:

Ralph Pasquinelli, Roy Rubinstein, Chuck Schmidt, Ding Sun, Kris Anderson, Bob Webber, Dave Peterson, Brian Chase, Joe Dey, Frank Bieniosek, Del Larson, Nancy Grossman, Dan Holslin, Howie Pfeffer, Duane Voy, Elliott McCrory, Bruce Hoffman, Mike Shea, Richard DeHaas, Phil Young.

Executive Summary

The goal of this project was to accelerate 3He++ for PET isotope production. Utilization of 3He does not require enriched target material and was believed to reduce neutron radiation flux.  The starting point was an existing Strategic Defense Initiative Organization (SDIO) funded 8 MeV RFQ accelerator that had reliability and performance problems. This report describes the redesign/rebuild of almost all elements of that accelerator, including raising the energy to 10.5 MeV. The project design goals are:

Peak Beam Current=12 milliamperes (mA electrical , 6 mA particle current)

Average Beam Current = 300 microamperes (µA) (150 µA minimum)

Duty Cycle= 2.5%

Beam Uniformity on Target= +/- 25%

Beam Reliability/Availability= 50% of scheduled time

Minimal Radiation Shielding Outside the Target Vault, i.e. not a radiation area

Extensive Radiochemistry Targetry Studies of 11C,13N,15O,18F

Technology Transfer for Potential Clinical Use

To date the accelerator has achieved 10.5 MeV 3He++ beams with the following typical characteristics:

Peak Beam Current= 5 mA (electrical, 2.5 mA particle current)

Average Beam Current = 100 µA

Duty Cycle= 2.0%

Beam Uniformity on Target= +/- 50%

Beam Reliability/Availability= 25-30%

Entire Accelerator Foot Print is a Radiation Area

The collaboration believes that the reliability of the accelerator will improve, but that the minimum design average beam current of 150 µA will not be demonstrated before the beginning of radiochemistry experiments. The achieved performance is adequate to begin the radiochemistry program in January 1998. The cost to date is $8 million out of the original $10 million budgeted. It is unlikely that the technology transfer goals will be pursued in view of the remaining funds.

Introduction

This introduction will try to serve as a narrative describing how the project was conceived, the initial goals, what actual performance was achieved, some of the short comings and the lessons learned.  More specific technical details are described in subsequent chapters of this report.

Project Description

The PET RFQ project (or ÒPET projectÓ) is a collaboration between Fermilab (FNAL, Batavia, Illinois), Science Applications International Corporation (SAIC, San Deigo, California), Biomedical Research Foundation (BRF, Shreveport, Louisiana), and the University of Washington (UW, Seattle, Washington) to create a linear accelerator for the production of Positron Emission Tomography (PET) isotopes utilizing Radio Frequency Quadrupoles (RFQs) .  3He is the particle to be accelerated to 10.5 MeV for the production of the four main radio isotopes used in PET, 18F,11C,13N,15O. Most of the accelerator development has taken place at Lab G on the Fermilab campus.  Originally, the project had three phases. The first phase was to design, construct and commission the 3He linear RFQ accelerator.  The second phase was to carry out radiochemistry experiments.  The final third phase was to investigate the possibility of technology transfer to commercialize the application of RFQ accelerators for PET isotope production. A number of difficulties and setbacks were uncovered during the design and commissioning of the accelerator complex that have made the possibility of phase three improbable with the current funding profile.

This report will concentrate on phase one of the project. Subsequent chapters of this report will detail the major technical problems encountered and their solutions.  A second volume under separate cover will concentrate on the radiochemistry aspects of the project to date.

History

In 1988, the Strategic Defense Initiative Organization (SDIO) of the US Department of Defense requested proposals for new accelerator technology, under development for military purposes, to be applied to medical research.1  Science Applications International Corporation (SAIC) was awarded funding in 1989 to develop an 8ÊMeV 3He++ RFQ accelerator for the production of PET isotopes.  There were several advantages noted for this technique.  The proposed RFQs were small and lightweight, and required little neutron shielding (compared to the more commonly used proton/deuteron cyclotrons).  In addition, the targets for PET isotope production using a 3He++ beam do not require enriched isotopes.

Dabiri et al2 described in 1990 the proposed SAIC 3He++ accelerator.  It included a 3He++ ion source (then currently under development at SAIC) and two 425 MHz RFQs  for accelerating the particles to 8 MeV.  The projected peak electrical current was to be 15 mA, with 166 microsecond pulses at 120 Hz for a 2% duty factor.  The RFQ transmission efficiency was predicted to be 97%.  In October 1990, SAIC announced3 the achievement of a 0.5 MeV proton beam in their RFQ prototype.

At the Targetry 91 workshop, Hagan et al4 updated the design parameters.  The ion source was now to produce singly charged 3He+, followed by a 212 MHz RFQ accelerating to 1 MeV and then a charge stripper; this was followed by a two tank 425 MHz RFQ accelerating to 8 MeV.  The output was to be 360 Hz, 55 microsecond pulses, giving 2% duty factor; pulse current was to be 15 mA (electrical), which corresponds to an average electrical current of 300 µAmps .  The original 3He++ ion source was felt to be too developmental, and there were also significant changes to the earlier RF system design.  At the end of October 1991, a 9 mA peak pulse current had been achieved4 of 1 MeV 3He+.

In July 19925, tests were carried out on the 8 MeV 3He++ performance.  A beam of 2.5 mA peak, 120 Hz, 33 microsecond pulses was achieved, giving an average electrical current of ~10 µAmps.

A letter in March 19936 described the then state of the accelerator, following termination earlier that year of the PET RFQ program at SAIC.  It noted that there were still significant technological challenges remaining in the RF system, and that several other accelerator systems would have to be improved in order to achieve the design current.  A very rough estimate of the costs to bring the machine to design specifications was of order $1M.

A 1993 report7 summarized the results achieved before project termination.  A current of 4 mA electrical of 8 MeV 3He++ was obtained, at a 1.6% duty factor (these numbers correspond to about 65 µAmps electrical average current).  Some reasons for the low current were given, including a charge doubling efficiency of only 20%, but the system was very unreliable.

In late 1995, the continuation of the project was funded by the DOE with $10 million. Fermilab was chosen as the managing collaboration institution.  Earlier work (under the SDIO funded project) had shown a need for an increase in beam energy over the 8 MeV initial design value.  The increase in beam energy would allow for a thicker target window and improved isotope yields. Since the funding of the project was limited and did not allow for major system redesign, it was decided  to increase beam energy by adding a fourth RFQ to the accelerator chain.  Mechanical production capabilities limited the fourth RFQ energy gain to 2.5 MeV,  hence the new beam energy was chosen as 10.5 MeV.

The project has been technically reviewed three times over the last two years, twice by DOE and once by an independent review team appointed by the Fermilab Director.  Each review committee consisted of experts on RFQs, accelerator technology, and radiochemistry.  Suggestions from these committees were carefully scrutinized and, when possible, implemented in the redesign of the accelerator.  Very little of the original SDIO funded accelerator remains with the current design.  These details will be addressed in the following report.

The original intention was to complete machine design and commissioning at Fermilab followed by dismantling the accelerator complex and shipping to BRF in Shreveport, Louisiana.  A facility in the physical plant at BRF has been completed should this option still be part of the collaborationÕs plans.  The decision whether or not to ship the accelerator will be made during Spring 1998.  The radiochemistry program could also be carried out at Fermilab should the collaboration decide to keep the accelerator at its current location in Lab G.  If the Fermilab option is chosen, some infrastructure modifications to lab G will be necessary to allow more efficient operations for the radiochemists.

Current status of the accelerator commissioning has the machine operating at Lab G under the stewardship of SAIC personnel.  Chapter 16 will contain the details of operations at Lab G during a trial period with minimal FNAL intervention.  The intention of this period was to simulate day to day operations of the accelerator in a remote location, an important factor to consider should shipping the accelerator to BRF be chosen.

Accelerator Layout

Schematic representation of the accelerator systems .  Each of the major components will be discussed in more detail in subsequent chapters of this report.

Resuming the Project

There was an extensive period of litigation between government agencies as to when transfer of the existing accelerator hardware could be made between DOD and DOE.  During this period, the accelerator had been moved to BRF from San Deigo for the dedication of the new Biomedical Research Institute (BRI). The project was officially resumed in September 1995, with a $10 million funding profile.  At this time, there was no detailed design report available.  The original machine concept described in Reference 2 was not the machine that was designed and built under the SDIO contract. What was built  under the SDIO contract was a three RFQ system where the first RFQ operated at 212.5 MHz and was an integral part of what became a 1 MeV doubly charged 3He source.

It was  early on at Fermilab that the collaboration decided to increase the energy of the beam to 10.5 MeV.  This was mostly based on the need for more robust target windows.  The original thin (less than 0.6 mil) target windows could not be guaranteed to be pin hole free by the manufacturer.  Nearly 1 MeV of energy was deposited in these thin windows, leaving barely 7 MeV beam for radiochemistry experiments.  A thicker window was desirable, hence more energy would be necessary.  The additional beam energy would allow for more specific activity of the target. (Specific activity is the ratio of radioactivity from a compound of interest (usually one radionuclide is involved) to the mass of that same  compound in the sample of interest.  It is usually expressed as Curies per millimole or Megabequerels per millimole.) The value of 10.5 MeV final energy was derived from the longest RFQ that could be machined with conventional machine shop tools.  (SAIC had experienced some past difficulties in building their patented RFQ design if lengths much beyond a meter were considered.)  It was also believed that with the limited funding of the project, that costs would be prohibitive to use any different accelerating structure (i.e. drift tube Linac).  In retrospect this may not have been the case.

The first course of action after unpacking the boxes shipped from Shreveport, was to evaluate the hardware.  Several tests were the preliminary goal, 1.  To understand the performance of the RFQs, 2. to assemble the singly charged 3He ion source, and 3. to experiment with the SAIC gas jet charge doubler.  Four to six months was necessary to assemble the test stand to carry out these investigations.  By spring of 1996, work on all three objectives was well underway.  Several very important discoveries were made during this period.

The x-ray emissions from the 212 RFQ greatly exceeded the minimal level required for continuous occupancy.  Numerous lead blankets were wrapped around the RFQ  to reduce the radiation level to allow continuous occupancy.  The RF system used to drive the RFQ was one of the surplus FNAL Linac stations that had recently been decommissioned.  Even though the RF station was adequate for the test, it clearly lacked controls and interfaces necessary for integration into a reliable accelerator (all the old Linac interfaces, interlocks and controls were not part the surplus hardware).  Because these tests were only to 1 MeV, there were none of the problems of phase lock and stability that would be discovered as subsequent RFQs were put on line.  The testing continued very smoothly through the summer of 1996.

An additional test was carried out on one of the 425 MHz RFQs once surplus hardware was procured from the canceled GTA project at Los Alamos. It was fortunate for the PET project that the GTA utilized the same 4616 tetrode in one of their RF drivers.  The PET project purchased three 4616 amplifier cavities and four solid state amplifier drivers.  These early tests of the 425 MHz RFQ showed some sparking of the RFQ vanes when driven with 73 kWatts, the estimated correct value for achieving the gradient to accelerate 3He++ from 1 to 5 MeV.  There was no real spark protection in the test setup.  Later inspection of the RFQ showed discoloration and loss of copper plating on the vane tips in the middle of the RFQ structure.  (In a subsequent inspection of these vanes by Gerry McMichael of Argonne National Lab, he disclosed that the damage to the vanes was not detrimental to their future use.)

The tests on the ion source showed a number of design flaws that needed attention. Initial testing indicated excessive usage of 3He gas.  At $115 per gaseous liter, this would become a serious operational expense if not remedied.  The source was totally disassembled and revealed a number of ÒholesÓ in the source chambers that passed the He gas through to the vacuum pump unnecessarily.  Once plugged, gas consumption  was immediately reduced.  The arc modulator power supply was not robust or reliable.  A redesign of a pulse forming network power supply similar to units used at Fermilab was pursued.

The gas stripper/charge doubler was initially based on a static gas cell.  Striping efficiency was low and could be improved by a gas jet, a totally new design. The valve used for the SDIO project was piezo electric and very expensive. It had a limited lifetime estimated at 1-100 million cycles.  With the estimated accelerator design duty cycle of 2.5% running at 360 Hz, this translates to 0.77 to 77 hours of operation, clearly an unacceptable replacement interval.   A new design based on an automobile fuel injector was adopted.  The gas load necessary to strip 3He+ to 3He++ was such that a new vacuum system with ample pumping was necessary.  In addition, these first tests experimented with a number of different gases to test stripping efficiency, including helium, nitrogen, argon, carbon dioxide and xenon.

First DOE Review

The first nine months of effort were spent trying to understand exactly what the characteristics of the inherited project were.  It was at this same time that the first formal DOE review was conducted on May 29-31, 1996.  The project was closely scrutinized by the review team and the following action items were disclosed: 1.  Perform an ion source to target particle tracing with space charge effects included, i.e. an end to end simulation.  2.  Set up a detailed project management scheme to aid tracking of project progress.  3.  Develop a specific set of performance standards that would be agreed upon by all collaborating institutions.  Meet these minimum requirements before shipping the accelerator back to BRF. 4.  Hold a second review of the project in six months.

Action items 1 and 3 were absolutely critical to the technical success of the project.  It was indeed true that no full simulation had been carried out by the SDIO project. By the same token, we were discovering the performance of the existing hardware and it became evident that some reverse engineering would be necessary.  The end to end simulation was part of this process.  Upon rebirth of the project, it was believed that the lack of a reliable RF system was a major cause for poor operations.  At this stage, this simple assessment was not true as many subsystems required attention. In the period between DOE reviews, extensive work was done on the simulations and redesign of hardware support systems continued in parallel. The performance goals for the project were optimistic as are most goals of accelerator design.  A  minimum acceptable performance was drafted and agreed upon by all collaborators on August 30, 1996.  This document has been included as an appendix.

One of the areas of greatest concern was the design of the Medium Energy Beam Transport (MEBT) with beam at the 1 MeV energy.  The original SDIO design utilized an RF bunch rotating cavity after the stripper to match the beam longitudinally between the 212.5 and 425 MHz RFQ string.  The bunch rotation proved ineffective due to the charge neutralized state of the beam after stripping.  As such, a new means of matching was necessary.  It was also at this time that the physical foot print of the accelerator was a main concern.  The accelerator was originally designed to be very light weight, requiring little shielding.  Such a design could easily be located almost anywhere.  The collaboration had the intention of locating the accelerator on the second floor of the newly dedicated BRI in Shreveport.  (In fact the SDIO designed machine was set up on the second floor for the BRI dedication.)  The room on the second floor had limited space that barely could house the original footprint.  The addition of the 4th RFQ would not easily allow the accelerator to be installed on the second floor if the accelerator remained an in line design.

A number of MEBT designs were considered.  The one chosen was the idea of Delbert Larson, an SAIC consultant.  The new MEBT would consist of an isochronous 540 degree magnetic lattice to preserve bunch length.  An added benefit of the design was that the accelerator now folded back on itself essentially shortening the overall length and easing the siting problem.  (As it turned out, the projectÕs future home was prudently relocated to the BRI physical plant because the unknown nature of the shielding requirements could have made location on the second floor impossible.)  There were serious concerns over the space charge effects of the beam in the MEBT.  Extensive modeling was conducted, but understanding any nonlinear space charge effects would have to wait until actual beam tests.

Once adopted, the design for the MEBT was pursued vigorously.  The lattice required the design and construction of two large 270 degree bending dipoles and seven quadrupoles of various strengths.  All magnets were designed and fabricated at the Fermilab Technical Support Division.  This effort continued through November 1996.  There were a few technical problems that required some rework, but for the most part the magnets were produced on schedule and have performed remarkably well.

Second DOE Review November 6-8, 1996

A great deal of activity took place between the DOE reviews of the project.  The following is a paraphrasing of findings of the second review committee and subsequent actions by the PET design team.

The original ion source operated well in preliminary testing.  The optics for the ion source were redesigned and required a new vacuum vessel.  From this point on in the project, the reliability of the ion source filament became a source of concern.  The components for the ion source contain some organic plastic insulators and the entire source was not stored in an inert environment.  It is believed that some form of contamination is the culprit for filament failures.  The filament continues to be problematic, but new and improved designs and procedures are being followed to improve performance and reliability.  Emittance measurements were performed with equipment borrowed from the FNAL Linac department.  Two recommendations were presented. Relocating the steering magnet and use of consistent units of emittance.  Both recommendations were or are being acted upon.

The transmission efficiency of the  212 MHz RFQ was typically 65% in actual testing at lab G.  Further simulations with the RFQ code PARMTEQ supported this transmission efficiency.  In the period between DOE reviews, the 212 MHz RFQ sprang a leak between the vacuum and water cooling passages of the vanes.  The leak was caused by the corrosive action of water on the aluminum alloy (7075-T6) from which the vanes are fabricated.  This problem was temporarily repaired with an impregnation technique to stop the leak (more details in chapter 12) and allowed continued testing.  Three recommendations were presented.  1.  Additional probes to measure fields in the RFQs should be added.  A total of 12 such probes were added to all of the RFQs.  2. Continued modeling of the RFQ should utilize higher order term analysis software.  This should be completed before making new replacement vanes.  It was decided to take this opportunity to not only improve modeling, but also redesign the RFQ in an attempt to improve transmission efficiency.  3.  X-ray production endpoints should be conducted to truly understand the intervane voltage.  These tests were conducted on the 212 MHz RFQ with conclusions that show agreement between the theoretical fields and the extinction level of the x-rays produced.

The charge stripper testing with the fuel injector was successful in prototype testing to 60 Hz repetition rates.  No measurable emittance dilution was observed at stripping efficiencies approaching 83%.  The final stripper design was able to utilize a single fuel injector operating at the full duty cycle of 2.5% at 360 Hz.  Additional pumping was added to the final stripper, a total of 4000 liters per second.  Final stripping efficiencies at full duty cycle are approximately 70%.  Argon gas showed the highest stripping efficiency, but its high molecular weight and low thermal conductivity caused excessive heating of the turbo molecular pumps at full duty cycle.  Nitrogen gas is now utilized daily with only a few percent degradation in stripping efficiency, but vastly improved vacuum performance.  Operating at the higher duty cycle reduced stripping efficiency because the pumps are not able to fully recover vacuum between 360 Hz cycles.

The MEBT received the highest level of scrutiny.  The review committee was convinced that the MEBT performance as designed was questionable at best.  The recommendations were to look into developing contingency plans in case the MEBT was a failure.  Other suggestions were: addition of an isolation vacuum valve to the MEBT diagnostic box,  use TRACE3-D to evaluate magnet settings, add as many diagnostics as possible, try to do additional modeling utilizing the code PARMILLA and WARP3D.  At this stage in the project, the PET team was committed to the MEBT design.  All the magnets in the lattice were close to completion, those that were complete met the specifications.  More modeling did take place as suggested.  The diagnostic box was jammed full of diagnostics including segmented Faraday apertures, a current toroid, and beam profile monitors for use at low duty cycles during commissioning.   As it turned out, it was mechanically very difficult to include a vacuum isolation valve in the MEBT, hence that recommendation was not followed.  Some back up plans were discussed, but if the MEBT did not work, there would be a big delay in the project.  It was a bit of a gamble, but a victory for the project.  The MEBT has worked very close to design performance and has been very reliable.

The HEBT comments included lack of instrumentation in the beam line, unclear how 10.5 MeV is verified, use of a dog leg to reduce neutron flux in the reverse direction.  The committee was impressed with progress on the target window development.  Recommendations included characterizing the HEBT magnets and look  into an insertable profile monitor.  The magnets were indeed sent to the magnet test facility for characterization.  They were also carefully studied for cooling efficiency since the HEBT magnets were designed to focus 8 MeV beam not 10.5 MeV.  As a result, they would need to be run at higher currents.  The magnets passed the thermal testing at design current for 10.5 MeV.  Because of the high beam energy in the HEBT, a profile monitor of the wire type would not survive for very long.  Instead a set of movable collimator jaws was designed and built that could handle the full beam power if necessary.  A software application was written to do collimator scans to test for beam uniformity on the target window.  This program has worked well and has been verified against carbon foil irradiations.  (A carbon foil is irradiated, cut into strips, then very carefully counting for residual activity to measure beam uniformity.)

Recommendations for the RF systems was to improve the arc protection protocol and add RF field probes to all RFQs.  The PET team has indeed incorporated a systematic means of controlling RF fields in the RFQs after arcing occurs.  Because each of the RFQs needed to be rebuilt due to water corrosion of the vanes, the probes were easily added to all RFQs.

Action items from the second review: 1.  Continue modeling of RFQs. 2. Appoint single lead subsystem mangers. 3.  The Fermilab Director should appoint an independent advisory committee to review work on Accelerator construction and plans for future radiochemistry experiments.  4. Conduct another DOE review if the accelerator has not met project milestones by spring of 1997.   Modeling continued and was completed.  Single subsystem managers were appointed, an advisory committee was chartered, and there was no need for the next review as 10.5 MeV beam was accelerated in April of 97.

DirectorÕs Advisory Committee 5/22-23/97

By the time the advisory committee convened, the accelerator complex was very close to completion.  Beam had already been accelerated to 10.5 MeV. A number of useful comments on operations were presented and appreciated.  A large part of the review concentrated on the targetry program and safety issues related to relocation of the accelerator to Shreveport.  As the targetry and Louisiana safety regulations are not part of this report, nothing further will be mentioned here.

Onward Toward 10.5 MeV Beam

All of 1997 was devoted to final construction, assembly and commissioning of the accelerator complex at Lab G.  Even though a number of serious problems had been addressed and corrective action was taken, there were still more unforeseen problems ahead.

One of the more serious delays was caused by the problems encountered with machining and plating of the RFQs.  The water corrosion problem meant that all four RFQs would have to be built by the project.  (Only the 425 MHz RFQ C was in the original plan.)  There were several iterations with machine shops to find a company that could precisely machine the vane contours.  The major headache was finding a plating house that could successfully apply the copper plate to the aluminum alloy.  Each of the RFQ vanes and the RFQ C housing experienced plating problems and were returned to the vendor.  A new plating vendor was finally found that could complete the job successfully.  By April of 1997, all major components were in place and 10.5 MeV beam was first accelerated.

As commissioning ensued, one problem after another surfaced.  The filaments in the ion source were failing after one to two weeks of operation.  Previous work with the ion source showed filament lifetimes exceeding two months. This performance was not repeatable. The RFQs were slow to condition, the RF power systems had several infant mortality problems.  As duty cycle was increased to the full 2.5 %, the RFQ coupling loops began failing due to overheating.  The design of the coupling loop was such that the vacuum sealing o-ring was located in the region of highest electric field.  As a result, they overheated and caused vacuum failure.  The loops were redesigned to relocate the o-ring to the interior of the center conductor.  This fix was effective as no new loop failures occurred.  The water systems for the project were specified internally, but procured on the outside.  They experienced cooling compressor failure, valve control failure, flow transducer failure, and improper control loop parameters.  All have been fixed and the system has been performing reliably since.  As is often the case with Murphy phenomena, all of the failures occurred separately, few in parallel, with the end result of extended down time necessary to fix the problems.  These types of difficulty plagued the project for the last half of 1997 and made commissioning and operation of the accelerator a harrowing endeavor.

Radiation safety issues were constantly being addressed.  The original design of the accelerator indicated very low radiation losses due to the linear directed nature of the beam and low beam energy (8 MeV).  The accelerator was not expected to require any special shielding except for the target vault. With the increase in energy from 8 to 10.5 MeV, accelerator shielding issues became less clear (see Section 10).   Once the RFQ x-ray problem was mitigated, accelerator shielding was studied.  Careful modeling of the RFQ transmission characteristics indicated beam losses approaching 20% in the one centimeter drift space between RFQs in the 425 MHz string. These losses did indeed materialize and are the source of high radiation production outside the target vault.  Initial measurements were made at low duty cycle and scaled appropriately.  It was clear that the losses would create a radiation environment and interlocking the accelerator enclosure would be required.  The major concern at this stage was whether or not the physical plant at BRI could be shielded sufficiently to allow open occupancy on the mezzanine above the accelerator and outside the building.  Several possible solutions were discussed and tabled until further measurements were made.  With the uncertainty of shipping the accelerator to Shreveport, little further attention has been paid to the shielding problem at BRI.  Sufficient shielding was already in place at lab G to not be a concern on the Fermilab campus.  As duty cycle of the accelerator increased, measurements showed that the beam losses at the RFQ B&C interface would require additional shielding at lab G to keep the control room area classified for continual occupancy.  An 8 inch polyethylene wall was constructed on a movable cart and placed near the RFQ junction, hence mitigating the problem.

A number of attempts to start preliminary radiochemistry experiments began in late May 1997.  The first few attempts were focused on operational procedures and shakedown of the hardware.  By the end of the year, most of the low beam current tests had been performed and the need  for sustained  beam currents approaching 100 uAmps was desirable.  By December 1997 most subsystems were operating reliably.  There was one major component that was still outstanding, the fast valve trigger.  A fast valve (one able of closing in 7 msec) is located in the HEBT.  Its primary purpose is to close rapidly in the event a target window shatters.  Earlier experiments showed that the fast valve trigger sensor supplied with the valve was so sensitive as to trip from outgassing of the target window with moderate beam current levels.  A new sensor was on back order for many months.  A backup sensor was employed, but not as fast as one would like.  The bottom line was that a window broke in December, the fast valve stopped most of the debris, but operation of the accelerator is not like horse shoes, close does not count.  The material from the window contaminated the RFQ C and returning to full gradient became impossible.  The RFQ was disassembled and clearly had signs of serious arcing damage.  The debris deposited in the RFQ was also now radioactive,  making for a contaminate waste dilemma.  The RFQ was cleaned, reassembled, and put back under vacuum before the Christmas holiday.  In early January, the RFQ was reconditioned and beam commissioning resumed.  By this time, the new fast valve sensor was delivered, inspected, installed and tested before the next chemistry experimentation period.

With most of the problems of reliability solved, one main headache remained, keeping the RFQs, all four of them, tuned on resonance and at full gradient.  For some as yet unexplained reason, the conditioning of the RFQs has remained a mystery.  Several weeks are required to recondition and recover from maintenance periods that bring the vanes up to atmosphere.  Even when conditioning has been reached, the acceleration of beam exacerbates the spark rate in the 425 MHz RFQ chain.  The beam losses between RFQs approach 20% and seem to increase the spark rate.  The detuning of the RFQs approaches several kilohertz per second after a spark.  The thermal tuning loops are unable to respond quickly and the RFQ frequencies start to wander.  When there are four nomadic RFQs, it can take 20-30 minutes to settle down.  This proves to be a very frustrating environment to perform chemistry experiments.  A solution to this problem is now in progress.  The original SDIO accelerator utilized mechanical tuning paddles for resonance control.  By themselves, they were not capable of maintaining resonance control and were abandoned early in the project.  A thermal control loop was adopted, but lacked the response time needed to recover quickly from sparks.  The hybrid system now being implemented uses both thermal and mechanical tuning.  It is expected that resonance control recovery will now be seconds not minutes.

Success at Last

In early February 1998, the first serious radiochemistry experiments were successfully carried out.  With numerous failures and fixes in the past, the accelerator was able to deliver sustained beam currents of 50-75 uAmps to the target.  The radiochemists were able to obtain twice as much useful data as in all previous attempts put together.  While the resonance tuning problems continued, they were not so severe as to stop the experiments.  A March 1998 run was very successful, with the new tuning paddles providing prompt recovery from arcs.  Plans are to install tuning paddles for the remaining 212 and 425 C RFQs.

Lessons Learned

As is evident from this introduction, the project was not without difficulties.  There were a number of designs that needed re-engineering.  The project clearly exceeded the initial time estimate for completion of the accelerator and the cost estimate.  As progress on the accelerator continued, many times it felt like opening PandoraÕs Box. Although this project utilized some of the hardware from the SDIO program and surplus RF stations from the FNAL Linac, the design of this accelerator has provided a number of novel hardware  contributions and important changes to software programs utilized in designing accelerators.  The MEBT design may be a useful mechanism for matching RFQs to subsequent accelerating stages.  High quality 270 degree bending magnets were designed and implemented.  The simple but effective use of a fuel injector for a gas stripper provides a robust and reliable gas jet target.  The extensive modeling of the accelerator revealed a number of fundamental errors in codes that have been used for years in the field of accelerator design.  All of these contributions and more will be described in subsequent chapters.

It was initially believed (SDIO) that the beam loss between RFQs could be tolerated because of optimistic goals for accelerator components.  In reality, no part of the accelerator achieved the original  design parameters.  The operating parameters that have been achieved are listed in the table below.  If the use of a 3He beam for producing PET isotopes proves to be superior to proton cyclotrons, a better means of accelerating the beam would be to use the same 1 MeV source and stripper, but to follow the MEBT with a short drift tube Linac.  The drift tube section would have a larger aperture, lower losses, and higher reliability over the RFQ structures used in this project.

Table of Specifications and Performance of the  3He++ PET RFQ Accelerator

Item					Design Value		Achieved Value

Peak Beam Current			12 mA (electrical ++)		5 mA (electrical ++)

Average Beam Current		300 uA (electrical ++)		100 uA (electrical++)

Ion source Current			25 mA peak			21 mA peak

Ion source emittance			0.76 pi mm.mr. (90%)	1 pi mm.mr. (90%)

Duty Cycle				2.5%				2.0%

Stripping efficiency			70%				68-70%

MEBT transmission efficiency	100%				70%

MEBT input emittance			0.8 pi mm.mr. (90%)		0.9 pi mm.mr. (90%)

MEBT output emittance a		0.9 pi mm.mr (90%)		0.8 pi mm.mr. (90%)

RFQ 212  transmission b		80%				80%

RFQ 425 A-B-C transmission		43%				34%

HEBT beam uniformity		+/- 25 %			+/-50 %

Personnel occupancy			Not a radiation area		Accelerator footprint is

radiation area

(a) Scraping is observed to lower emittance in the MEBT

(b) - Accurate measurements of emittance and Twiss parameters exist only for

the old 212 RFQ.  The new 212 produces more beam (18 mA=75% ?) but much of

the additional current is lost in the MEBT/stripper.  Losses may be caused

by scraping due to a different exit angle (Twiss parameters), or increased

output emittance.  Unfortunately we did not have the opportunity to remeasure

output emittance and Twiss parameters for the new RFQ.

(c) Initial 'design value' numbers were very aggressive and perhaps unrealistic.

References

1.  See the introduction in Reference 7.

2.  A. E. Dabiri et al., Nuclear Technology, Vol. 92, p. 127, October 1992.

3.  Announcement of Proton Beam in SAIC Radio Frequency Quadrupole Accelerator.

4.  W. Hagan et al., Proceedings of the IVth International Workshop on Targetry and Target Chemistry.  PSI Villigen, Switzerland; September 9Ð12, 1991; edited by R. Weinreich, p. 19.

5.  Memo K. Krohn and J. Link to P. Young and W. Hagan, 15 July 1992, subject:  Trip report for July 6Ð9, 1992.

6.  P. Young to K. Krohn, March 29, 1993.

7.  K. A. Krohn et al., Proceedings of the Fifth International Workshop on Targetry and Target Chemistry.  Brookhaven National Laboratory, SeptemberÊ19 to 23, 1993; edited by R. Dahl, R. Ferrieri, R. Finn, D. Schlyer, p. 20.

Chapter Summaries

Chapter 1. Pre 1995 Project History.  A short description of the project before it was restarted with the current collaboration.

Chapter 2.  Ion Optical Design of the RFQ PET Accelerator. The design of a doubly charged ion source was beyond the scope and budget for this project.  A singly charged ion source original to the SDIO project has been modified and improved.  Filament problems have plagued this source since the early stages of the project. When it appeared that the problems with filament burnout were overcome, they resurfaced in the last 3-6 months.  A serious effort is now underway to understand the lack of reliability.  Currently produced filaments typically last only 2-3 weeks.  Filaments have been produced that lasted 2-3 months, an acceptable lifetime.  This level of reliability must be re-established. The ion source does deliver the design beam current when the filament is operational.

The RFQs for the project are basically the same design as the original RFQs under the SDIO funded program.  All RFQs needed to be rebuilt because of water corrosion problems. It was decided to take this opportunity to redesign the first RFQ in the chain to improve its capture efficiency.  In addition a fourth RFQ was added to increase the energy of the beam to 10.5 MeV.  All four RFQs were designed, built, tuned and tested within the current collaboration.

The original accelerator design consisted of two RFQs that accelerated 3He++ to 8 MeV.  While still under SDIO management, the accelerator was reconfigured to utilize three RFQs, the first being a 212.5 MHz capture RFQ to accelerate 3He+ to 1 MeV  (the energy at which the second electron is stripped, essentially creating a 1 MeV doubly charged ion source), followed by two tandem 425 MHz RFQs.  The need to strip to double positive charge and momentum match into subsequent 425 MHz RFQs for acceleration was not realizable with an RF bunch rotation cavity due to charge neutralization of the beam caused by gas leaking from the charge doubler.  A novel 540-degree-bend isochronous and achromatic matching section, the Medium Energy Beam Transport (MEBT), was designed (in the current project) to maintain the bunched characteristics of the beam while separating out the singly charged and electron remnants.  This was the most controversial aspect of the project during early DOE reviews as there were fears of debilitating space charge effects.  In fact the MEBT did not exhibit the predicted space charge or focusing problems and works reliably. The matching technique demonstrated in the MEBT may also be an attractive means of matching low energy beams in other applications.  The Low Energy Beam Transport (LEBT) and High Energy Beam Transport (HEBT) sections are similar to those in the original project and were also carefully modeled and studied.  A complete end to end beam transport simulation was performed.

Chapter 3.  RFQ Tuning Systems.  The resonance tuning system employed in the SDIO program exhibited a number of reliability problems associated with mechanical paddle tuners.  The complete system was redesigned utilizing thermal tuning via water cooling/heating.

Chapter 4.  Low Level RF.  The LLRF system is a completely new design based on the latest electronic techniques.  Extensive digital signal processing is employed to give the system a high degree of flexibility.

Chapter 5.  High Level RF.  The High Level RF of the original SDIO program was a serious reliability problem.  The use of planar array power amplifiers was a constant source of operational down time.  At the outset of the current project, it was believed that the surplus FNAL Linac RF stations could be modified to provide the RF power.  These surplus stations had a 25 year high reliability operational history.  The stations were indeed modified and are now operating with minimal maintenance.  Additional 425 MHz surplus hardware was purchased from Los Alamos National Lab.

Chapter 6.  Charge Doubler.  The 425 MHz RFQs are designed to accelerate doubly charged 3He++. Calculations and analysis for removing the second electron showed the need for a gas jet charge stripper versus a stripping foil. The technique from the original SDIO project of utilizing a piezo valve for the gas jet proved unacceptable due to short lifetime and poor performance of the piezo valve.  A new gas jet stripper utilizing an automobile fuel injector was designed, built, and tested.  This device now routinely provides 70-80% charge stripping efficiency.

Chapter 7.  Machine Operations and Performance.  The chronology of events leading up to present day operations and current performance is presented.

Chapter 8.  Diagnostics.  A complete suite of diagnostic instrumentation was designed for the accelerator.  Some of the devices include charge integrators, wire profile monitors, Faraday apertures and cups, and a beam intercepting longitudinal monitor. An emittance scanner was borrowed from the ion source group at FNAL to do emittance scans at 1 and 5 MeV.  The equipment has worked extremely well, allowing for ease in commissioning all sections of the accelerator.

Chapter 9.  Equipment Interlocks.  Virtually all of the hardware associated with the accelerator is new to the current project.  An extensive hardware protection interlock system was designed and built based on commercially available Programmable Logic Controllers (PLCs).  This system has already proven valuable in protection of RF, vacuum, and water subsystems.

Chapter 10.  Radiation Safety and Shielding.  Radiation safety for this machine demanded a careful in-depth effort.  A number of serious problems were encountered, analyzed and mitigated.  Although one of the selling points of a linear particle beam was low radiation levels, the opposite was found to be true.  The initial SDIO effort concentrated more on light weight design than on low radiation levels.  As such the RFQ vanes, housings and vacuum vessels were designed from aluminum alloys.  The x-ray radiation levels of the RFQs in the aluminum vacuum vessel exceeded 10 Rads/hr on contact.  New Stainless steel chambers 1-5/16 inch thick were designed, installed and eliminated the x-ray hazards.  The neutron production from 8 MeV 3He++ on aluminum was difficult to estimate.  Radiation levels near the RFQ junctions were found to exceed 100 mrem/hr due to particle beam losses associated with the gaps between adjacent RFQs.  This required a radiation interlock system to be installed.  The entire accelerator enclosure is now an interlocked radiation area.  Additional shielding will be necessary for relocation of the machine to Shreveport.  (This problem is currently being addressed.)  The radiation levels in the target vault  exceed the shielding capabilities of the current vault design.  While this does not present a problem in the lab G location at Fermilab, a new or modified vault design will be necessary for BRF in Shreveport.

Chapter 11.  Magnet Power Supply Systems.  With the addition of the MEBT to the project came the need for nine additional powered magnets.  Together with existing magnets for LEBT and HEBT, the system now has in excess of twenty power supplies.  The MEBT has the additional requirement for stable current regulation that exceeds standard catalog power supply specifications.  A complete remotely controlled and monitored power supply system has been designed, built, installed, and runs reliably.

Chapter 12.  Vacuum and Mechanical Systems.  The complete mechanical systems for the accelerator were redesigned from the ground up, literally.  New stands for supporting the accelerator structure were designed to allow easy assembly and maintain ten mil alignment tolerances.  A new vacuum system was carefully specified, analyzed, designed and installed.  All mechanical designs have taken ÒmobilityÓ into consideration so that the accelerator could be easily relocated to Shreveport.  A great deal of mechanical design was required to create the functional Charge Doubler described above.  Water corrosion problems in the RFQs required a temporary impregnation fix as well as coating new RFQs with Teflon for long term protection.

Chapter 13.  Water Cooling Systems.  The design of the accelerator calls for self contained cooling systems.  The water systems for the project are based on commercially manufactured components.  The systems include three types of cooling loops, Low Conductivity Water (LCW), four independent RFQ cooling loops, and a central heat exchanger loop.  After some initial infant mortality of components, the water systems are functioning well.  Some water temperature control problems are being addressed as the factory settings on the heat exchanger control loop were not optimized for our system.

Chapter 14.  Control System Hardware.  The control system hardware is the spinal chord of the accelerator.  Clearly the design of this accelerator held many challenges.  One system where challenges were not welcome was the control system.  It was decided to adopt the field proven design of the FNAL Linac control system.  The hardware did not require extensive redesign, hence reducing cost to the project.  The control system has indeed provided reliable operational experience.

Chapter 15.  Control Software.  Although the control system  hardware existed, a great deal of application code needed to be developed to support accelerator commissioning and operations.  In addition, it was decided to create a user friendly graphic control environment to facilitate daily operations and diagnostics.  Software was written utilizing commercial and in house applications.

1.  Pre 1995 Project History

The project to develop a He-3 accelerator for use in the production of short lived isotopes (C, F, O, N) was first proposed in 1988 in response to a Broad Agency Announcement (BAA) from the Strategic Defense Initiative Office (SDIO).  The SDIO was at the time interested in helping to develop spin off products from technologies that had been significantly invested in by the core SDIO program.  Accelerator technology and in particular Radio Frequency Quadrupoles (RFQ) accelerators was one of these technologies.  At the same time there was significant interest by the Positron Emission Tomography (PET) community in finding smaller, cheaper, lighter sources for the short lived isotopes that are of interest to this community.  As a result, one of the items in the BAA was a solicitation for new and innovative ideas for production of PET isotopes.

In response, SAIC teamed with the University of Washington to propose using 3He to produce the PET isotopes.  This was a very interesting idea for several reasons.  In addition to using a technology that SDIO had made significant investment in, this approach was believed to hold other advantages such as:

Small size  low weight, Linacs lighter than cyclotrons

Single particle, cyclotrons for PET are often dual particle

No need for enriched targets, enriched targets are expensive can be difficult to obtain

Cyclotrons use protons or deuterons as the projectile and require enriched target material

Low neutron production, deuteron cyclotrons require large shielded enclosures and at  8 MeV.  3He  is below the coulomb barrier of high Z materials so few neutrons are produced in the accelerator and only the target needs to be shielded.

Following the review of all the proposals, the SDIO funded two programs one being the SAIC He-3 approach.  The characteristics of that first proposal are summarized in the following table:

| Output Energy | 8 MeV, He-3++ |
| --- | --- |
| Beam Current Electrical | 15 mA (electrical) |
| Ion Source | He-3 ++ |
| Duty Factor | 2% |
| RF Power | 400 kW |

As originally envisioned the accelerator would be composed of a doubly charged He-3 ion source followed by a matching section, two RFQs, and the high energy beam transport.

In October of 1989 work began on the program.  The first part of the project was to investigate the critical technologies and move the design from concept to preliminary design.  As part of the critical technology investigation, a study was initiated to look into the difficulty of a doubly charge 3He++ ion source.  Ion source expertise was obtained from Los Alamos and Lawrence Berkeley Laboratory in order to research this problem.  This roughly yearlong study resulted in a doubly charged source that produced approximately 1.5 mA of doubly charged beam, far below that which was required.  This outcome resulted in a rethinking of the layout of the entire machine.  An ad hoc design group looked into the other possibilities for producing the desired 8 MeV beam.  The resulting report recommended the machine be changed so that a singly charged ion source could be used followed by acceleration to an energy where the stripping cross sections were favorable for creating a doubly charged beam of sufficient current.  This is the approach that is currently being used.

This new design was then presented to the projects sponsor, SDIO, and rejected due to the increase in weight over the simpler doubly charged source approach.  In retrospect the decision by the SDIO not to approve the changes was somewhat misguided by their belief that the increase in weight would make the technology unattractive to the medical community.  Later discussions with General Electric Medical Systems revealed that this small increase in weight was not critical to the acceptance of the RFQ technology by the medical users.  Nonetheless, the first stop work was issued on the project.  A series of meetings was held to restart the program and in February of 1991, a preliminary design review was held where the new design was presented.  The following table (taken from PET note 3, viewgraph 02-05-91 and PET note 2, Preliminary Design Report) shows this design. (PET notes are a series of reports generated from the original project and available from current project management.)

| Item | Technology | Characteristics |
| --- | --- | --- |
| Ion Source | Duoplasmatron | 3He+ , 20 keV, >20 mA, 200 usec, 120 Hz |
| LEBT | Electrostatic | Emittance < 105 pmm x mrad |
| 212 MHz RFQ | Modified 4 vane | 1 MeV, > 15 mA (Tr 75%), Emittance 20.6 pmm x mrad |
| Charge Doubler | Gas jet | 3He+ to 3He++ , 80% strip efficiency, 24 mA out |
| MEBT |
| 23 mA electrical (Tr 95%) |
| 425 MHz RFQ | (2) 4 vane RFQs | 8 MeV, 3He++ , 285 kW, 15 mA (Tr 65% total through chain) |
| HEBT/ Target |
| Water or Carbon |

This design was still relatively compact.  The total length was about 5 meters.  In order to keep the weight as low as possible (still a sensitive issue with the SDIO) an all aluminum RFQ structure was used, a light weight einzel lens was used for focusing in the LEBT, and the vacuum tanks were fabricated from light weight aluminum.

The program then went into final design and fabrication (a series of approximately 80 reports were written which document the design of the SDIO system, PET 1 Ð 83, i.e. PET notes).  A number of issues became clear as each stage was constructed.  First, the einzel lens that had been built for the LEBT focusing into the first RFQ proved to be incapable of focusing the high current and partially neutralized beam from the ion source beam.  The decision was made to use a solenoid lens for focusing, going back to the lens that had been used on the ion source development effort and abandoned due to weight.  Second, it became clear that a fast way for controlling the resonant frequency of the RFQÕs was needed.  This led to the implementation of paddle tuners (PET 8 May 12, 1992 SDIO progress report).  Third, the design of a close coupled RF system which had been originally proposed to keep the entire system compact was abandoned as too developmental and a more conventional planar triode array was used(PET 2, 2/6/91).  There were also a number of other less major changes to the design as the system was developed.

The end of 1991 and the first half of 1992 were focused on the construction as the following table shows.

October 1991		1 MeV beam out of the 212 MHz RFQ

February 1992		5 MeV beam out of the first 425 MHz RFQ

March 1992		8 MeV beam out of the final RFQ

July 1992		First attempt at radiochemistry

During this same period of time and in accordance with the original goals of the program, SAIC sought out commercial interest in this technology.  The major commercial entities involved in the development of the PET market were General Electric Medical Systems (GEMS) and Siemens Medical.  GEMS had shown a keen interest in this technology due to its potential to Òleap frogÓ the market.  GEMS had already purchased the controlling interest in the PET cyclotron business of Scandatronix, and after searching all other technologies, believed that the He-3 approach was the future for isotope generation for PET.  In 1992 SAIC and GEMS negotiated an agreement whereby SAIC licensed its patent to GEMS and both companies participated jointly in the development.  Throughout the last half of 1992, SAIC and GEMS worked together to develop a program whereby this technology could be developed and commercialized.

The original funding for the project, 3.6M from the SDIO, was fully expended in mid 1992.  Support for the continuation of the program came from SAIC and GEMS.  The total funding through the end of 1992 was around 4.9M dollars.

In November of 1992, GEMS and SAIC held a concept review whereby the progress of the program was reviewed and the plans where discussed for the development of the first prototype unit (the existing SDIO funded system was the proof of concept unit).  The following table summarizes the performance to date as of this review (CASPR Concept Review).

| Location | Transmission | Achieved Current (11/12/92) |
| --- | --- | --- |
| Ion Source (3He+) |
| 22 mA peak |
| LEBT | 80 | 17 mA peak |
| 212 MHz RFQ | 68 | 12 mA peak |
| Charge Doubler and MEBT |
| 13 mA peak |
| 425 MHz A and B RFQ | 23 | 3 mA peak |
| HEBT to Target | 95 | 50 microamps Average |

A few notes are important with regards to the operation of the systems at that point in time.  The peak average current that had been achieved was 50 microamps.  Unfortunately this current could not be maintained on a regular basis due to the unreliability of the RF power system.  Also, even though stripping efficiencies better than 80% had been seen, the valve that was used to pulse the gas was unreliable and did not have good long-term stability.  An automotive fuel injector valve was proposed to replace the existing piezoelectric valve, but never implemented.

The MEBT , a linear combination of permanent magnetic quadrupoles (PMQ) and an RF buncher, was difficult to analyze and tune, since one could not change the value of the PMQÕs and the combination of singly and doubly charge beam confused the measurement.  The PMQÕs were necessary due to the very limited space that could be allowed for transverse focusing unless a second longitudinal RF buncher was used.  The operation of the RF buncher in the presence of the high gas loads from the charge doubler was emerging as one the areas of difficulty in this MEBT approach.  Since making a longitudinal emittance measurement at these low energies is very difficult, the operation of the buncher could not be analyzed without the 425 MHz RFQ in place.  This difficulty combined with the slow turn around on the varying of the PMQ fields (3 weeks), made the MEBT/charge doubler the focus of most of the development efforts during this period.

At the close of 1992, the PET market was going through a significant slowing, as was health care in general, due to the uncertainty over the direction that the PresidentÕs health care reform initiative would take.  This uncertainty resulted in GEMS canceling all of their internal research programs with paybacks that were in excess of 2 years.  The 3He RFQ project fell into this category and in February of 1993 the program was stopped again.  For about six months after that the project continued at a low level on internal SAIC funding until July when the system was shut down.  Most of the effort during this last period was focused on the buncher in the MEBT.

In late 1993 and early 1994 the program was again started by the Department of Energy which resulted in the present collaboration between Fermilab, SAIC, Biomedical Research Foundation of Northwest Louisiana, and the University of Washington.  As the program was reviewed and proposed for DOE funding, it became clear that the PET market had significantly changed since the original SDIO funding.  The role of 8 MeV 3He was considered to be too marginal in terms of its predicted production of the PET isotopes.  The final energy of 8 MeV had originally been selected as a trade-off between accelerator length (compactness, weight, etc.) and isotope production.  The radiochemistry part of the collaboration, the University of Washington, believed that the machine needed to achieve at least 10 MeV to be able to make a significant contribution to the body of knowledge on PET targetry.  This then changed the machine into its present status of 10.5 MeV.  The table below, which is part of the Interface Control Document written for this program, gives the energy and current requirements for which the existing machine was designed.

The program as it currently stands is significantly different from that system proposed in 1988.  As its configuration has changed so has its role.  Today we have a very powerful source of 3He, probably the most intense one in the world.  That is not the only achievements of this machine however as the following list attests:

Worlds most intense source of accelerated 3He

First time three RFQs have been operated in series, or for that matter four

First successful isochronous MEBT to match two RFQs, no RF bunching

Resonant control of four RFQs operating in series has never been attempted before

Demonstration of magnetic spreading of beam to form a uniform beam on target.

Demonstration of the concept of using automotive fuel injectors for stripping cells.  First proposed at the SSC but never tested.

Demonstration of Segmented Vane RFQ structure (212 MHz RFQ), small cross section could be an enabling technology for low frequency RFQs

Development of thin, high energy density target windows

Development of 3He targetry

Shielding studies for a 10.5 MeV beam of 3He had not been performed before and may have relevance to other low energy accelerator systems.

LONGITUDINAL TWISS AND SYSTEM PARAMETERS

|  | Ebeam |
| --- | --- |

Tr

%

Ielect.

| mA | al |
| --- | --- |

bl

deg./keV

el

deg-keV

| 6*rms | Comments |
| --- | --- |
| Ion Source Out | 20kV |
| 30 | - | - | - |
|  | Prestripper RFQ In | 20kV | 83 | 25 | - | - | - | Nov. 92 PREPET.PAR Input |
| Prestripper RFQ Out | 1.003MeV | 80 | 20 | .283 | .828 | 880 | WDC archives |
| * Poststripper RFQ A In | 1.003MeV | 70 | 28*** | -.0420 | 1.54 | 1800 | Optimised input DSun 10/95 |
| Poststripper RFQ A Out | 5.047MeV | 82 | 23 | .0194 | .381 | 2500 | 28-JAN-93 PARMTEQ |
| Poststripper RFQ B In | 5.047MeV | 95 | 22 | .116 | .385 | 2500 | 28-JAN-93 PARMTEQ |
| Poststripper RFQ B Out | 8.025MeV | 85 | 19 | .417 | .229 | 3200 | 28-JAN-93 PARMTEQ |
| Poststripper RFQ C In | 8.025 MeV | 95 | 18 |
| Poststripper RFQ C Out | 10.539 MeV | 85 | 15 | .1404 | .198 | 4478 | 10-JAN-96 PARMTEQ D.Sun |

*    NOTE:  FROM ÒPrestripper OUTÓ to ÒPoststripper RFQ A InÓ the frequency of the bunch doubles so that one must double the emittance value and the beta function to convert from 212.5 MHz units to 425 MHz units.

**  NOTE: In the BRI PET project the x and y coordinate axis have been moved 45 degrees from the SDIO PET project so that now the x axis is in the vertical plane and the y axis is in the horizontal plane

*** NOTE: Electrical currents doubles in the MEBT due to the stripping and charge doubling

TRANSVERSE TWISS PARAMETERS**

|  | Ebeam | av |
| --- | --- | --- |

bv

mm/mrad

ev

pmm-mrad

un-norm

| 6*rms | ah |
| --- | --- |

bh

mm/mrad

eh

pmm-mrad

un-norm

| 6*rms | Comments |
| --- | --- |
| Ion Source Out, Demo Electrodes, 15mA/90% | 20 kV |
|  | 180 ±15 |
|  | 180 ±15 |
|  | Ion Source Out, PET Electrodes, | 20 kV | -2.60 | .450 | 100-150 | -2.60 | .450 | 100-150 |

TRACE2D 31/jan/91

| At exit of extraction electrodes |
| --- |
| Prestripper RFQ In | 20kV | 1.62 | .0284 | 192 | 1.62 | .0284 | 192 | Measured FNAL 6/96 |
| Prestripper RFQ Out | 1.003MeV | -1.17 | .130 | 30 | -1.08 | .112 | 30 | Measure FNAL 6/96 |
| Poststripper RFQ A In | 1.003MeV | 2.00 | .0460 | 33 | -1.42 | .0371 | 33 | Calculated D.Larson MEBT 96 |
| Poststripper RFQ A Out | 5.047MeV | 1.51 | .0638 | 8.3 | -1.24 | .0507 | 8.3 | 28-JAN-93 PARMTEQ |
| Poststripper RFQ B In | 5.047MeV | .370 | .0221 | 8.5 | -2.46 | .134 | 8.5 | 28-JAN-93 PARMTEQ |
| Poststripper RFQ B Out | 8.025MeV | -1.07 | .0359 | 5.5 | 2.96 | .159 | 6.0 | 28-JAN-93 PARMTEQ |
| Poststripper RFQ C In | 8.025 MeV |
|  | Poststripper RFQ C Out | 10.539 MeV | -.3883 | .0398 | 6 | 1.8295 | .1489 | 6 | 10-JAN-96 PARMTEQ D.Sun |

**  NOTE: In the BRI PET project the x and y coordinate axis have been moved 45 degrees from the SDIO PET project so that now the x axis is in the vertical plane and the y axis is in the horizontal plane

2.  Ion Optical Design of the RFQ PET Accelerator.

Comparison Between End to End Design and Performance.

Introduction

The BRF-FNAL-SAIC-UW PET Accelerator is now operational, and much has been learned about its operation.

The initial expectations for device performance were:

150 µA (acceptance criterion) to 300 µA (design) of average 3He++ beam current at an energy of 10.5 MeV

Beam uniformity at the target considerably better than what would be expected from a Gaussian beam

The actual performance to date (March 1998) is:

Up to 120 µA of average 3He++ beam current at an energy of 10.5 MeV

Beam uniformity at the target considerably better than what would be expected from a Gaussian beam

This report section will present a comparison of the design and performance for the device, treating each section individually.  As will be discussed further below, the low and high energy matching lines have worked very well, the medium energy transfer line and stripper is not at its design goal, and the RF and/or RFQs have not functioned up to their initial design expectations.

Review of Accelerator Design Parameters.

The PET Accelerator consists of a 3He ion source, a low energy beam transport (LEBT) region, a 212.5 MHz RFQ, a medium energy beam transport (MEBT) region, a 425 MHz RFQ string, and a high energy beam transport (HEBT) region.  To achieve the most efficient acceleration of the 3He ions to the energy needed for isotope production, it is desirable to doubly ionize the 3He beam.  This is accomplished by initially accelerating the 21.5 keV 3He+ source beam to 1 MeV through the 212.5 MHz RFQ.  At this energy the ionization cross sections are such that a gas jet stripper can be used to remove the second electron from the 3He+.  The resulting 3He++ ions are then transported and the transverse and longitudinal beam parameters manipulated for matching into the subsequent RFQ.  The 3He++ beam can now be efficiently accelerated to approximately 10.5 MeV through the 425 MHz RFQ string.  The MEBT, which has a principal function of matching the beam into the 425 MHz RFQ string, was anticipated to be the most challenging section to design and implement.  Due to space and vacuum constraints, a design based on a near-symmetric, 540 degree isochronous triple focus bend was adopted.

The final summary design report for the PET accelerator is entitled ÒEnd to End PET DesignÓ and is available on the PET WWW page.1  Table 2.1 presents an overview of the end to end design, specifying peak current, normalized emittance, and the analysis codes used for each section of the device.

The end to end design uses typical peak current values throughout.  To convert to average current values one must multiply by the design duty factor of 2.5%.  Using this conversion factor, the design electrical average current output at the end of the accelerator is 300 microamps.  Quoted emittances are normalized, 90% (5 RMS).

The study of the  PET accelerator has been divided into various sections.  For this project the source is defined as the portion of the device between the plasma and the ground electrode; the LEBT is defined as the portion of the device between the source and the 212.5 MHz RFQ; the MEBT is defined as the portion of the device between the 212.5 MHz RFQ and the first 425 MHz RFQ; and the HEBT is defined as the portion of the device between the last 425 MHz RFQ and the target.  A diagram of the accelerator appears in Figure 2.1.

Table 2.1. Parameters of the End to End Ion Optics Design.

Beam Section

Analysis Codes Used

Peak Output

Electrical Current

Output

| Transverse Normalized Emittance |
| --- |
| Source | EGUN | 24 mA | 0.76 p mm-mr |
| LEBT | TRACE 2-D | 24 mA | 0.76 p mm-mr |
| 212.5 MHz RFQ | PARMTEQ | 20 mA | 0.8 p mm-mr |
| MEBT |

TRACE 3-D, SCAT,

| TRANSPORT | 28 mAa | 0.9 p mm-mr |
| --- | --- | --- |
| 425 MHz RFQ | PARMTEQ | 12 mA | 0.49 p mm-mrb |
| HEBT | TURTLE, TRACE 2-D | 12 mA | N/A |

a - Stripping occurs which doubles the input electrical current within the MEBT.

b - Intentional scraping of the beam occurs reducing normalized emittance.

Figure 2.1.  Schematic Diagram of the PET accelerator.

Section by Section Comparison of Design vs. Performance as of October 1, 1997.

Improvements to the PET accelerator are ongoing, and here we will use data logged up to October 1, 1997.  The operation up to that point had been worked on diligently, with each device section tuned to obtain maximum accelerator achievement.

Achieved vs. Design Beam Current.

Table 2.2 compares the design values of beam current with those achieved to date for the various sections of the PET accelerator.  Table 2.3 converts the beam current design values into percentage transmission coefficients for each accelerator section.  Table 2.4 compares the design and performance duty cycle and the design and performance average current for the total project.

| Table 2.2. Performance vs. Design for Each Section of the PET Accelerator. |
| --- |
| Beam Section | Design Output Peak Electrical Current | Achieved Output Peak Electrical Current |
| Source | 24 mA | 24 mA |
| LEBT | 24 mA | 24 mA |
| 212.5 MHz RFQ | 20 mA | 15 mAb, 14 mAc |
| MEBT/stripper | 28 mAa | 21 mAa,b, 14 mAa,c |
| 425 MHz RFQ | 12 mA | 7 mAb, 5.5 mAc |
| HEBT | 12 mA | 7 mAb, 5.5 mAc |

a - Stripping occurs which doubles the input electrical current within the MEBT.

b - Results recorded for low repetition rate (60 Hz) operation.

c - Results recorded for 360 Hz operation.

Table 2.3.  Performance vs. Design Transmission Coefficients

| for Each Section of the PET Accelerator - Peak Currents. |
| --- |
| Beam Section | Design Transmission Coefficient | Achieved Transmission Coefficient |
| Source | 24 mA | 100% |
| LEBT | 100% | 100% |
| 212.5 MHz RFQ | 83% | 63% b, 58% c |
| MEBT | 70% a | 70% a,b, 50% a,c |
| 425 MHz RFQ | 43% | 39% |
| HEBT | 100% | 100% |

a - Stripping occurs which doubles the input electrical current within the MEBT.

b - Results recorded for low repetition rate (60 Hz) operation.

c - Results recorded for 360 Hz operation.

| Table 2.4. Performance vs. Design for Duty Cycle and Average Current |
| --- |
| Quantity | Design Value | Achieved Value |
| Duty Factor | 2.5% | 2.0% |
| Average Current | 300 uA | 110 uA |

As can be seen from the above tables, the source, LEBT and HEBT have reached their design goals.  The MEBT/stripper has equaled its peak design goal when run at low duty cycle (60 Hz), but achieves only 72% of its design transmission goal when running at 360 Hz, as stripping efficiency falls off at the higher repetition rate.  The original 212.5 MHz RFQ is the furthest away from meeting its design goal, achieving 76% of its peak design transmission at low duty cycle, 70% of its peak design transmission at 360 Hz.  The 425 MHz RFQ string meets 91% of its peak design transmission at 360 Hz.  All RFQs are operating at 80% of their design duty factor, causing a further reduction in achieved average current.

Much of the falloff in beam transmission as the repetition rate increase from 60 Hz to 360 Hz occurs in the stripper/MEBT, and is due to several factors.  Because of the presence of neutralizing electrons, it is difficult to precisely apportion losses between the stripper and the MEBT.  But our best understanding of the efficiencies is as follows.  Measurements made on the spectrometer test stand showed a maximum stripping efficiency of 83% in argon.  When operating in nitrogen under typical operation, the typical stripping efficiency is expected to be in the range of 75% at low repetition rate.  Thus 15 mA beam current into the stripper becomes 22.5 mA of He++ beam.  The transmitted current through the MEBT at 60 Hz is 21 mA when the MEBT is tuned for maximum throughput.  The difference (7%) is likely due to beam scraping in the MEBT.  When the MEBT is tuned for maximum 10.5 MeV beam, the transmitted current falls to typically 18 mA.  In this case, MEBT transmission is about 80%, with the remainder of the beam presumably lost to scraping in the MEBT.  At 360 Hz, with MEBT tuned for maximum 10.5 MeV beam, the transmission through the MEBT is 14 mA ( an additional drop of 22%).  The majority of the additional loss is probably due to the stripper, as the gas throughput is limited to the maximum capacity of the vacuum pumps.  Other contributing factors include a small drop in RF power and RFQ output as repetition rate increases to 360 Hz, and a possible small charge-exchange loss in the MEBT as the background gas pressure rises.

The performance of the device at 360 Hz can be summarized as:

Source - 100% of peak design current obtained.

LEBT - 100% of peak design current obtained.

212.5 MHz RFQ - 70% of peak design current obtained.

MEBT/stripper - 72% of peak design transmission obtained.

425 MHz RFQ string - 91% of peak design transmission obtained.

HEBT - 100% of peak design transmission obtained.

Duty cycle - 80% of design rate achieved.

The overall efficiency, 1 x 1 x 0.7 x 0.72 x 0.91 x 1 x 0.8 = 0.367, leads to 110 uA output current out of our 300 uA design.

Achieved vs. Design Beam Uniformity.

The HEBT section of the PET accelerator was designed to fold in the tails of the vertical beam distribution in order to make a more uniform beam at the target window.  This was done in order to spread the heat load of the beam more evenly on the window, in order to enhance its survivability.  Evidence is that we have achieved a beam uniformity of plus and minus 50% about a mean value over the desired window aperture.  This achievement is in reasonable agreement with the TURTLE design studies.  The achievement of 50% about the mean is twice the value of 25% that we had proposed as a shipping criterion for the accelerator.

The specifications for delivery of the PET accelerator were arrived at, as they usually are, by first doing an extremely careful design analysis of the entire accelerator and then by estimating how closely the actual implementation would come in achieving that design. The careful design study involved use of EGUN for source modeling, TRACE 2-D for LEBT modeling, TRACE 3-D for MEBT modeling, PARMTEQ for RFQ modeling, and TURTLE for HEBT modeling.  While the design value for the average current output from the device could be fairly accurately determined as a function of beam emittance from the PARMTEQ work, the beam uniformity specification could not easily be determined.  This is because 1) the TURTLE codes used in HEBT analysis were only capable of simulating 10,000 rays and 2) the beam distribution entering the HEBT was unknown.

The limitation in the number of rays simulated meant that the number of rays entering any individual pixel was in the neighborhood of 5-15, and statistical variations due to the small number of rays per pixel made an accurate assessment of the beam uniformity difficult.  Also, there is debate generally, and for the PET project specifically, about what sort of beam distribution one assumes for the input into the HEBT beamline.  While it is popular to assume a Gaussian particle beam distribution in each of three uncoupled phase space planes, actual beam distributions are often parabolic, uniform, or hollow and coupling between the phase space planes is often relevant.  Due to the uncertainties in beam distribution entering the HEBT, the approach taken was to use the 10,000 ray TURTLE code to model the HEBT assuming a Gaussian, uncoupled, three dimensional beam at the HEBT input.

The plan decided upon was to use quadrupole and multipole magnets inherited from the previous SDIO project in the HEBT.  The magnetic fields of these magnets were measured and those measurements were used in the TURTLE study. Drift lengths in the HEBT were varied until the beam size and uniformity on target achieved the desired characteristics.  The desired uniformity characteristic was that the beam have a uniform vertical profile and a Gaussian horizontal profile.  (See the end to end design report, available on the WWW.)

Modeling predicted, and experiment has verified, that the quadrupole magnet can be adjusted to vary the width of the horizontal Gaussian distribution. Thus, when the specifications for the machine were drawn up, there was a tradeoff between the amount of current one could deliver to the chosen target and the uniformity of the beam at that target.  (One could simply defocus the beam horizontally to achieve a wider, flatter Gaussian, throwing away the beam in the tails.  Indeed, this has been verified experimentally, as we have been able to achieve 25% uniformity of the beam, but at the expense of throwing away about half of that beam.)   To date we have yet to achieve 150 µA of average current even when the beam is focused tightly at the target.  For that reason we do not have the luxury of discarding beam at the target location, and we have a less uniform beam than specified originally.

Beam Studies.

It was strongly suggested by DOE and national lab reviewers that detailed beam studies be done at every point along the machine.  The source and LEBT beam emittance was studied in great detail, as was the beam emittance with and without a stripper at 1 MeV.  The 1 MeV beam throughout the MEBT was carefully studied using wire profile monitors, a spectrometer magnet, an emittance scanner, and a spectrum analyzer.  5 MeV beam studies were also done.  At each step the measurements are in quite good agreement with the final beam optics design.

Pointer to More Detailed Documentation.

This report is meant only to convey the nominal design of the PET accelerator, and is not meant as an all encompassing detailed study.  For more detailed information on the various beam sections the reader is referred to the documents entitled: ÒLEBT 96Ó; ÒMEBT 95Ó; ÒMEBT 96Ó; ÒReport on End to End Simulation of RFQ A, B and CÓ; and ÒHEBT 96Ó.  All reports are on the PET Project's World Wide Web Site or can be obtained from the office of the PET project manager.

Operations with the New 212.5 MHz RFQ.

The original 212.5 MHz RFQ was replaced in October, 1997.  The primary reason for the replacement was corrosion in the vane water passages.  There were grave doubts that the original 212.5 MHz RFQ would survive through 1998.  Since the 212.5 MHz RFQ could only produce 70% of its expected peak output current, a redesign of the vane structure was also done.  The new vane structure was predicted to lead to greater beam output from the 212.5 MHz RFQ, but it was also predicted to lead to more scraping of beam in the MEBT, since the MEBT was designed assuming output conditions from the original RFQ.

Accurate measurements of emittance and Twiss parameters exist only for the old 212.5 RFQ.  Measurements to date indicate that he new 212.5 MHz RFQ produces significantly more beam (18 mA peak) than the old RFQ but much of the additional current is lost in the MEBT/stripper.  Unfortunately we did not have the opportunity to re-measure output emittance and Twiss parameters for the new RFQ, due to budget and schedule constraints. Without such measurements it is difficult to ascertain specific performance characteristics.  It has been noted that beam transmission through the MEBT peaks at significantly different magnet settings than the total 10.5 MeV beam transmission peaks.  This may be indicative of beam scraping, which could be caused by either a larger output emittance in the new 212.5 MHz RFQ, or a mismatch in Twiss parameters.  Some additional scraping, due to a mismatch in Twiss parameters, was expected.

Where and Why the PET Accelerator Fails to Meet Expectations - Summary.

Original 212.5 MHz RFQ Operation - Identifying Where Expectations Fell Short.

With the original 212.5 MHz RFQ the PET accelerator had clearly measured problems in the 212.5 MHz RFQ transmission, MEBT/stripper performance, and 425 MHz RFQ string performance.  In each case, failure to achieve design goals can be attributed to overly aggressive initial design parameters.  At each step of the design process numbers were chosen that represented the upper limits of possible theoretical designs.  The project was originally sold through the proposal process as 300 mA electrical 3He accelerator, and the design had to be very aggressive in order to achieve this.

As shown in detail above, those sections which do not meet the design are:

Duty cycle - 80% of design rate achieved.

212.5 MHz RFQ - 70% of peak design current obtained.

MEBT/stripper - 72% of peak design transmission obtained.

425 MHz RFQ string - 91% of peak design transmission obtained.

It was expected that the duty cycle of the RF power units would be in the range of 2 - 2.5%.  The higher (more aggressive) value was used in our design study; but the lower limit was what we have been able to achieve in practice.

The pre-stripper RFQ design originated with the earlier SAIC/UW project. The earlier project design specified a 20 mA output from the pre-stripper RFQ.  Operations during that project were reported to be about 18-20 mA, although the documented beam currents from that project were less than this number. Based on the oral reports of 1992 performance and modeling, 20 mA was chosen for our design.

The MEBT was predicted to transport between 55% and 100% of the beam, depending on space charge considerations.  The stripper was measured to convert 80-85% of beam into doubly charged 3He when operating at 60 Hz or less, and 70% when operating at 360 Hz.  Again, the most aggressive parameters were chosen for design values.

The 425 MHz RFQ string was predicted to have between 16.8% and 60% transmission, strongly depending on input emittance.  Measurements excluded the 60% value from possibility, so the most optimistic value of 43% was chosen for our design.

The transmission designs led to a prediction that the PET accelerator could achieve up to 300 uA of average current.  Realizing the aggressiveness of the design, a value of 150 uA average current was chosen for the shipping criterion of the accelerator.

Underlying Reasons for Lower than Desired Transmissions.

In summary, we have identified three major causes for the lower than desired transmission.

1.  Overly-aggressive goals. It is clear that the present project made aggressive goals for beam emittance and transmission in order to achieve the 300 uA of average current stated in the original proposal.  The value for transmission of the old 212.5-MHz RFQ of 83% quoted in the end-to-end simulation was based on the original 1990 design.  It was not confirmed in experiment or simulations performed in the present project.  The RFQ design used a value for the assumed beam emittance of 0.5 p mm-mr, 90% normalized.  Under such an assumption, beam transmission through all of the RFQs becomes much greater (see below), and 300 uA of average current is readily obtained.  Unfortunately, measured emittances from the LEBT through the MEBT are significantly higher.

2.  Falloff in performance from 120 Hz to 360 Hz.  We have experienced a larger drop off of MEBT/stripper transmission than expected as we go from 120 Hz to 360 Hz.  For example we have seen 47 uA of steady average current at 120 Hz, but only 110 uA of steady average current at 360 Hz.  As described above, the majority of the shortfall is due to increased gas loads in the stripper.  Despite the pulsed nature of the stripper, at 360 Hz the gas load on the vacuum pumps reaches their pumping capacity.  This fact requires us to lower gas flow into the stripper region, below that which would be experimentally optimal as scaled from 120 Hz operations.

3.  Duty factor.  Finally, duty factor (beam pulse length) has been limited by the RF equipment to 2% instead of the originally proposed 2.5%, a significant limitation.

3He+ Duoplasmatron Ion Source

Introduction

The ion source for the PET Project is a standard duoplasmatron type ion source operated at high peak power (7.5 kWatt) and modest duty factor (~3%, i.e. 360 Hz, 80 microsecond pulse) with helium.  Twenty-five milliamps of 3He beam at 21.5 kV is extracted from the source for injection into the first RFQ.  4He is used for startup and maintenance of the source to save on 3He cost.

Fig. 2.2 Pet Duoplasmatron Ion Source

General operation

The source uses a heated oxide coated (barium and strontium oxide) filament as an emitter of electrons.  A pulsed "arc" voltage between the filament (-) and source anode (+) extracts and accelerates the electrons into the He gas, ionizing the gas within the source and producing a dense plasma while the arc pulse is on.  The produced plasma diffuses throughout the source.  A strong magnetic field between the iron poles of the intermediate electrode and the anode converges on the anode aperture.  This field pinches the plasma through the small aperture and into the expansion cup from which ions are extracted.  A small aperture (0.5-mm dia. x 0.25-mm long) is important for minimizing the gas flow from the source to conserve the usage of 3He, maintain a good vacuum in the extraction region, and minimize vacuum pumping.  Typical pressure in the plasma generating region is 1-1.5 Torr and several times 10-6 Torr in the extraction region.  With the source at +21.5 kV and the extraction electrode at ground potential a 21.5-keV 3He+ beam is extracted.  Just before the extraction electrode is an electron trap electrode (-1 to -4 kV) which traps electrons within the beam to assist neutralization and prevents electrons from being accelerated back onto the source.  This may also improve the intensity slightly and give some focusing to the beam.

Performance

For the needs of this project the source is expected to have:

¥	25-mA 3He+ beam (peak),

¥	80-µsec pulse width,

¥	360-Hz repetition rate,

¥	low emittance,

¥	low gas consumption,

¥	long lifetime (3 months), and

¥	reliable operation.

The source has shown that it can meet these objectives, with the exception of long lifetime in recent history.

The source typically produces 23-25 mA of 3He beam at the extraction voltage of 21.5 kV which is the injection energy for the following RFQ accelerator.  A beam of ~26 mA is the theoretical (Child-Langmuir) limit for this extraction gap (10.6 mm), aperture (6.6 mm) and voltage (21.5 kV).  The estimated beam emittance for the initial 21.5-keV 3He beam, extrapolated from the emittance measured at the end of the 21.5 keV line (LEBT) is approximately 0.8-1.0 p mm mr for the normalized (90%) emittance.

For accelerated beam in the RFQs and isotope studies the source operates on 3He gas.  To conserve 3He and operational cost, the source is started and operated on 4He whenever beam is not needed for extended periods of time.  Switching from 4He to 3He or back requires 3-4 minutes and is done by opening and closing two valves through the control system.

The source operates at the full 360 Hz, with an ~80 microsecond pulse width (~2.8% duty-factor).  It has operated for at least two long periods of 3-3.5 months without failure.  During these periods the source was on at least 90% of the time and only turned off when necessary for accelerator work.

Unfortunately the source hasn't always been this good in terms of lifetime.  There have been periods when the source didn't operate or failed within a few days due to filament failure.  Recently it has operated for only 1-3 weeks before the filament loses emission and fails due to poisoning from a contaminant.  However, during these times the other objectives of the source were essentially met so long as the source was given sufficient attention to maintain operation.  It is expected that 3-4 months of reliable and easy operation can be achieved with further investigations and improvements.

Modifications

The original source was a commercial duoplasmatron for producing hydrogen ions at a low duty-factor (<1%).  For the PET Project several modifications were necessary.  It could not operate at 360 Hz with a pulse length of 80 µsec without over heating the filament.  A large gas consumption due to a larger aperture and several misplaced vented screws were also found.  A change in some of the electronics was also desirable.

Filament

To achieve a useful lifetime (a few months), it was necessary to make significant changes to the filament.  The original filament, made of nickel wire mesh, would not withstand the heating by the plasma at full duty factor (The accelerator is designed for 2.5% duty cycle and the source provides a wider beam pulse for a duty cycle of 2.8%).  Heating and helium bombardment would make the nickel brittle so that it cracked, developed voids, and broke within a few days.  Nickel, being an active metal, absorbs helium and becomes brittle.  Changing to a molybdenum wire mesh for the filament overcame this problem.  With molybdenum there is significantly less damage from helium bombardment so the mesh remains flexible throughout its lifetime.  The higher melting point of molybdenum gives more latitude for conditioning and heating the filament and allows operation at the full duty-factor.

Fig. 2.3 Source filament.

To use molybdenum, new assembly techniques needed to be developed.  Spot welding molybdenum is rather difficult due to the high melting temperature.  However, spot welding molybdenum to nickel works well, so the molybdenum mesh is spot welded to nickel rods utilized for current leads and support.  Since the rods are relatively large they do not get hot enough to melt.  In places where the molybdenum mesh is folded for additional strength, a thin strip of nickel is placed between the fold to strengthen the weld.  This has made working with molybdenum filaments rather simple and easy.

In the duoplasmatron source it is customary to use an oxide coated filament to produce the necessary electron emission, at a reasonable temperature, for high plasma production, hence it is important to understand the oxide coating on the filament.  The initial coating material is a powdered mixture of BaCO3 and SrCO3 - purchased commercially and called a "radio mixture" in the electrochemical industry.  It is mixed with a solvent to form a slurry with which the final shaped mesh can be coated.  After the filament has fully dried it is heated in air to ~300oC to burn away the solvent.  The final conditioning, to convert the carbonates to oxides, is done in a good vacuum.  The carbonates decompose starting at ~950oC converting to an oxide which is complete at ~1100oC.  Thus it is important to reach a sufficiently high temperature to fully produce the oxide coating.  While outgassing the solvent, H2O and CO2 develop.  The heating should be controlled so the pressure does not exceed 0.2 Torr.  Once the outgassing ends and the vacuum is 10-5 Torr or better, activation is done by placing several hundred volts between the filament (-) and a close metal surface (+).  When fully activated the emission should be several hundred milliamperes at 100 V or less.  Following conditioning, storage should be in an inert atmosphere.  The filament should be in air for a minimum time to reduce contamination and conversion of the oxide to a hydroxide (Ba(OH)2).  Once placed in the source the filament will need to be outgassed and conditioned again, but for a much shorter time.

Gas consumption

To minimize the usage of 3He gas, it was necessary to close all unnecessary openings across the anode surface.  This required removing a few openings that vented the gas to the high vacuum region.  In addition it was possible to reduce the anode aperture from 1 mm to 0.5 mm.  The present helium gas flow for operation is 2-3 SCCM (standard cubic centimeters per minute).  This represents a 3He consumption of ~1 liter(stp) per an 8-hour period (1 liter(stp) of 3He gas costs ~$100).

Electronics

Using a combination of ideas from Fermilab and SAIC, an arc modulator supply was developed that was simple, efficient and has been very reliable.  The arc modulator was reduced to essentially three parts.  A PFN (pulse forming network) to store and provide a minimum of energy during the pulse, a charging power supply to recharge the PFN between pulses, and an IGBT (insulated gate bipolar transistor) solid state device to switch the pulse on and off.  A modulator of this type has been operating on the source for over a year switching 50-100 A, 100-300 V at 360 Hz without failure.  The complete unit is in a 9-inch-high standard chassis and produces little heat.  The triggering unit requires a 5-V gate to turn the IGBT on and off.

Fig. 2.4 Basic arc modulator circuit

Improvements

Source

A significant difficulty with long term operation (~3 months or more) is the filament lifetime due to poisoning from contamination.  As the oxide coated filament becomes poisoned it must run hotter to compensate for what would be a loss in emission.  As the temperature increases the filament eventually destroys itself.  Contamination has been found to come from several areas.

Water vapor was found coming from the plastic support insulators holding the source and extraction electrodes after they were in air for a few months during a summer shutdown.  When vacuum was reestablished the LEBT chamber supporting the source would only pump down in the 10-6 Torr range and the filament failed to achieve good emission when installed in the source.  Very large amounts of water vapor and some hydrocarbons were observed in the gas spectra.  After the chamber insulators and parts were cleaned and vacuum baked, the vacuum improved to the low 10-7 Torr and the source operated well.  The chamber support insulators and epoxy parts can be used but they must be carefully maintained and outgassed for good source operation.  Ideally it would be desirable to change to ceramic insulators and remove all internal gassy parts from the vacuum system.

Recently the gas handling system was relocated.  This was useful for removing the valves and gas controls from the high voltage enclosure which reduces the electronic components at high voltage and their potential for failure.  It also moved the He bottles from the ion source electronics rack and placed the gas assembly in a convenient space at ground potential and closer to the source.  Connecting to the source required  approximately a 15-foot length of tubing to prevent discharges through the gas line.  The end result decreased the time to change from 4He to 3He (or back) from ~15 minutes to ~3 minutes.  Unfortunately an SO2 contamination was recently observed which appears to be coming from the long Teflon-type gas feed line.  Sulfur, among many other things, is a known contaminant for oxide coated filaments.  It slowly poisons the filament, requiring it to run hotter and causing it to fail after one to three weeks from over heating.  Different tubing and possibly glass is being considered for this line.

If the source were to be used for long term or in a clinical environment, significant redesign should be considered.  The filament is poorly supported since the feedthroughs are weak and ceramic beads are used to keep the filament shield from sagging and touching the intermediate electrode.  Unfortunately the filament parts connect to the intermediate electrode base plate.  This plate is small and held by screws to the intermediate electrode making it difficult to modify.  A better arrangement is to mount the filament from an insulated base plate on strong feed through insulators.  A threaded collar rather than screws would facilitate filament changes.

Several other areas of the source could be improved.  The intermediate electrode has shown some erosion and should be designed so its front can be replaced.  A smaller anode aperture made of tungsten should be placed over the source anode. Since this source is a commercially produced item there are no complete drawings available.  Before the source could be used by untrained personnel considerable rework and possibly a new design with drawings, would be needed.

Electronics

The arc modulator is a Fermilab-SAIC designed unit that operates with excellent reliability.  The magnet supply is a commercial power supply.  The source pressure is measured by a barotron gauge.  These units are all at high voltage and are monitored and controlled through the control system, which is also at the extraction voltage (21.5 kV).

The current to heat the filament comes from an ac power transformer which is manually controlled with a Variac.  Since the filament current is seldom adjusted, once the source is operating, it has been adequate but there is no remote control or monitoring.  Remote control and monitoring of this function would be desirable.

The filament temperature should be remotely monitored.  Since the filament is at the arc potential (~150 V, 50 A), the thermocouple signal, a few tens of millivolts, has considerable noise.  A useful signal of the temperature has not been implemented in the control system.  Instead a panel meter shows some measure of the filament temperature.

Improvement of the filament supply and filament temperature monitoring are desirable but do not prevent present operation.  Complete spare supplies are planned in the future.

Summary

The duoplasmatron source is capable of achieving the objectives of the present PET Project.  It has on several occasions fully met the objectives.  On several other occasions, however, it failed to have a desirable or even useful lifetime primarily due to contamination problems.  In one case this was found and corrected by cleaning and baking insulators.  The present case is under investigation but a contamination from the gas feed tube appears likely.  Contamination is a serious problem for ion sources.  Following good vacuum practices and using good vacuum material are mandatory.  Contamination has been the greatest difficulty with using the PET source but it is an obstacle that can be overcome.

Several things which could be done to further improve the source have been mentioned, such as:  ceramic support and electrode insulators; removing or isolating parts in the LEBT vacuum chamber; modifying the source assembly for better filament support and easier changing; and improving the intermediate electrode and anode.  These are relatively expensive changes and are not necessary for current operations with experienced personnel.  For the present project these would probably be more disruptive than beneficial.  However, if this project were to go into a further accelerator development phase, these modifications would be beneficial.

The ion source design is discussed in more detail in the document entitled ÒLEBT 96Ó (available on the WWW).  The beam optical performance of the ion source is in excellent agreement with its design.

Low Energy Beam Transport (LEBT) Section.

The LEBT design is discussed in the document entitled ÒLEBT 96Ó (available on the WWW).  The beam optical performance of the LEBT is in excellent agreement with its design.  Essentially 100% beam transmission is obtained, and the emittance has been measured to be 0.8-1.0 p mm-mr at the end of the LEBT.

As expected, some minor difficulties occurred during LEBT commissioning, and these have been solved over time.  The magnetic center of the LEBT solenoid was measured to not coincide with the physical center.  This required the solenoid to be moved somewhat away from center.  In its original incarnation the beam pipe that fit inside the solenoid was too large to allow for sufficient solenoid movement.  The original beam pipe was replaced by a smaller one, and that allowed the LEBT to function as designed.  A second issue is space charge neutralization within the LEBT.  As discussed more fully in ÒLEBT 96Ó, the ion optics of the solenoid appear to be best modeled under an assumption of full space charge neutralization.  This neutralization of course depends on gas pressure in the LEBT.  We have experimented with a technique that bleeds small amounts of argon gas (1-2x10-5 Torr) into the LEBT region to assist space-charge neutralization.  Throughput of the 212.5 MHz RFQ and subsequent components increases approximately 10% by this technique.  As the reliability of the remainder of the accelerator improves, this technique may be revisited as a potential performance enhancer.  Transported beam currents quoted above are in the absence of LEBT gas injection.

Pre-stripper and Post stripper RFQ

Introduction

The PET RFQ accelerator consists of four RFQs (pre-stripper RFQ, post-stripper RFQ A, B and C).  In this chapter, general RF structure and tuning, design, basic operation results, existing problems and possible future improvement of these RFQs will be discussed.  Since the project started at Fermi lab, all three original RFQs (pre-stripper RFQ and post-stripper RFQ A and B) have been re-built and a fourth RFQ (post-stripper RFQ C) has been added. The re-built post-stripper RFQs A and B are the same as the previous ones. The contour of the vane tips of the re-built pre-stripper RFQ was slightly modified, but the basic RF structure was kept the same. The basic RF structure of the new RFQ C was also kept the same as the RFQs A and B. The decision not to change the RF structure such as the aperture is due to several reasons: the available RF power, the time schedule and budget limit of this project which has been reported in the general introduction section of this report.

RF Structure and Tuning

The pre-stripper RFQ has a segmented 4-vane structure: ÒwindowsÓ were cut through the vanes1 to reduce the radial dimension of the RF cavity. There are three ÒwindowsÓ in each quadrant: one is at the middle and two are at the ends of the vanes (Figure 2.5). One extra benefit of this segmented 4-vane structure is that it moves the frequency of the TE210-like mode (the operating mode) below that of the TE110-like  mode (the dipole mode). However these windows disturb the longitudinal uniformity of the field which has been confirmed by both field measurement and calculation (using computer code MAFIA).

The post-stripper RFQs are typical 4-vane type RFQs: there are no windows. All three post-stripper RFQs are connected together. (There is an end wall between each other.) These RFQs are individually powered by separate RF amplifiers.

The vanes and cavities are made of copper plated aluminum. RF joints between the vanes and the cavity are made by pure pressured contact.  Each vane is pulled against the cavity housing by 39-42 screws to maintain the integrity of the contact.  The vanes are adjustable: they can be pulled down, pushed up or tilted by adjusting these screws (Figure 2.6).

All RFQs were tuned by mechanically adjusting the vanes while the RF field was measured by a field perturbation method. The final goal for tuning is that the dipole component of the field must be less than 2% of the quadrupole mode. Actually this ratio reached 1-1.5% after tuning. The perturbation method used for tuning the post-stripper RFQs was to insert a metal cylindrical bar through the holes on the cavity housing into the outer region of the cavity. A better perturbation method was developed for tuning the pre-stripper RFQ: a small bead sitting inside a hollow plastic straw was inserted into the cavity until the straw touched the vane. Two types of beads were used, plastic and metal. The advantage of this method is that it can obtain exclusive field information near the critical region - the vane tip. A beadpull method was also implemented in this region, however the thread used in the beadpull introduced a large perturbation which imposed an impractical restriction on the accuracy of thread positioning. It also was proven by the measured field data that the straw-bead method is better than the beadpull method.

RF power is coupled into the cavities through a 1-5/8 inch coax line and a magnetic coupling loop (drive loop). Each RFQ has only one drive loop.  The vacuum window for the drive loop is made of Rexalite with o-ring  seals.

In each quadrant, there are 23-25 holes (diameter of 0.5 inch) on the wall of a cavity housing. These holes are used for maintaining the vacuum inside the cavity. Three of these 23-25 holes are used to insert a small pickup loop. They are located at the middle and near the ends of the cavity. All pickup loops in a single RFQ are adjusted to have the same coupling value to within 0.25 dB (nominal values range between -47 ~ -50 dB). These pickup loops provide the operator with a tool to monitor the RF field at 12 positions (3 pickup loops in each quadrant) during operation. Currently only two loops are used in each RFQ cavity for feedback.

Figure 2.5.  Schematic Drawing of Pre-stripper RFQ (segmented vanes, RF cavity and vacuum tank)

Figure 2.6.  Adjustable Vanes and RF Cavity

Pre-stripper RFQ

Design goal

The original pre-stripper RFQ was designed and built at SAIC. The one used now is a slightly modified one.  This RFQ is designed to accelerate 3He+ ions from 21.5 keV to 1 MeV with a transmission efficiency of 80% (or better) for an injected current of 25 mA.

Design parameters

The computer program PARMTEQ (SAIC version) was used to do beam dynamics design and simulation and the computer program RFQVG (SAIC version) was used to generate the data file of the contour of the vane tips. The pre-stripper RFQ was designed with constant aperture (r0) and constant transverse radius.  (Here the aperture (r0 ) is a commonly used term in RFQ design back to the 1970s. It is not the minimum radius (a) of the vane tips. Rather it may be regarded as a characteristic average radius of the RFQ vane tips. The designed r0 is 0.25 cm while the minimum radius of the vane tips is 0.174 cm.)

The detailed design parameters are listed in Table 2.5. The data of the contour of the vane tips is in document drawing #905A30141-905A30142.

Table 2.5. Design Parameters of the new Pre-stripper RFQ

| Particle | 3He+ |
| --- | --- |
| Frequency (MHz) | 212.5 |
| Aperture ro (cm) | 0.25 |
| Modulation (at end of buncher) | 1.78 |
| Input energy (MeV) | 0.0215 |
| Output Energy (MeV) | 1.0 |
| Inter-vane Voltage (kV) | 57.0 |
| Maximum E Field (MV/m) | 32.2 |
| Maximum E Field (MV/m) (at middle) | 41.2 |
| Q0 (MAFIA)/measured | 7600/6100 |
| Power (kW) (MAFIA, without beam) | 65.3 |

Power(kW)(needed, without beam)

| (power x Q0 )(MAFIA)/(measured Q0) | 81.4 |
| --- | --- |
| Pulse Width (ms) | 70 |
| Repetition Rate (Hz) | 360 |
| Inject Current (mA) | 25 |
| Transmission | 80% |
| Number of cells | 151 |
| Length (cm) | 103.965 |

Design note

Both the experimental and simulation results showed that the transmission of  the original pre-stripper RFQ was about 65%.  Therefore a modification on the contour of vane tips was made to improve the transmission when the pre-stripper RFQ was redesigned. However there was a restriction on the modification: the total length of the vanes must be kept the same as before in order to fit in the vacuum vessel. The buncher section was made longer and the inter-vane operating voltage was increased from 54 kV to 57 kV. This operating voltage corresponds to a 32.2 MV/m maximum surface field (2.1 times Kilpatrick limit) which  should not cause a sparking problem. (The formula used to calculate the Kilpatrick limit is the one used at Los Alamos Lab: f = 1.643E2 e-8.5/E , where f is frequency in MHz and E is breakdown field in MV/m. This formula was transformed from the original Kilpatrick formula at Los Alamos lab. The Kilpatrick limit is only an empirical criterion predicting the possibility for electrical breakdown to occur at a given frequency and field. Tests at various accelerator labs have shown that electric fields as high as several time the Kilpatrick limit can be used without causing breakdown.)

The RF power needed to get the designed inter-vane voltage is ~81.4 kW (without beam). (This is calculated by comparing the power and Q calculated by the 3D RF design program MAFIA with the measured Q: power (needed) = power(MAFIA)* Q(MAFIA)/Q(measured).) The total RF power needed for accelerating 25 mA beam to 1 MeV is 106.4 kW.

The RF field in the pre-stripper RFQ is not longitudinally uniform (it is 28% higher at the middle of the RFQ) due to the introduction of windows in the vanes. This has been proven by measurement and agrees with simulation. Therefore the surface field at the middle of the RFQ is about 41.2 MV/m (2.7 times the Kilpatrick limit) at the designed power level (81.4 kW without beam). The corresponding Òinter-vane voltageÓ at the middle of the RFQ is 73 kV.

One should bear in mind that the field and power quoted here are based on the modeling results using the MAFIA code. Due to the complicated geometry of the RFQ, it is not unusual that such modeling results in 10% or higher inaccuracy.

In the design, the last four cells of the vanes are modified (the aperture was gradually increased while modulation was gradually reduced to 1) to make the transverse phase spaces of the output beam close to each other (diverging) in both the x-xÕ and y-yÕ planes. This is to reduce the large divergence originally present in one plane 3.

Due to machining difficulty caused by the position of the water cooling channels, the contour of the vane tips at the exit end of all vanes were slightly modified from the data file generated by RFQVG  to raise the vane tip by ~0.0-0.025 inch. The data in final drawing files 905A30141 and 905A30142 reflect this change.

Simulation results

Simulation results show that the transmission is 80% for the input parameters at the designed inter-vane voltage (57 kV) with no significant emittance growth.  If the operating voltage is increased to 20% above nominal, the transmission can be 87.6%. Shown in Fig 2.7 is the transmission versus the inter-vane voltage. Detailed simulation results have been reported in other documents4,5.

Since the RF field is not longitudinally uniform, a modified version of PARMTEQ was developed at SAIC which can incorporate such an effect into the simulation. The results from this version of simulation show that there is no significant increase of beam loss.

Figure 2.7.  Transmission Efficiency of the Pre-stripper RFQ (simulation results) for  0.5 ¹ mm mrad.

Operation results

Operation results with the new RFQ show that an output current of 18 mA has been obtained out of 21 mA injected current at 120 Hz of repetition rate. This 85% transmission efficiency is better than the designed transmission efficiency (80%). The RF power required for this performance is about 94-100 kW which is also in agreement with the designed value (99.4 kW for 18 mA). The injected emittance, however, is 60-100% larger than the value chosen for the design. This means this RFQ  actually exceeds the design goal. The output emittance, of course, is also larger than the designed value for next stage of RFQs.  Note that the currents into and out of the RFQ are measured on current toroids only, and that we have not done measurements with an emittance scanner or a suppressed Faraday cup.  Therefore these measurements are not as accurate as one would like.

A frequently asked question is how the operating voltage was determined. The operating voltage (inter-vane) was determined by power scanning: gradually adjusting RF power and looking at the transmission efficiency. From the scanning, the power needed to start accelerating beam at high transmission efficiency (beginning of a plateau) can be determined. This power is compared with the power needed (calculated from MAFIA results and measured Q) to determine the operating voltage. For example, recent data show that the operating power is 94 kW to get 18 mA output current. This means that the power for the RF field is ~76-77 kW . Compared with the 81.4 kW power needed from the MAFIA simulation (adjusted by the measured Q), the 76 kW power gives an operating voltage 0.97 times the designed operating voltage. Taking into account the possible deviation from the MAFIA simulation to the real field, we believe the 76 kW is very close to the designed inter-vane voltage (57 kV +/- 5%).

The X-ray spectrum was also used to calibrate the operating inter-vane voltage. X-ray measurements at an RF power level ~120 kW show that the majority of the photon energy is around 67 kV (plus and minus 20%) while the high end of the photon spectrum is at 90 keV. Using 120 kW and 90 keV high end energy, a simple calculation shows that  the highest Òinter-vane voltageÓ at 76 kW is 71.6 kV (at middle of the RFQ) which corresponds to a minimum 56 kV inter-vane voltage in the rest of the RFQ.

This RFQ has been run at designed or higher power level for a long time without a sparking problem. This fact proves that the operating voltage is not very close to the sparking limit.

Post-stripper RFQs

Design goal

The original design of the post-stripper RFQs had two RFQs to accelerate 3He++ ions from 1 MeV to 8 MeV. Later on, a decision was made to add a third RFQ to increase the final energy to 10.5 MeV. The total transmission efficiency (from entrance of RFQ A to exit of RFQ C) is 60% with aforementioned emittance.

Design parameters

All three post-stripper RFQs have similar RF structure. They have only acceleration sections with constant aperture (r0) and constant transverse radius. (The r0 is 0.18 cm and the minimum radius of the vane tips is 0.1097 cm for all three post-stripper RFQs. The definition of r0 has been explained in a previous section.)

The basic design parameters are listed in Table 2.6. The data of contour of vane tips are in document drawings #905A35101-905A35104 and 905A35163-905A35164.

Design note

The length of vanes for all RFQs is limited by the fabrication capability (~ 148 cm) of the available computer controlled milling machine. The corner at each end of the vane tip was chamfered (1/4 circle with radius of 0.5 cm) to facilitate a smooth end. The gap between the end of a vane to the end wall of the cavity is 0.5 cm. The thickness of the end wall is 0.16 cm. Adding all these lengths together, there is a 2.16 cm drift space between each post-stripper RFQ (Figure 2.8). Strictly speaking, this drift space is only an approximation since it is not a pure (field free) drift space. However the fact that the transverse RF field in this region is much smaller than in the acceleration region warrants the approximation. It should be pointed out that the thickness of the end wall is only 0.16 cm and the rest of drift space is for RF structure.  Therefore the total 2.16 cm space is almost the minimum space needed for connecting two separate RFQs.

The designed inter-vane voltage is 58.4 kV (RFQ A and B) and 59 kV (RFQ C) corresponding to a ~39.9-40.3 MV/m maximum surface field (~2.0-2.025 times Kilpatrick limit) which should not cause a sparking problem. The RF power needed to get the designed inter-vane voltage is 71-77 kW (without beam). The method to estimate this power has been described in pre-stripper RFQ section.

Table 2.6  Design Parameters of the Post-stripper RFQ

| Particle | 3He++ | 3He++ | 3He++ |
| --- | --- | --- | --- |
| Frequency (MHz) | 425 | 425 | 425 |
| Aperture r0 (cm) | 0.18 | 0.18 | 0.18 |
| Modulation | 2.1 | 2.1 | 2.1 |
| Input energy (MeV) | 1.0 | 5.05 | 8.025 |
| Output Energy (MeV) | 5.05 | 8.025 | 10.54 |
| Inter-vane Voltage (kV) | 58.4 | 58.4 | 59.0 |
| Maximum E Field (MV/m) | 39.9 | 39.9 | 40.3 |
| Q0 (MAFIA)/Q0(measured) | 9500/7800 | 9500/8900 | 9500/8900 |
| Power (kW) (MAFIA) | 63.0 | 67.0 | 68.3 |

Power(kW)(needed, without beam)

| (power* Q0)(MAFIA)/Q0(measured) | 76.7 | 71.5 | 72.9 |
| --- | --- | --- | --- |
| Pulse Width (ms) | 70 | 70 | 70 |
| Repetition Rate (Hz) | 360 | 360 | 360 |
| Inject Current (mA) | 28 |
| Transmission | Table 2.7 | Table 2.7 | Table 2.7 |
| Number of cells | 86 | 61 | 51 |
| Length (cm) | 137.1 | 146.04 | 145.58 |

Figure 2.8.  Transition Region between Post-stripper RFQs, arrows direction of Beam.

RFQ vane tips are depicted.

Simulation results

Due to the special configuration of the post-stripper RFQs, beam loss can not be neglected. Therefore extensive simulations were carried out to study the details of beam loss in the post-stripper RFQs. In addition to the SAIC version of PARMTEQ, another version of PARMTEQ from Argonne National Lab was used to check the results. This version is substantially different from the SAIC version in that it uses a finite element method to establish RF fields and includes higher order terms of expansion coefficient of the RF field. The detailed results of these simulations have been reported before4,5.

Shown in Table 2.7 is the total transmission efficiency at the end of RFQ A, B and C. The table shows that total transmission from entrance of RFQ A to the exit of RFQ C is 60% (when inter-vane voltage is increased to 1.1 times designed value).  Shown in Figure 2.9 is the simulation results of total transmission efficiency versus the operating inter-vane voltage.

A simulation using Argonne LabÕs PARMTEQ yields higher transmission through the post-stripper RFQ A, but 10-20% lower or higher total transmission depending on the input parameters.

The beam loss in post-stripper RFQ A is a little higher than that in the acceleration section of a normal RFQ (see Table 2.7).  Simulation results show that this is mainly due to longitudinally mismatch and the larger transverse emittance. In a normal RFQ, when beam arrives at the acceleration section, it has been already bunched: the half length of the bunch is about 30 degrees for good transmission. However the input beam to RFQ A has a half bunch length of 65 degrees. If the bunch length can be shortened, the transmission can be increased to above 90%. Of course, if smaller transverse emittance or current is used, the transmission can be above 90% .

Simulation results show that the drift space between post-stripper RFQs is the major source for the beam loss in RFQ B and C since beam is transversely mismatched after drifting through this space. A possible solution to avoid this drift space problem is to join all three RFQs together. However this would require more study on possible problems such as mode coupling and power distribution which was beyond the scope of this project.

Table 2.7.  Simulation Results using the SAIC PARMTEQ code of Total Transmission of RFQ A, B and C with various transverse emittance.

(input current 28 mA,  65° half bunch length.)

| Emittance | Transmission at End of A | Transmission at End of B | Transmission at End of C |
| --- | --- | --- | --- |
| 0.5 ¹ mm mrad | 0.865 | 0.655 | 0.600 |
| 0.8 ¹ mm mrad | 0.675 | 0.490 | 0.377 |
| 1.05 ¹ mm mrad | 0.520 | 0.290 | 0.168 |

Operation results

Post-stripper RFQ A was commissioned first and the output current was measured. Then the whole string of RFQ A, B and C were commissioned. The beam current out of RFQ C was measured while the beam current out of B has never been measured due to the tight commissioning schedule.

Figure 2.9.  Transmission efficiency of Post Stripper RFQ (Simulation Results) for 0.5 ¹ mm mrad.

During the commissioning of RFQ A, a peak output current of 12 mA was obtained while the injected current was 20 mA (60% transmission efficiency.) The injected emittance, however, was 60-100% (0.8-1.07 p mm-mrad) larger than the value chosen for the design. The repetition rate of the RF pulses was 120 Hz.  With these transverse emittances, the simulation results showed that the transmission efficiency would range from 68% (0.8 p mm-mrad) to 52% (1.07 p mm-mrad).  Therefore this RFQ did perform as the simulation predicted. Note: the simulation does not depend upon the RF duty cycle.

An output current of  7 mA has been obtained at the end of RFQ C while the injected current into A was 18 mA (39% transmission efficiency). The injected emittance, again was 60-100% (0.8-1.07p mm-mrad, normalized, 90%) larger than the value chosen for the design and the repetition rate of the RF pulses was 120 Hz. With these transverse emittances and injected current, the simulation results showed that transmission efficiency would be ~34% (0.8 p mm-mrad) and ~32% (1.07 p mm-mrad).  Therefore in terms of transmission efficiency,  the whole string of post stripper RFQs did perform as the simulation predicted or even better. The operation at 360 Hz repetition rate is not stable at the time of this writing due to a variety of problems (see the operation section of this report). However, the data at the 120 Hz repetition rate is valid for the comparison between the design and the achieved value since the RF field and the beam parameters should be the same at both the 120 Hz and 360 Hz repetition rates.

RF power (with beam) used for the aforementioned current and transmission are: ~107 kW for RFQ A, ~90 kW for RFQ B, and ~85 kW for RFQ C with beam. These numbers correspond to the power levels (without beam): ~80 kW for RFQ A,  ~75 kW for RFQ B and ~78 kW for RFQ C. This means that the RF fields in the post-stripper RFQs were ~1.02-1.03 times higher than the nominal values which is also in agreement with the design. There was no x-ray spectrum measurement performed on these RFQs to determine the operating voltage, since we were convinced by the x-ray measurements on the pre-stripper RFQ that the operating power measurement could give relatively accurate information.

Summary of Performance, Problems and Future Improvements

As with all RFQs in operation, a natural (and frequently asked) question is: does this machine achieve designed values? To answer this question, first it has to be pointed out that currently the real beam emittances are 1.6-2 times the emittances chosen by the original design. Then the answer is: even with this emittance the new pre-stripper RFQ does provide transmission efficiency of as much as 85% which is higher than the designed goal, although measurement problems make this number suspect. The total transmission efficiency of the post-stripper RFQs is 39% which is comparable to the value predicted by the simulation design study reported before 2,3.  To facilitate understanding of the performance of these RFQs, the comparison of performance and design/simulation are listed in tables 2.8 and 2.9 (at 120 Hz of repetition rate).

Table 2.8.  Designed and utilized inter-vane voltage

|  | Pre-stripper |
| --- | --- |

Post-stripper

A

Post-stripper

B

Post-stripper

C

Inter-vane

| voltage (design) | 57 kV | 58.4 | 58.4 | 59.0 |
| --- | --- | --- | --- | --- |

Inter-vane voltage

| (utilized) | 57-60 kV | 58.4-61.3 kV | 58.4-61.3 kV | 59.0-62.0 kV |
| --- | --- | --- | --- | --- |

Table 2.9.  Achieved Transmission Efficiency and Simulation Results real emittance, 0.8-1.07 p mm-mrad, normalized transverse emittance.

New Pre-stripper

(21 mA inject current)

Post-stripper A-C

| (15.5 mA inject current) |
| --- |
| Transmission (simulation) | 80 % | 32-34% |
| Transmission (achieved) | 85 % | 39% |

What are the existing/remaining problems and can a better machine be designed and built?  They can be summarized as follows.

1.  The transverse beam emittance of 0.5 p mm-mrad chosen by the original design was too optimistic. Accordingly, the RFQs were designed with little room left for a beam with larger emittance. Larger emittance will impose a more severe challenge for an RFQ at this energy and frequency.

2.  The change in frequency from 212.5 to 425 MHz between pre and post stripper RFQs causes longitudinal beam dynamics problems (bunch length is effectively doubled) that are not totally solved by the MEBT. The buncher in the original design did not achieve the designed bunching effect due to beam charge neutralization while the alpha magnet MEBT is a good bunch length keeper instead of a real buncher. Therefore the bunch length is still too long.  In a conventional RFQ, the half bunch length of a well bunched beam in the acceleration section is about 30 degrees. The half bunch length of the beam injected into RFQ A is 65 degrees.

3.  Since it was not practical for this project to build a single long (~ 4.3 meters) post-stripper RFQ, three independent RFQs are used and this creates two drift spaces. Both drift spaces cause transverse mismatch and beam loss as has been verified with radiation surveys.

Based on these factors, a future design may wish to study the following improvements:

1. Reduce the emittance of the beam injected into the pre-stripper RFQ.

2.  An RF structure for bunching the beam injected into post-stripper RFQ A should be considered. This buncher should compress the half bunch length from 60-70 degrees to at least ~40 degrees. An innovative option may be to design an extra entrance section for post-stripper RFQ A to serve as a buncher.   Alternatively, one might attempt to bunch the beam more tightly at the exit of the pre-stripper RFQ, since the MEBT serves as a bunch length conservator, and the tighter bunching can be made prior to MEBT entry.  Lastly, one could consider an RF buncher near the end of the MEBT, where vacuum does not have to compete with gas stripping, and may therefore be adequate to allow for RF bunching of the beam.

3.  All post-stripper RFQs could be joined into one single RFQ. Drift space between RFQs is undesirable. Multi-meter long RFQs are being developed at Los Alamos National Lab and Lawrence Berkeley National Lab.

4.  The average aperture of the RFQs may be increased to accommodate larger emittances. However this approach is facing a limit. The radial focusing force of an RFQ is approximately proportional to l2v/ r02 where l is the wave length, v is inter-vane voltage and r0 is the average aperture. From this expression, one can see that when the aperture increases, the focusing strength decreases. In order to keep the focusing strength, the inter-vane voltage has to be increased much more than the aperture. The consequence is that the maximum surface field (which is proportional to v/r0 ) now is increased and will soon reach the sparking limit.

5.  Based on the aforementioned ideas, a preliminary design exists which shows that if average aperture is increased to 0.2 cm, inter-vane voltage is increased to 77 kV and modulation is decreased to 1.7, such an RFQ may have transmission efficiency of 95% for 28 mA 3He++ with transverse emittance of 0.8 p mm-mrad and half bunch length of 50 degrees. Even with the half bunch length of 65 degrees ( which means the buncher is still not in use) the transmission may still be 91%. The transverse emittance of 0.8 p mm-mrad is close to what is being injected into the post-stripper RFQs. For this design, the maximum field is 53 MV/m which is 2.7 times the Kilpatrick limit. This level of RF field is high and challenging, but it may not be impossible based on the results of RF breakdown tests performed in other labs. Therefore at the very end of this project, a careful test of the RF field limit could be conducted using our RFQs. Also the shape of the transverse section of the vane tips needs to be studied.  The power needed for such an RFQ would be about 500-600 kW (without beam).

Medium Energy Beam Transport (MEBT) and Stripper Section.

The MEBT section of the PET accelerator was the most challenging to design and build, and was, by far, the most scrutinized portion of the device during reviews and scientific meetings.  Due to its difficult nature, the MEBT was studied in great detail, as discussed in the documents entitled ÒMEBT 95Ó and ÒMEBT 96Ó, both available on the WWW.

The problem posed by the MEBT region was to match the rapidly diverging, rapidly debunching beam emanating from the pre-stripper RFQ into a second RFQ where the beam must again be bunched and be very small.  In addition to the matching constraint, the 3He+ beam must be stripped to form 3He++.  Since the beam has an energy of only 1 MeV, foils would not survive and a gas stripper had to be used.  The 1992 project learned that gas from the stripper would short out an electric RF buncher, and an alternate bunching strategy therefore had to be found for the present project.  In addition to matching and stripping the beam, it was desired that the MEBT region leave the PET accelerator as short as possible.  A schematic diagram of the chosen alternative appears above as Figure 2.1.

The MEBT design is based on the fact that faster particles take outward trajectories in bends to arrange for a system that passes all particles in the same time.  (The additional time required to traverse the extra distance in the bend is exactly offset by the time saved due to the fact that the particles are moving faster.)  Introduction of bending magnets into the beamline implied that the MEBT would have a dispersion function.  (The dispersion function h(s) is used to determine the horizontal offset, xh, of a particle from the ideal orbit because of its off-momentum, xh = h(s)(dp/p), where dp is the difference between the momentum of an arbitrary particle and the ideal beam momentum p.)  In order not to introduce undue emittance growth, which would lead to beam loss in the downstream RFQ string, it is required that both the dispersion, and the dispersion gradient, be reduced to very low levels by the time the beam enters the downstream RFQ string.  This led to the consideration of a MEBT design with a three dimensional waist at the center of the drift between the two bending magnets.  By using such a symmetry, the dispersion function, and the gradient of the dispersion function, would both be near zero at the exit of the second bending magnet.

A first concern regarding the MEBT design was space charge.  Implementation of the MEBT design required a beamline of considerable length (about 6 meters).  At this length, and with the low velocity (1/40 c) of the 3He particles, and with the large (28 mA) peak design current, space charge was a major concern.  An intense effort was made to model the MEBT section.  The original design was done using SCAT, a 2D code that includes some 3D effects (SCAT calculates dispersion as well as the energy at which a beam line is isochronous).  Next, the 3D nature of the MEBT was studied using TRANSPORT, a well known, widely used code.  Since TRANSPORT does not include space charge in the analysis, the MEBT design was also studied using TRACE 3-D.  Comparison between TRACE 3-D and TRANSPORT showed a discrepancy.  The root of the problem was traced to a disagreement in the R56 matrix element used in the codes.  Analysis from first principles showed that TRACE 3-D was the code with the bug; the author was notified and the code was fixed.  Once fixed, TRACE 3-D agreed with TRANSPORT on the zero space charge limit optics.  TRACE 3-D was then used to model both the linear and non-linear space charge effects on the beam optics.  The results of the study indicated that full space charge in a Gaussian beam would lead to beam loss of about 40-50%.  (An efficiency of 50%-60%.)  The linear component of space charge would move the final focal point (which should coincide with the entrance to the second RFQ) as a function of beam current.  Pulse to pulse and intra pulse beam current stability of 5% was deemed necessary to control fluctuations of the position of the focal point to an acceptable level under full space charge situations.  It was realized that space charge neutralization could offset the problems of space charge, and that a parabolic or uniform beam distribution would also be beneficial.  For these reasons, an efficiency of transfer in the MEBT was estimated at between 80% and 85%.  For full details, please consult the documents ÒMEBT 95Ó and ÒMEBT 96Ó.  The efficiency of the stripper was also estimated at between 80% and 85%, for a combined MEBT/stripper efficiency of 70%.  Since the particles come in singly charged, and leave doubly charged, the electrical current doubles per particle leaving the combined MEBT/stripper design efficiency as 140%.

A second concern regarding the MEBT design was the quality of the magnetic fields.  In the MEBT beam sizes range from under one mm to 43 mm.  Such a large ratio of beam size puts a premium on magnetic field quality where the beam is large.  Tracking studies (with a code specifically written for this project) were done that indicated a required magnetic tolerance of plus or minus 1.6 G out of the 4.1 kG fields in the dipole bends.  This in turn led to a machining tolerance of 0.5 mil for the pole pieces of the dipoles, which also used a multi-conic section design to achieve the desired field uniformity.

A third concern regarding the MEBT design was tunability.  The uncertain amount of space charge neutralization was one source of uncertainty in the design.  Modeling was done with both full and zero space charge, and a range of magnetic strengths were determined that would allow a match over the entire range.  In the MEBT, the quadrupoles used to confine the beam were very short, with magnetic cores about two inches long in the beam direction.  The pole piece separation is about equal to the length of the magnet, making 3-D effects a dominant contributor to the beam optics.  The uncertainty in accurately modeling for 3-D effects, and the uncertainty in the level of space charge neutralization, led to a desire to have as many tunable magnets present in the system as there are variables one wishes to tune for.

A fourth concern regarding MEBT design was compactness.  A guiding goal of the overall PET accelerator was to keep the device small and lightweight.  Since the MEBT folds the beam over, it contributes significantly to compactness.  But in order to keep things light, the dipole magnets were designed to have a bending radius as small as possible, which in turn limited the amount of straight section space available for the MEBT diagnostics, pumping and vacuum hardware.  This presented a challenging engineering problem which was solved during the construction of the MEBT.

Space charge had a significant effect on the design of the MEBT magnets, and the magnets were designed so that the MEBT could be tuned to meet its matching criteria in the presence of either full or zero space charge forces.  Optimizing the design required a different pole face rotation angle for the dipoles depending on the space charge assumption.  We chose the rotation angle appropriate for full space charge.  Operation has shown that zero space charge is more appropriate.  Thus the dipoles could probably be improved by shimming the pole pieces.  This improvement might bring about a 10% increase in MEBT/stripper transmission.

The 0.5 mil machining tolerance of the dipoles proved to be difficult for the vendor.  When the half cores came in, three of the four were measured to meet the specification.  The fourth was out of tolerance and sent back to the vendor.  It was worked on again, sent back again, and still out of tolerance.  Since they had made no progress, the decision was made to put the dipoles together and measure the fields.  The out of tolerance half core led to magnetic measurements that were just barely acceptable.

When the MEBT beam pipe was received it was found that the pipes (304 stainless steel) had become magnetic at the welds, despite our efforts inquiring about non-magnetic welding techniques.  POISSON studies indicated that magnetized welds would cause unacceptable field errors.  It was determined that annealing might restore the stainless steel to a non-magnetic state; a vendor was found to do this heat treatment, and the beam pipes were then acceptable (more details in chapter 12).

In the first phase of MEBT commissioning it was found that optimum operation was obtained with the last quadrupole, Q5, excited to the voltage limit of its power supply, with an associated current of 285 A (300 A is the current limit of the supply).  At this power level the magnet also became hot, as the upper limit of the expected power had been reached.  It had been realized that such an excitation might be required, but due to the uncertainties in space charge and fringe fields, the design went forward with a less robust quadrupole than the worst case would require.  Once experiment showed that more strength was indeed required, the decision was made to add 10 additional partial laminations to the quadrupole pole tips. (The original design uses 35 full laminations.  An alternative solution would have been to acquire a different power supply, but that alternative would have led to even more required power, further heating of the quadrupole, and would have been very difficult as the quadrupole iron was beginning to magnetically saturate.) This was a straight forward fix which resulted in successful MEBT operation.  The present optimum quadrupole excitation is 202 A with the operation temperature considerably below the klixon protection value of 70 degrees Centigrade.

Operation of the MEBT has been excellent, with beam transmission meeting the design specifications at low duty cycle.  (The fall-off of the MEBT/stripper transmission at 360 Hz is due to the stripping, and possibly recombination losses, not the beam optics or magnets.)  By appropriately adjusting each of the seven quadrupoles (five main and two trim quads) in the MEBT, the emittance was measured to be slightly less when it leaves the MEBT than its entry value.  (Presumably this is because of scraping of a portion of the beam in the MEBT region.  This scraping could be reduced by shimming the dipole entrance/exit edge angles as discussed above.)  Operation at current levels up to 21 mA shows that space charge is not the problem it was calculated to be; this may indicate the presence of beneficial neutralization caused by electrons trapped within the beam.  No emittance growth also indicates that the stripper caused no determinable emittance growth.  This latter effect was unanticipated, since a na•ve calculation based on widely used formulas indicated that an observable emittance growth was expected.

While the design of the MEBT was quite challenging, and its design scrutinized in utmost detail with grave concerns expressed, in practice it has operated with excellent reliability, and was commissioned on time.  The magnets were measured to meet their tight specifications in all cases, and were delivered on schedule.

The development of the  MEBT  is an important success of this project, and it led to the following achievements:

Identification and correction of a bug in TRACE 3-D, thereby enhancing the accelerator physics tools of the accelerator community.

Identification of a weakness in the prevailing interpretation of a widely used formula for multiple scattering caused emittance growth.  (JacksonÕs next edition of his classic text will more fully express caveats about the formula in question.)

Observation of minimal space charge problems in a 1 MeV, 20 mA 3He++ beam. Suggestive of neutralized transport due to electrons trapped in the beam.

Development of a new means to match bunched beam accelerators, which might be used in the future to match RFQs to linacs.

High Energy Beam Transport (HEBT) Section.

The HEBT design is discussed in the document entitled ÒHEBT 96Ó and is available on the WWW.  The beam optical performance of the HEBT is in reasonable agreement with its design.

As expected, some minor difficulties occurred during HEBT commissioning.  The quadrupole and multipole magnets have to be physically moved in order to center the beam depending upon their excitations.  (They presently steer.)

Early on in the project there were some concerns about the HEBT magnets overheating.  Increasing the beam energy to 10.5 MeV meant that the HEBT magnets had to be energized more for the present project than for the 1992 efforts, and the HEBT magnets were cooled by a cooling plate, not water cooled magnet wire.  Magnet measurements were made as a function of excitation current and it was determined that the HEBT magnets could be used.

The beam uniformity produced by the HEBT is a reasonable match to the TURTLE design studies.  Beam uniformity of plus and minus 50% about the mean has been obtained experimentally for all pixels within the desired radiochemistry target window area.  While this exceeds the specification of plus and minus 25%, it is adequate to begin targetry studies.  Further improvements are expected with experience.

References

1. http://www-linac.fnal.gov/pet

2. C. W. Schmidt and M. Popovic, "Duoplasmatron Source Modifications for 3He+ Operation".  1997 International Conference on Ion Sources, Taormina, Italy.  To be published in Rev. Sci. Instrum. (1998).

3. W.D. Cornelius and P.E.Young, Design of a 1 MeV 3He+ RFQ for the SAIC PET accelerator facility, Nuclear Instrument and Methods in Physics Research B79(1993) p.933

4. D. Sun, Report on End to End Simulation of RFQ A, B and C, Internal Report, (08/1996)

5. D. Sun, Report on End to End Simulation of PET RFQs Using PARMTEQ with Ò8-term PotentialsÓ, Internal Report, (12/1996)

3. RFQ Tuning and Resonance Control System

Introduction

This chapter describes the history, recent design, operational performance, and present state of the PET Radio Frequency Quadrupole cavity resonance control system.  Prior to the beginning of the PET project at Fermilab in 1995, three of the PET RFQs had been operated in tandem to accelerate 3He++ to 8 MeV by the SAIC/UW collaboration. RFQ cavity resonance control had been accomplished by a combination of mechanical tuning paddles and water flow control. During that time, paddle shaft failures due to RF heating were experienced. That problem was addressed and thought to be solved by the time the RFQs arrived at Fermilab, although operating time at high RF power and high pulse repetition rate had been quite limited. An SAIC report1 documents early measurements (1992) of the sensitivity of the 212 MHz RFQ resonant frequency to RF power and to water flow.

System Design at Fermilab

System Requirements

Requirements of the resonance control system for the four PET accelerator RFQs appeared straightforward:

The RFQs must be able to be powered up individually and independently from a standby state to nominal RF power levels at 360ÊHz without need for manual intervention.

The resonant frequency of each RFQ must be able to be independently controlled and maintained at its nominal frequency of 212.50 or 425.00 MHz.

The RFQs must reach nominal frequency within a small number of minutes after startup or major perturbation.

The RFQs must recover gracefully from perturbations, e.g. cavity sparks, without manual intervention.

Initial Operation

Operation of the 212 MHz RFQ began at Fermilab in late 1995. Initial operation was not to accelerate beam, but rather to test the Fermilab RF power amplifiers which were adapted to replace the failure prone amplifiers used previously at SAIC and characterize RFQ performance and x-ray production. The RFQ water flow valves and controller, paddle motor controller, and interface electronics previously used were neither readily available nor immediately compatible with the Fermilab machine control system hardware. RFQ operation at Fermilab began without the presence of anyone who had the experience of the previous operation.

For initial operation, the RFQ tuning paddles and water flow and temperature were fixed and a manually controlled RF frequency input to the amplifier was used to drive the RFQ on resonance; the drive frequency, not the cavity resonant frequency, was controlled. RFQ cavity cooling was provided by a NESLAB recirculating chiller unit2 which supplied constant temperature water to the RFQ. This mode of operation proved only marginally satisfactory even for low RF power, low pulse rate operation. At higher average RF power levels it was apparent that manual frequency control was inadequate to cope with the sensitivity and dynamics of the RFQ detuning due to RF heating.

A control system for the PET machine had already been chosen. It was based on the system used in the Fermilab Linac and selected because of its ready availability and proven performance. The control system had a history of supporting software feedback loops to control various parameters in the Linac amplifier and cavity systems. This existing feature provided the most direct and expedient solution to the initial resonance tracking problem.

Phase comparison of a RFQ field probe signal and an amplifier output forward power directional coupler signal provided a measure of the difference between the RF drive frequency and the RFQ resonant frequency. The phase detector output, applied to a standard control system sample/hold and digitizer channel, served as the input to a software feedback algorithm. Running at a 10 Hz rate, this algorithm (called the VCO, voltage controlled oscillator) controlled a DAC (digital to analog converter) to adjust the RF drive frequency to quickly and accurately track the RFQ resonance variations. This immediately resulted in a stable operating mode suitable for amplifier testing. It provided the additional benefit that the standard control system now contained the information necessary for systematic measurements of the resonance control problem.

Measurements

Operating in this mode, the dynamics of the 212 MHz RFQ detuning as a function of RF power level and pulse repetition rate were measured. At very low average RF power levels, where RF heating was insignificant, this method also provided a means to study the sensitivity of resonant frequency to other variables such as RFQ cooling water temperature.

Results similar to those reported by SAIC were found. When RF power is applied to the RFQ, the initial detuning rate is minus 10 KHz per second per kilowatt. At the nominal operating power of about two kilowatts, this detuning can exceed the cavity bandwidth in less than three seconds if not controlled. When RF power is applied, a double time constant characteristic is observed with the resonant frequency initially moving lower with a time constant of about 20 seconds, then returning partially back with a time constant of nearly four minutes. These characteristics are shown in FigureÊ3.1. The sensitivity to uniform temperature change of the whole RFQ structure was measured to be 6ÊKHz per degree Centigrade.

The large and rapid detuning of the RFQ upon application of RF power was believed to be due to differential heating between the vanes and the housing of the structure. This theory was supported by the double time constant behavior; the vanes and housing had different heat dissipation, different cooling, and different thermal masses. The smaller heat capacity of the vanes indicated that the vane temperature was the fast component.

Separate cooling water paths for the vanes and the housing provided a means to control and quantize this effect. A commercial cartridge electric heating element was introduced into the vane water inlet path and a 208 volt AC controller was fabricated to power the heater up to 4500 watts. The controller3 consists of a solid state relay operated by a pulse width modulator running with a 0.5 second period (short compared to RFQ thermal time constants) and provides for linear power and therefore linear water temperature rise control. Thermocouples were used to monitor the vane inlet, housing inlet, and combined return water temperatures. The NESLAB delivered a constant temperature water flow of 3 to 4 gallons per minute which was typically split two parts to one between the vanes and housing respectively.

Figure 3.1  212 MHz RFQ Resonant Frequency Response to Change in RF Power

Measurements of the 212 MHz RFQ resonant frequency as a function of the differential vane to housing temperature using the heater showed a sensitivity of 70 KHz/Cû with a time constant of about 40 seconds. The measurements demonstrated that the differential vane to housing temperature is indeed the important variable. They also showed that the vane inlet water temperature provides an effective handle to control the resonant frequency. Utilization of the heater to control the resonant frequency appeared to be an attractive alternative to the active mechanical tuning previously used. Elimination of moving parts would presumably result in a more reliable system and questions as to whether the tuning paddle problems had been adequately solved would be mute.

At this time a second software feedback algorithm, the resonance control loop, was installed to control resonant frequency by adjusting the water heater power. While the VCO loop forced the amplifier drive frequency to track the varying RFQ resonance, the resonance loop on a slower time scale compared that drive frequency to the desired frequency and drove the difference to zero. Tests showed that this combination of loops permitted automatic turn-on at full RF power and attainment of the desired operating frequency within a small number of minutes of turn-on. Once up to power and Òon frequencyÓ, RFQ operation was very stable and the resonance control system needed to make only small slow corrections.

This test system formed the basis on which the resonance control system for the four RFQs in the PET accelerator would be designed and implemented. When the 425 MHz amplifiers and RFQs became available for measurement they were found to exhibit detuning sensitivities several times smaller than the 212 MHz structure; presumably because the 425 MHz vanes lacked the large cut-out of the 212 MHz vanes and they had different cooling water channel placement. As a result of these measurements and the operational successes, the mechanical tuning paddles would be eliminated from all the structures in favor of the water temperature tuning mechanism.

The benign view of steady state operation experienced at this point of the project would turn out to be optimistic once beam acceleration with multiple RFQs was attempted, RFQ voltages were pushed to the limit, and beam induced sparking became common. Had these operational problems been foreseen at the inception, some form of mechanical tuning to improve response time may have been warranted.

Simulations

The initial operations and measurements described were performed running only one RFQ at a time. In this mode, the precise RFQ resonant frequency was not an issue so long as the drive frequency tracked. Beam acceleration through multiple RFQs however requires phase coherence of the accelerating fields from one RFQ to the next. This is achieved by driving all the RFQs from a single fixed frequency reference source; 425 MHz is derived from 212.5 by a frequency doubler circuit. A simulation of the complete RFQ cavity, amplifier, heater, and water system was undertaken to understand the non-trivial issues of switching under power from a variable frequency RF source (required for startup) to a fixed frequency RF source (required for beam acceleration) and maintaining resonance control in the process. The simulations were done using the EXTEND4 software package.

The measured sensitivities and time constants formed the basis for the simulation. Significant effects like water flow time delays, RFQ cavity bandwidth, and the fact that error signals can vanish if the RFQ is driven too far off resonance were included. The VCO and resonance control software feedback loops of the operating system were included and complemented in the simulation by additional loops. The added loops serve to establish a stable Òstand-byÓ mode for RF turn-on and to provide resonance control in the fixed frequency drive mode. A logic block orchestrated switching the various loops on and off between stand-by operation, variable frequency (VCO) operation, and fixed frequency (MASTER) operation.

The simulation results closely matched performance which had been measured to date. This gave confidence that the simulation could be relied upon for the overall system design. The simulation indicated that a satisfactory and stable system could be designed using the vane water heater to control the RFQ resonant frequency. The simulation proved to be a useful, powerful and effective tool. It led the way to the final system design which ultimately resembled the simulation very closely in both implementation and performance.

Design Decisions

Following the initial operation, measurements, and simulations, the overall multi-RFQ resonance control system design proceeded based on the following decisions.

Each RFQ would have its own closed loop cavity cooling water system with a NESLAB chiller providing temperature control and circulating water. Each NESLAB would be operated and utilized as a source of constant temperature water.

Tuning control for each RFQ would be achieved by heating the NESLAB water at the vane inlets. The housing would receive the NESLAB water directly.

The mechanical tuning paddles were considered unnecessary and would be eliminated.

Software feedback loops would provide the required active control functions.

The RFQs would be operated with variable frequency drive at turn-on and during major perturbations in order to track fast and large resonance variations.

Once up and in a stable operating state near the nominal resonant frequency, the RF drive frequency would be switched to the fixed reference at exactly 212.50 or 425.00 MHz frequency.

System Description

Tuning and Resonance Control System Hardware

The hardware of the resonance control system is quite simple. Each RFQ cavity is on its own separate closed loop water system with NESLAB chiller, heater and heater power supply, and three thermocouples as described in the Measurements section above. The NESLAB provides constant temperature water. The heater modulates the temperature of the water seen by the RFQ vanes. The thermocouple measuring the combined vane and housing return water temperature is used for active feedback in the system standby mode; the other two are used for passive monitoring only. An over temperature switch on the heater housing and a water flow interlock protect the heater from burnout due to insufficient water flow. The same two mechanisms protect the RFQ from damage due to overheating caused by lack of water flow or failure of the NESLAB cooling system.

Four major software components are important to the tuning and resonance control system. Multiple instances of a code module which performs generic proportional, integral, and differential feedback operations (PID loop) are at the heart of the real-time system. Five PID loops are used for each RFQ: the Return Water Temperature Control PID, the RF Frequency Control PID, the VCO Resonance Control PID, the Master Resonance Control PID, and the Average Power Feed Forward PID. A real-time logic module (Switch Logic) controls the state of the PID loops for each RFQ system. LabView applications provide graphical interfaces for monitoring and manual control of the various parts of the tuning systems. LabView code also controls sequenced RF turn-on and turn-off procedures. The standard Linac control system parameter page provides access to all tuning system parameters and controls.

The PID processes run in control system Internet Rack Monitor nodes. At a 10 Hz rate this code compares the value of an input variable to its desired value and generates proportional, time integral, and time differential error signals. These three components with individually programmable gains are summed with each other and with an optional direct input to produce the moduleÕs output. This output is then available for application to a control point to form a closed loop feedback circuit. The PID includes logic inputs to disable operation which permits Òwire or-ingÓ multiple PID instances to the same control point.

The Switch Logic module is application specific code which orchestrates the operation of five PIDs for the resonance control task. There are three possible states of operation of the tuning and resonance control system. The states are named Standby, VCO, and MASTER. The Switch Logic module controls transitions among the states and its function is best understood in the context of the system operation described below.

Figure 3.2 shows the LabView interface to the tuning and resonance control system for one RFQ. It depicts the system hardware on the right side and the software processes on the left. Several switches and setting controls are available in this interface. A different LabView interface provides sequenced RF on and RF off switches. These sequences initialize the startup RF drive frequency and send the proper signals to the low level RF system and the Switch Logic module for startup from standby.

Figure 3.2  LabView RFQ Tuning and Resonance Control Interface for 212 MHz RFQ

Standby State

In the standby state, direct water temperature regulation maintains the RFQ resonant frequency at a known stable value. The Return Water Temperature PID adjusts the water heater to control the temperature of the combined vane and housing return water to a programmable value. This temperature alone does not uniquely determine the RFQ resonant frequency; but given a constant supply water temperature from the NESLAB, known flow rates to the vane and housing, and the absence of RF heating, the return water temperature does translate to a predictable frequency. The VCO and Master Resonance Control PIDs are disabled in this state.

Variable Drive Frequency VCO State

The variable RF drive frequency or VCO state is the active state during RF startup and during recovery from tuning perturbations outside the range of the MASTER state. In this state the RF Frequency Control PID adjusts the low level RF system drive frequency (transparently through the Switch Logic module) to track the RFQ resonance in response to the cavity tuning error signal. This error signal is provided by the phase detector comparing amplifier forward power to RFQ cavity RF. Simultaneously, the Frequency Control PID output serves as the input to the VCO Resonance Control PID. This loop controls the water heater to force the RFQ resonant frequency and therefore the drive frequency to the nominal value. Loop gains are adjusted so that the VCO Resonance loop slowly nudges the resonant frequency to where it belongs while the Frequency Control loop deals with fast tuning changes. The Return Water Temperature and Master Resonance Control PIDs are disabled in the VCO state.

The Average Power Feed Forward PID was included to provide a fast input to the tuning system in response to possible sudden changes in RF power. In fact, this feature proved to be of little value due to the fact that a fixed gradient is required to accelerate beam in the RFQs, hence this PID is generally not used and left switched off and/or set to zero gain.

Fixed Frequency Drive MASTER State

In the MASTER state, the Switch Logic maintains the low level RF system frequency at a constant and precise 212.50 or 425.00 MHz. This results in RF drive to each of the RFQs at a fixed phase relative to the common reference frequency source. The Master Resonance PID controls the water heater in response to the cavity tuning error signal from the phase detector. This feedback corrects any resonant frequency variations within the bandwidth of the heater/RFQ system to maintain RFQ resonance at the nominal 212.50 or 425.00 MHz. All other PIDs are disabled or ignored.

State Control

The Switch Logic code for each RFQ supplies the RF drive frequency setting to the low level RF system and handles PID state control based on a combination of manual switches and active run-time inputs.

The STANDBY state is entered either by actions of the LabView RF shutdown sequence or by manual selection of the Temperature position of the Resonance/Temperature switch shown on Figure 3.2. The Switch Logic enables the Return Water Temperature PID and disables all other PIDs upon entrance to this state.

The LabView RF startup sequence selects the Resonance position of the Resonance/Temperature switch and the Switch Logic defaults the system into the VCO state where it can track large resonance variations resulting from RF turn-on. The Auto/VCO switch determines whether the system is forced to remain in the VCO state or is permitted to automatically transition to the MASTER state. The Auto/VCO switch must be manually selected by the operator.

In the Auto mode, transitions between VCO and MASTER states are controlled by the Switch Logic based on the cavity tuning error signal and the RF Frequency Control PID output. A switch from VCO to MASTER will occur if both the tuning error signal and the frequency error are smaller than preset tolerances. This indicates that the RFQ is being driven on resonance and that the resonant frequency is close enough to the nominal 212.5 or 425 MHz to jump the drive frequency to exactly that value. The system then remains in the MASTER state so long as the cavity tuning error signal remains in tolerance. The tuning error going out of tolerance indicates a perturbation beyond the capacity of the MASTER state to handle and causes a transition back into the VCO state. This is necessary since the cavity tuning error signal is based on a measurement using a RFQ voltage signal which can vanish if the RFQ is driven at a frequency too far from its current resonant frequency. In the VCO state, the system can track any large resonant frequency variations and settle back into a stable condition until ready again for MASTER operation. The speed of resonant frequency tracking in the VCO state is limited by the 10 Hz update rate of the RF drive frequency setting, whereas the speed of resonant frequency control in the MASTER state is determined by the 40 second time constant of the RFQ response to vane water temperature changes.

Since each RFQ tuning system operates independently of the other three, it is only via the common reference frequency oscillator that the phase coherence required among the four RFQs to accelerate beam is achieved. This common reference condition exists only when all systems are operating in the MASTER mode.

Operational Performance and Present Status

Operationally the RFQ tuning and resonance control systems perform well within design specifications. Using the LabView controlled turn-on sequence any one or all four RFQs can be powered up from STANDBY with the click of a single switch. In less that five minutes from turn-on at full power, all systems achieve stable operation in the MASTER state. Rarely do the automatic RFQ tuning systems Òget lostÓ and require manual intervention, even under extreme operating conditions such as RF pulse repetition rate switches and periods of RFQ sparking.

Imperfections in the low level RF system which resulted in a coupling of RF amplitude to RF drive frequency caused some complications for the tuning systems in the early stages. Switching from the VCO to MASTER state would produce a step change in RF power delivered to the RFQ which would in turn cause a RFQ detuning step. This step could be so large as to be out of the range of the MASTER resonance control loop, so the system would quickly revert to the VCO. The instability was overcome by careful setup of the low level RF hardware to minimize the coupling, however it did point out the most serious shortcoming of the resonance control system design - limited response bandwidth in the MASTER state.

Though the tuning and resonance control systems perform as designed, the design has been less than optimum for the operational mode of the PET machine to date. Cavity sparking has been a persistent problem in typical daily operation. The sparking has two primary causes: 1) the RFQ operating voltage is normally pushed as high as possible to maximize beam transmission, and 2) the beam itself induces fits of sparking. The sparking and response of the RFQ spark protection system cause variations in the average RF power applied to and absorbed by the affected RFQ. These variations produce sufficiently large resonant frequency changes in a short enough period of time that the heater is not able to overcome them and the affected system must revert to the VCO state. Depending on the cessation of sparking, recovery to the MASTER state may take seconds to minutes. Since any one RFQ not in the MASTER state prevents stable beam acceleration and all four RFQs are operated with a high likelihood of sparking, significant beam downtime is suffered.

The tuning and resonance control system of course is not able to affect the frequency of occurrence of cavity sparks, but lost beam time might be reduced if the tuning system included a mechanism to facilitate faster response to the effects of that sparking. This is where the mechanical tuning paddles may have proved beneficial had they been maintained in the system design. Their response time could have been seconds, compared to the tens of seconds achieved by water temperature modulation.

PostScript on Tuning Paddles

In March 1998, after the body of this section was written, interruptions of stable beam due to RFQ sparking and resultant cavity detuning continued to be unacceptable.  A decision was made to install one  tuning paddle (two tuning paddles were used in the original SAIC SDIO design) in each of the 425 MHz RFQÕs A and B.  The single paddle provided a ±25 KHz prompt tuning adjustment range.

Automatic control of the paddle was integrated into the existing system of software feedback loops.  In the VCO state, the paddle rests at the middle of its control range and operation is exactly as previously described.  In the MASTER state, a Paddle Control loop adjusts the paddle position in response to the cavity tuning error signal from the phase detector.  Within its range, this control maintains the resonant frequency at the desired nominal with a speed of response at least an order of magnitude faster than the water heater system alone.  The Master Resonance PID has been reconfigured to monitor the paddle position and control the water heater to maintain the average paddle near the center of its range.  This combination of paddle plus water heater results in a system with both large dynamic range and fast response.

The positive effects of the new arrangement were both immediate and dramatic.  The ability to respond quickly to changes in cavity tuning, whether due to beam loading, cavity sparking, or RF power variations, greatly reduced the likelihood that an RFQ system would switch off the MASTER state and significantly shortened the recovery time when it did.  This in turn broke the vicious cycle of coupled instabilities in which beam transients caused by sparking or tuning errors in one RFQ system induced similar problems in another RFQ.  Subsequently a tuning paddle was re-installed in the 212 MHz RFQ.  This further stabilized the whole machine making possible steady beam currents above 100 microamps for long periods.  Plans are presently underway to design a tuning paddle for the 425 MHz RFQ C.

References

1.  Wayne Cornelius and Steve Ringler, Pre-Stripper Water Flow Experiments, SAIC PET Note #62, 1992.

2.  Model HX-150, NESLAB Instruments, Newington, New Hampshire.

3.  Fermilab drawing #9700-EB-348007.

4.  EXTEND modeling code by Imagine That, Inc., San Jose, CA.

4.  Low Level RF (LLRF)

Introduction

The PET Low Level RF (LLRF) System regulates the accelerating voltage  in the four RFQ cavities  by controlling the  frequency, phase and amplitude  of the RF signal driving the High Level RF system.  The central LLRF hardware for all four cavities  resides in one VXI crate.  This crate supports a CPU card, a clock decoder card and two Baseband Processor modules.  Each Baseband Processor (BBP) module supports two RFQ RF systems.  Each BBP contains one embedded SHARC DSP1 (Digital Signal Processor) that controls all board functions.  All system and subsystem functionality may be broken down into the following groups; control system interface, timing interface, RF waveform generation, frequency control, feedback regulation, and cavity spark protection.  These functions and the system specifications are derived from the following system requirements.

One 212.5 MHz and three 425 MHz  LLRF.  All systems have a common frequency reference source based on a 212.5 MHz crystal  oscillator.

RF repetition rate of 360 Hz and control system rate of 10 Hz.

Separate amplitude and phase control for each station with regulation of transient beam loading.

Full control of RF waveform for each station.

Detection of cavity sparks with fast RF kill, slow cavity protection and  recovery.

Cavity resonance detection and frequency  modulation of RF pulse.

Full access  to all important  system waveforms through the control system at a 10 Hz rate

Control System Interface

The PET control system is based around the Internet Rack Monitor (IRM).  For the LLRF system, an  IRMÕs CPU card and timing card are installed directly into the LLRF VXI crate.  Standard IRM processes run in this CPU as well as several LLRF specific applications.  These include downloading DSP code to the BBP modules, parameter settings and readings, waveform acquisitions  from the DSP, cavity spark recovery  process, and error handling.  This interface is described in detail in chapters 14 and 15.  The CPU provides data to console  programs and data loggers, as well as other IRMs requiring  data for local process control.  This interface  has adapted well to changes  in the DSP code for the  BBP modules.

Timing

The timing card provides triggers to the CPU and BBP modules  based upon an event plus delay.  The LLRF system responds to the 10 Hz control system trigger and the RF start trigger.  The 10 Hz trigger  synchronizes  the CPU and the BBPs  with the rest of the control system.  The start LLRF waveform trigger may be aligned at  the optimal relationship with the high level RF.  This trigger starts the Direct Access Memory (DMA) and spark detection routines  running.

Baseband Processor

The Baseband Processor (BBP) module is the central component of the LLRF system.  This module can be thought of as a two channel vector signal modulator  and a two channel vector signal analyzer with the processing done by a SHARC DSP.  Each BBP regulates two cavity RF systems.  A block diagram of the module is shown in figure 4.1.  Four AD9026 12 bit 26 MHz ADCs and four AD9713B 12 bit high speed DACs are connected directly to the 48 bit data bus of the SHARC.

Figure 4.1  Baseband Processor

The accelerator  operates with a nominal repetition rate of 360 Hz and a maximum RF pulse width of 80 micro-seconds.  When the SHARC receives a start trigger from the timing card it starts a DMA process that will play out and acquire RF waveforms.  Two of the 10 DMA channels in the SHARC IO processor have hardware DMA request and grant  lines.  By configuring the DMA controller, the IOP (Input Output Processor) will play and acquire waveforms without external  hardware or memory.  The IOP is configured to play and acquire at one half the DSP clock rate.  The high speed, high spectral purity digitizers are combined with signal analysis software in the DSP to provide the building blocks for a vector signal analyzer.  The combination of the DACs and DSP software is the basis for a vector signal modulator.

The analog IO from the ADCs and DACs is connected to two general purpose daughter cards.  PET daughter cards perform RF IQ modulation and demodulation.  Two models have been built to support 425 MHz and 212.5 MHz RF  These cards frequency translate baseband vector signals up to and down from the local oscillator frequency.  With IQ modulation, the DSP has complete control and feedback regulation of RF amplitude, frequency, and phase.

RF Waveform Generation

At the 360 Hz rate, two 1024 word waveforms are played to the RF modulators.    At the 10 Hz rate of the control system, a trigger from the timing card starts the waveform  processing.  This processing is done by the SHARC  DSP by routines written in ÒCÓ.  The program waveform array is built from the parameters of pulse length, rise time, amplitude, RF frequency and phase.  With feedback off, the program waveform array is written to memory to be played out by the DMA controller.  With feedback on, the complex arrays are processed as shown in the feedback diagram, figure 4.2.  The processing includes vector array multiplication, addition, filtering, and limiting.  Group delays in the RF system are taken out by adjusting array indexes  The complex time domain signal is transformed by FFT to measure the resonant frequency for input to the cavity tuning control loop.  Ten 256 sample waveforms per system are returned by the control system for 10 Hz display update.  This processing is done for each LLRF subsystem and completes  in about 50 ms.

Figure 4.2  PET Feedback

Early tests of the feedback system went well.  Before a RFQ was available for testing, the LLRF was run closed loop with the HLRF (High Level RF) driving a dummy load.  Closed loop performance was as predicted by the simulations done with ÒExtendÓ, a commercial time domain  software simulation program.  Next the HLRF was connected to the cavity.  At this point closing the feedback loops was hampered by several nonlinearities.   The worst being a spurious oscillation in the PA (Power Amplifier).  This oscillation  would grow during the 80 micro-second pulse to about 20% of the nominal drive level.  The root cause of the oscillation is traced to the interaction of the RFQ and the output cavity filters in the PA.  Outside its 30 KHz bandwidth, the RFQ reflects  all energy back to the PA.  With this reactive  load the PA output cavity  provides little filtering  for the tube.  The network based on the tube, output tank, drive line length, and the RFQ is marginally stable at many frequencies.  One way to deal with this would be to add circulators in the drive line.  Circulators for a 212 MHz system are too large and too costly for this project.  Instead the system was made stable by careful mistuning of the output stage of the PA.  While this made operation possible, it limits the peak output power and dynamic range of the HLRF. The 212 MHz HLRF also was found to be very nonlinear .  No output was measured until the low level drive was about 40% of nominal.  All stages of the station operate in class C mode so they all are inherently nonlinear.  The largest nonlinear stage turned out to be the solid state amplifier.  By increasing the drive level and padding the output of the amp, nonlinearity was minimized.   Cavity gradient regulation is shown in figure 4.3 and fast IQ loop response is shown in figure 4.4.

Figure 4.3 Cavity Gradient Regulation for 100 seconds. Plotted relative volts vs. time.

Figure 4.4 Cavity Amplitude, Phase, I and Q Error Signals. Plotted volts vs. sequence time during pulse.

Spark detection

The original spark detection  circuit works by monitoring the reflected power signal from the cavity drive.  The output of a diode detector  is compared to a reference voltage.  The output of the comparitor is Òor-edÓ with the comparitor of the other RF system in the module.  This generated an interrupt to the DSP that killed the RF to both systems.  This coupling between pairs of RFQs caused stability problems at high repetition rates combined with high spark rates.  This problem is fixed by a redesign of the RF daughter card that adds an RF switch to the output of each IQ modulator.  The logic for controlling the switch is in hardware while spark counting and inhibit for high spark counts is still done in software.  One other problem found with the spark detection is false detection of sparks with high reflected power from an off resonant cavity.  A false spark causes the RF to be shut off for a short time which allows the cavity to go further off resonance, cascading the problem.  The solution is the placement of a high pass network on the output of the diode detector.  This allows high sensitivity of the fast rise time spark waveforms while providing attenuation of the slow waveform from the off resonance condition.  The DSP will shut off the RF and start a spark recovery process when the number of sparks occurring in a 100 ms period exceeds a set value.

Other Changes

The PA has a high phase dependence on many factors such as screen voltage, average power, and power line voltage.  Large changes in loop phase are difficult for IQ regulation to handle.  A Slow phase loop was added that regulates a phase offset term.  This regulation insures that modulation and demodulation vectors are always in proper alignment.  During conditioning of the cavities the spark rate is so high that the feedback learning may become unstable.  A slow feedback loop was added to regulate the RF amplitude set point based on the cavity gradient signal.  This loop has good regulation of the average cavity pulse and will work with the fast feedback loop turned off.

Future Options

At this point in the project, the biggest area that the LLRF might improve the acceleratorÕs over all performance is spark recovery.  One improvement would be real time loops that would better handle gain changes in the HLRF during heavy sparking.  This could be done with a redesign of the RF daughter cards.  The other possibility is to improve the regulation of cavity resonance by providing fast control of the RF power dissipation in the RFQs.  This power would be controlled by pulse width modulating the RF waveform.  This may reduce the time required to return the RFQ to its nominal frequency after heavy sparking.

Reference

1.   ADSP-2106x SHARC UserÕs Manual, First Edition, © 1995 Analog Devices Inc.

5.  High Level RF (HLRF)

Introduction

The requirements for High Level RF (HLRF) are shown in Figure 5.1. The Full Duty Factor of 2.5% for the project is found from  a 70 µs Òflat topÓ time with a repetition rate of 360 Hz.  The right-hand column of Figure 5.1 gives actual measured data for each of the stations into a 50 ½ Dummy Load.  The other goal of the HLRF was to establish reliability for each of the Power Amplifier Stations.  This reliability issue would not only be required in each of the different Power Stages within each station but also in the internal system components of each station.  Finally, recommended future upgrades will be listed.

| Power Amplifier | Frequency | Total Power Required | Power Observed into Dummy Load |
| --- | --- | --- | --- |
| Station |
| at Full Duty Factor | at Full Duty Factor |
| PA 212 | 212.5 MHz | 120 - 143 kW | 170 kW |
| PA 425 A | 425 MHz | 136 - 156 kW | 200 kW |
| PA 425 B | 425 MHz | 120 - 140 kW | 200 kW |
| PA 425 C | 425 MHz | 105 - 125 kW | 200 kW |

Figure 5.1: HLRF Design Parameters and Actual Measured Performance.

General High Level Performance Issues

In order to achieve the power goals each station would require a solid-state stage, a Burle 7651 Power Tube stage, and a final Burle 4616 Power Tube stage.  A block diagram of these stages is shown in Fermilab Drawing # 9700-ED-348023.  The stations were created from four Fermi National Accelerator Laboratory 200 MHz Power Amplifier  that were surplussed after a 1993 upgrade to the LINAC accelerator.  All of the stations required an upgrade of internal system components for reliability and remote control.

Figure 5.2: 425 MHz Solid-State Amplifier.

The input from the Low Level RF is a nominal 10 dBm (decibel referenced to one milliWatt, 0 dBm = 1 mW) for each of the stations.  The Solid-State stage has a capability of up to 400 W.  In PA212 this is done with two amplifiers, a Mini-Circuits ZHL-5W-1 and a Microwave Power Devices PCA 201/1973A.  The Mini-Circuits amplifier was required because of the gain capabilities of the Microwave Power Devices amplifier.  Each of the 425 MHz stations use a single Microwave Power Devices PCA 425-82/10075A Solid-State amplifier as shown in Figure 5.2.  Four Solid-State 425 MHz amplifiers were purchased from the Los Alamos SDI surplus equipment.

Solid-State Problems Encountered and Reliability

The reliability of the Solid-State Drivers has been very good.  There has been only one instance of failure since receiving the Microwave Power Devices PCA 425-82/10075A from Los Alamos.  This occurred on July 30, 1996 and was repaired.  The repair entailed the replacement of a LS logic chip on the pulse input of the amplifier.

Figure 5.3: 425 MHz Burle 7651 Power Tube Amplifier.

The second stage is a Power Amplifier using a Burle 7651 Power Tube.  This stage is capable of producing up to 4 kW of power.  The change from 200 MHz to 212.5 MHz in this stage of PA212 required nothing more than adjusting the finger stock short on the output section of the 7651 stage.  To modify the 200 MHz Power Amplifier to 425 MHz for the other three stations required some hardware modifications.  The paper ÒModification of the LINAC 7651 driver to operate at 425 MHzÓ contains details.1

7651 Stage Problems Encountered and Reliability

One Burle 7651 tube has been replaced (It failed due to extensive operational hours in the LINAC).  A problem with the -14 VDC Kepco supply to the 7651 Bias Modulator caused sagging during its 70 µs Òflat topÓ time at 360 Hz.  This was discovered in late May of 1997.  The solution was to improve power supply regulation by the addition of a 200 ½, 14 W resistor across the -14 VDC Kepco supply so that it would draw and regulate current in its proper quadrant.

A second problem encountered in changing from the LINACÕs Duty Factor of 0.68 % to the PET Duty Factor was found in the middle of August 1997.  A 100 ½, 2 W resistor in the 7651 Bias Modulator was being overheated over an extended period of time by the longer duty factor for PET.  After the circuit was analyzed, the proper higher wattage resistor was installed.

Figure 5.4:  212.5 MHz Burle 4616 Power Tube Amplifier.

The third stage of the power amplifier uses a Burle 4616 Power Tube.  This stage is capable of producing at full duty cycle up to 170 kW @ 212 MHz and 200 kW @ 425 MHz.  For PA 212 (Figure 5.4) the only modifications from the LINAC station to PET station were to move the finger stock shorts on the input and output section and adjust the input and output coupling to 50 ohms.  For the 425 MHz stations three Burle 4616 power amplifiers cavities were purchased from Los Alamos SDI Surplus Equipment.  The three LINAC surplus stations were then modified to accept these new amplifiers.

4616 Stage Problems Encountered and Reliability

On May 24, 1996 it was discovered when commissioning the second 425 MHz  4616 Power Amplifier that the RF output would dip during the 70  µs pulse.  Upon further investigation it was discovered that the finger stock short on the output section of the amplifier was too small in diameter and did not deflect the finger stock correctly. Thorough measurements showed a need for a new output short.  This power amplifier now resides in PA425A and has worked flawlessly.  This problem was not seen on any of the other 425 MHz Power Amplifiers.

In the spring of 1997 it was discovered that the line voltage in Lab G would sag when the Tevatron in Fixed Target mode would ramp.  This would cause the DC anode voltage of all the 4616 amplifiers to dip from 18 kV by as much as 10 %.  This problem did go away when the Tevatron was turned off for the Main Injector upgrade in September 1997, and should not present a future problem for the project.

In late March of 1997 a 25 µF, 20 kV 4616 anode capacitor in PA425A failed.  It was replaced with a spare from the LINAC and the voltage across the capacitor was dropped from 20 kV to 18 KV by moving the tap points on the Anode Supply transformer.  The changing of tap points to 18 KV was also done on the other three Anode Supplies.  This problem has not been seen again.

In the middle of June 1997 we lost a 4616 Power FET Screen Supply in both PA425B and PA425C.  The cause of failure was from exceeding the average power rating of resistor R7A and R7B in Fermilab Drawing # 0230.00-EC-60663.  Upon further investigation it was found that a SCR was missing on the 4616 Screen Modulator Regulator card in both stations.  This would allow the screen supply to stay on for longer than 70 µs and change the average power across the resistors.  This SCR was checked in the remaining two stations.   All four 4616 Power FET Screen Supplies also received a Dale 25 ½, 25 W wire wound resistor to replace R7A and R7B and the supplies controller card had a potentiometer turned to reduce the maximum ÒONÓ time to 110 µs.

In the middle of July 1997 two Burle 4616 Power Tubes failed.  One in PA425C with a grid short and the other in PA425A with a screen short. These tubes were sent back to Burle for failure examination and repair.  The report from Burle is that failure was caused by the use of Hasteloy B2 material in manufacturing the filament-cathode assembly.  This failure mechanism has been noticed in tubes returned by other facilities after a nominal 3000 hours of operation.  New 4616 tubes are now manufactured with an improved version of the Hasteloy material and occurrences of grid shorts have not been reported.

In late August 1997, the bias supply for the screen voltage for the 4616 Power Tube was increased to improve screen voltage regulation in all four stations.  A noticeable improvement in RF power regulation resulted from this modification.

Station Improvements

The original 200 MHz LINAC stations needed to have their control systems updated to allow for more monitoring capabilities and the ability to send status bits to the Internet Rack Monitor (IRM) installed in each of the stations.  Some of the new  capabilities are to monitor RFQ water flow, RFQ vacuum, and cooling water conductivity.  In using this new control system an operator is able to quickly interpret the current status of the station either from the front control panel or remotely by computer.

Another function of the IRM is to read back via analog channels the power levels of each of the different stages in a station.  The last important function of the IRM is to provide programmable timing signals to a station.

The cooling water system for the 4616 Power Tube required a new manifold.  This upgrade allowed for the installation of three water flow meters and the ability to easily remove the 4616 Stage from the station for shipment to Shreveport.

The final improvement was the addition of remote control of the 4616 screen voltage.  Remote adjustment is useful when trying to turn on a station that has repeated anode current overloads or when a new 4616 Power Tube is sparking internally during conditioning.

Recommended Upgrades

In the course of running the accelerator it was discovered that increasing the pulse period to 80 µs of Òflat topÓ time, beam current could be increased.  This change in duty factor caused the 4616 DC Anode Supplies to drop from 18 KV to between 17 and 16 KV depending on the station.  Thus, the maximum power out of each of the stations was decreased.  It was then proposed to raise the anode voltage to 19.5 KV using a variable transformer (Variac) inserted into the 480V - 3 phase primary on one of the Anode Supplies. The test showed an increase of 13.5% in output power with the anode voltage at 19.5 KV.  A recommended Anode Supply upgrade is to replace the existing 20 KV 25 uF cap with a 25 KV unit ($2000 per station),  to replace the transformer and install a new one with higher ratings ($3000 per station),  and to install a new SCR primary controller ($1500 per station).  The reason for the SCR controller is to aid in system turn-on without Anode Supply current overload.

Figure 5.5: 4616 18 KV DC Anode Supplies.

References

1.  PET Web page, http://www-linac.fnal.gov/pet

6.   Charge Doubler

Introduction

The charge doubler converts 3He+ to 3He++ by means of a pulsed gas-jet stripper.  Stripping fractions are typically in the range of 70-80%.  Fractions up to 83% have been observed under certain conditions.  Since the beam-particle charge is doubled, the electrical output current is larger than the input current.

A summary description of the charge stripper was presented at the 1997 Particle Accelerator Conference1, which is also posted on the PET web page.  This document provides a more thorough description of the device, and contains additional information concerning design approach, problems encountered, and operating modes.

A stripper design based on a pulsed gas jet appears to be preferable to alternative approaches, all of which suffer from serious difficulties. (a) Development of a plasma-based stripper (He++ ion source) was deemed too technically challenging given the scope of this project; (b) a solid foil is not expected to survive under the beam intensities in use; (c) a static-fill cell suffers from spill over of gas to adjacent regions of the accelerator and beam heating of the gas; and (d) by utilizing a pulsed gas jet synchronized with the beam it is possible to significantly reduce the gas load on the vacuum pumps, and the pressure rise in adjacent regions of the accelerator.

Because of charge-exchange processes , a non-plasma-based charge stripper requires operation at an energy in the range of 1-MeV or higher for good stripping efficiency.2 The charge stripping process is a competition between the desirable ionization process He+ -> He++ and the undesirable charge-exchange processes He++ -> He+ and He+ -> He0.  For efficient stripping the He+ beam ions must attain sufficient energy to significantly exceed the electron velocity corresponding to the binding energy of the He+ ion, which is relatively large, 54.4 eV 3.  At 1 MeV, the beam ion velocity is the same as the velocity of a 180-eV electron.  Although some cross-section information does exist for stripping helium beams on carbon foils, ionization cross sections for 3He are in most cases not well known, but can generally be expected to favor heavy molecules, such as N2, CO2, Ar, etc., over light molecules such as He and H2.  The required gas line density for stripping is approximately 3-6 x 1016 molecules/cm2.

A differentially-pumped static gas cell was utilized in the original SAIC project, after initial attempts to operate using a piezoelectric pulsed gas valve.  One problem with a static fill is that pressures in adjacent regions of the accelerator are high enough, for example, to short out the electric fields in a conventional buncher.  This concern lead to the development of the novel MEBT design utilized in this project.  Another problem is that the stripper gas is heated by the He+ ions passing through the gas.4  An early estimate of this effect is posted on the PET web page (ÒThermodynamics of gas stripper cellÓ).  In particular, the beam heating of the background gas can be expected to cause a localized density reduction in the gas, which then leads directly to a reduction in stripping efficiency.  In fact, attempts to operate the stripper cell as a static gas fill observed erratic stripping rates, as well as difficulty in obtaining high stripping efficiencies .  Pressures in the RFQ and downstream of the stripper were high.  In a gas-jet target, the refresh rate of the gas is high enough that the gas is relatively unaffected by the beam.

Injector and nozzle

Because of difficulties with a piezoelectric pulsed gas valve, we investigated mechanical fuel injectors5.  Automotive-type fuel injectors are rugged and fast mechanical valves.  We chose for operation in the stripper the valve with the fastest response among several valves tested, a Nissan fuel injector, Part No 16600-40F01.  A MOSFET-based pulser provides 75-V, 200-300 µs pulses to the injector.  The electrical response of the injector is predominantly inductive, with current rising linearly during the electrical pulse until the injector opens at about 1 A.  The pulser rapidly shuts off the current at the end of the pulse, which closes the valve to minimize on-time of the injector and to prepare for the next pulse.  The voltage level of the pulse is sufficient to allow rapid operation of the injector, while remaining well below the breakdown strength of the insulation.  Injectors have been shown to operate reliably at 360 Hz for 109 pulses.  The throughput of the pulser is approximately 150 Torr-liters/sec of gas in a 300-µs pulse.  Pumping capacity of 3000 liter/sec is required to remove this amount of gas at a pressure of 5 mTorr and repetition rate of 360 Hz.

The injector injects gas into a converging-diverging nozzle.6 The nozzle was designed to match the pressure of the injected gas in the converging section through a throat to a diverging section.  The nozzle converts the energy of thermal motion of the injected gas to directed motion in a gas jet.  If the nozzle is properly matched, the gas flow undergoes a theoretical transition between subsonic and supersonic flow at the throat.  The gas cools as it expands, and may reach very high directed velocities.  It is possible for the beam to condense into clusters containing large numbers of molecules.  All of these properties (e.g. super cold gas, cluster formation) tend to reduce the pressure of the gas jet.  We chose a .020Ó (0.51-mm) diameter throat, and a diverging section which opens to the full diameter of the beam tube, 15-mm.  Although sophisticated diagnostics were not available to probe in detail the properties of the gas jet,  measurements of relative pressures in the stripper cell and the adjacent regions (RFQ and MEBT) indicated that under the appropriate conditions, a reasonably well-directed gas jet was formed.

1-MeV Test

A 1-MeV beam test was made to investigate performance of the stripper cell.  A top view of the test chamber is shown in Figure 6.1.  Total pumping capacity in the test cell was 1000 liter/sec.  A spectrometer magnet bends the 1-MeV He+ and He++ beam ions.  The magnet is a small trim dipole magnet borrowed from the Antiproton Source.  The triangular-shaped drift chamber allows the 3 charge states He0, He+, and He++ to separate.  They are collected at 3 biased Faraday plate collectors at bend angles of 0o,11.5û and 23.6û .  In addition 2 wire profile monitors were installed between the collectors to measure the effect of the stripper gas on beam profiles.

The greatest stripping efficiency was obtained with argon gas, surpassing 80% in some cases, followed closely by nitrogen.  The stripping efficiency in He gas was less than 40%.  As noted elsewhere in this report, due to heating and slowing down of the turbopump vanes when using argon gas, we normally operate the stripper cell in nitrogen gas, despite the slight loss in stripping efficiency.  A plot of stripping efficiency as a function of time delay of the beam pulse with respect to the stripper pulse is shown in Figure 6.3.  Roughly 400 µs from the time of the beginning of the electrical pulse to the injector is required for the gas to appear at the interaction region.  The gas in injected for a period of roughly 400 µs, then it is pumped out until the next beam pulse.   Stripping measurements were made in a variety of gases including Ar, He, CO2, N2,  and Kr.  The results of some of the measurements of stripping efficiency are summarized in Figure 6.2.

Figure 6.1.  1-MeV beam test.

Figure 6.2.  Performance of gas-jet stripper on He+ beam in 1-MeV test.

Figure 6.3.  Yield of He+ (dashed) and He++ (solid) in the Faraday collectors as a function of stripper delay time in the 1-MeV beam test for argon gas at 60 Hz.

Emittance measurements of the 1-MeV beam are described on the PET web page.  Emittance growth of the beam due to scattering on the gas in the stripper cell was initially predicted to be a matter of concern.  However measurements showed no significant beam size increase due to gas in the stripper cell.  A calculation based on the work of Sigmund & Winterbon (SW)7, agrees with the measured lack of emittance growth due to scattering.

SW give for the scattering angle a

where Z1=2 (helium ion), Z2=7 (nitrogen atom), e is the electronic charge, e0 is the permitivity of free space, E=1 MeV is the beam energy, a = 1.4¥a0¥Z2-1/3 is the atomic radius from the Fermi-Thomas screened potential model, and a0 is the Bohr radius (0.53¥10-10 m).  The parameter as is a dimensionless parameter derived from Figure 6.3 of SW as a function of t = ¹¥a2¥nl, where nl= 6 x 1020 atoms/m2 is the atomic path length of the stripper gas .  The result of the calculation is that the expected scattering angle is about 0.9 mrad.  The RMS size of the curves above is about 4 A (He+), which corresponds to about 30 mrad for this geometry, assuming a point source.  The increase in beam size is thus predicted to be negligible, as observed in the experiment.  It should be noted that the beam profiles (Figure 6.4) are not purely Gaussian, but have somewhat broader tails than a Gaussian distribution.  The enhanced tail on the He++ profile at large magnet currents is due to the residual He+ beam ions remaining after stripping.

Figure 6.4.  Wire scans of beam profile for stripped and unstripped beams.  He+ is in the absence of gas in the stripper, He++ is in the presence of gas in the stripper.

Operational performance

Details of the stripper cell are described elsewhere in this report.  The injector and nozzle geometry remain as described above for the 1-MeV test.  Pumping capacity is 3000 l/s in the lower section (turbo) and 1000 l/s in the upper section (scavenge).  Gas is directed down into a stripper chamber for interaction with the beam, and into a chamber evacuated by two large turbo pumps.  Operational performance of the stripper cell is summarized in figures 6.5 and 6.6.  The pressure in the turbo section is a measure of the gas injected by the jet toward the turbo pumps.  The pressure in the scavenge section is a measure of the gas scattered back into the scavenge section.  Note that the pressure in the scavenge section  is much lower than the turbo pump pressure, indicating that well over 90% of the gas is injected into the turbo section  As a result the bulk of the gas flows are isolated from the other regions of the accelerator.  In particular the 212-MHz RFQ adjacent to the stripper cell operates at a pressure of less than 1 x 10-6 Torr.

For a given back pressure on the injector, the amount of gas injected increases rapidly up to a peak as measured by the pressures at the two pressure gauges in the stripper cell.  Above the peak, the amount of gas injected drops.  The position and amplitude of the peak is a function of the back pressure on the injector.  For injector pulse lengths below the peak, gas throughput decreases as back pressure increases.  Above the peak the reverse relationship holds true.  The stripping efficiency as measured by the amount of current detected at the end of the MEBT also peaks when the pressures peak.  In order  to prevent

(a)

(b)

Figure 6.5.  Performance of the stripper cell at 120 Hz as a function of injector pulse length for (a) 20 psig and (b) 30 psig nitrogen gas back pressure on the fuel injector and 13 mA He+ beam out of the 212-MHz RFQ.

overloading the pumps at the peaks of the curves, these plots were taken at 120 Hz.  Time was not available to do a more thorough investigation of this performance, or to relate it to theoretical parameters of the nozzle and injector.

The performance of the stripper as a function of time depends on the operating point chosen.  Figures  6.6a and 6.6b show stripper performance as a function of time.  Note that in contrast to the 60 Hz data shown above, there is a large floor in the stripping fraction before the injector is turned on.  This is due to the presence of gas in and near the stripper cell that has not been pumped out.  Figure 6.6a shows beam current out of the MEBT for a point below the peak.  The beam current slowly increases with time, indicating a slowly forming gas pulse, reaching a peak at about 1200 µs.  Figure 6.6b shows the same the beam current again, this time taken above the peak of Figure 5.  The stripping efficiency, hence the gas injection rate,  increases much more rapidly, reaching a peak at about 900 µs.  Since the time available to pump out the stripper cell between beam pulses is very short (2.78 ms), the above-peak operating point appears to be modestly more advantageous to operation because an additional 300 µs is available to pump out the cell after the injected gas pulse is over.  At least as important is the fact that the beam intensity is more stable from pulse to pulse.  This is the nominal operating point.

At 360 Hz there is a roughly 10% decrease in stripping efficiency from the efficiency obtained at the lower repetition rates.  This is at least partly due to the fact that it is necessary to operate at less than maximum throughput to prevent overloading the pumps.  Although direct measurements of the stripping efficiency are not possible, it is likely that the stripping efficiency drops from about 80% at 120 Hz to about 70% at 360 Hz.  The implied efficiency of transport of beam through the MEBT is about 70%, based on the overall measured efficiency on the stripper-MEBT combination of about 50%.

Effects on MEBT performance

Typical operating pressure in the MEBT is in the range of 10-5 Torr.  This is a sufficiently high pressure to generate charge-neutralizing background electrons due to ionization of the background gas.  On the other hand, charge exchange on background gas, if allowed to take place, could deplete the beam current by creating He+ beam ions, which would then be lost in the MEBT.  Expectations are that the gas density in the MEBT remains below the density required for significant amounts of charge exchange to take occur.  But the cross sections and detailed pressure distributions in the MEBT are not well known.  Future investigations are required to determine whether charge-exchange losses in the MEBT, or some other mechanism, contribute to the observed shortfall in stripping efficiency at 360 Hz.

These and other sources of electrons in the stripper ensure that there is a copious supply of electrons for charge neutralization in the MEBT.  As described in Reference 1 and elsewhere in this report, space-charge neutralization due to the presence of electrons is a problem for reliable operation of conventional bunchers, but is probably advantageous to operation of the MEBT.

(a)

(b)

Figure 6.6.  Beam current out of the MEBT as a function of stripper pulse delay at 360 Hz in nitrogen gas.  (a) 10 psig back pressure, 229 µs pulse length (below peak of figure 6.5), (b) 20 psig back pressure, 292 µs pulse length (above peak).

References

1.  F. M. Bieniosek, K. Anderson, R.J. Pasquinelli, M. Popovic, C.W. Schmidt, R. Webber, D.J. Larson, P. Young, Charge stripper and MEBT for the 3He RFQ accelerator, Proc. 1997 Particle Accelerator Conference.

2.  The 3He RFQ PET tracer production system, Preliminary Design Report, Nov. 26, 1990, Internal Project Report PET 2.

3.  M. Gryzinski, Classical theory of atomic collisions, Phys. Rev. 138, A336 (1964).

4.  J. Gorres, K.U. Kettner, H. Krawinkel, C. Rolfs, The influence of intense ion beams on gas jet targets, Nucl. Instrum. Meth. 177, 295 (1980).

5.  JL Dobson and BRF Kendall, Controllable leaks using electrically pulsed valves, J Vac Sci Technol. A 1990, p 2790

6.   B. Franzke, N. Angert, Ch. Schmelzer, Charge exchange of fast iodine ions in a dense jet of carbon dioxide, IEEE Trans. Nucl. Sci. 19, 266 (1972).

7.  P. Sigmund, K.B. Winterbon, Small-angle multiple scattering of ions in the screened coulomb region, Nucl. Instrum. Meth. 119, 541 (1974).

7.  Machine Operations and Performance

Introduction

After two years of  intense effort building the PET accelerator at Fermilab, it's worth pausing briefly to review how we got where we are, examine the accelerator's current performance, and assess our operational status. The following topics will be covered: operations history, accelerator performance, and targetry sessions.  We cover activities and performance results up through Mar. '98.

Operations History

The time line presented in Figure 7.1 is a synopsis of major milestones based on data retrieved from the project log books.  The first phase was the design of the new PET accelerator.  This ran roughly from January 1995 to October 1996.  Part of the design phase included completing experiments to test several design concepts.  Three major efforts were pursued in parallel, 1. Getting the ion source functional, 2. Characterizing the 212.5 MHz RFQ, 3.  Testing the performance of a gas jet stripper.   During this first year, project staff designed and built much of the final hardware.   A detailed series of target window break tests were performed to begin understanding the dynamics of the HEBT. Toward the end of this phase we discovered vane damage in the 425 A RFQ due to arcing during RF conditioning.  Water corrosion within the RFQ vanes was first observed at this time and resulted in leaks between the vanes and the vacuum. The collaboration now faced not only building a new fourth RFQ for acceleration to 10.5 MeV, but the need to replace the vanes in the three existing RFQs.

First beam from the new ion source took place on October 14, 1996.  One MeV beam was accelerated two weeks later and tests of the new stripper hardware began on December 12.  MEBT installation commenced in mid-January '97 and was completed by the end of the month.  First beam through the MEBT occurred on January 27, 1997.  After the delays and setbacks experienced so far, the rapid progress and quick success of the MEBT was a pleasant surprise.  Given the complexity of the task and the unproved beam physics, most members of the team predicted a longer and more difficult process in getting the MEBT on line.

Installation of the 425 A RFQ was initiated with 5 MeV beam being accelerated by March 11, 1997. Our rapid progress and relative success during this phase led to the decision to install 425 B & C simultaneously.  Installation of B and C started on April 10.  A vacuum leak in RFQ 425 C caused a short setback.  Once fixed, the first 10.5 MeV beam was accelerated on April 17, 1997. Elapsed time was six months from setting up the new ion source to  accelerating 10.5 MeV beam.  After the initial setbacks with the RFQ vanes, progress had been fairly rapid.  The collaboration expected to conclude development quickly and move to Shreveport by  the summer 1997.   This was not to be the case.

A number of activities took place in parallel during the 425 B &C commissioning phase.   The HEBT was installed, a number of radiation surveys were conducted, and  work continued daily on tuning and improving accelerator performance.  The HEBT was installed April 28 with subsequent delivery of 10.5 MeV beam to the target vault by May 2. The radiochemists performed their first target studies on May 21. The constant efforts on improving accelerator performance were paying off.  Fifty µA  of beam was delivered by May 23.   Radiation surveys indicated alarming high levels of radiation along the 425 RFQ chain.  Reasons for this were not completely understood at the time.  On June 9 we had our first RF coupler window failure.  This turned out to be a warning signal of more problems to come.

After the initial successes, the project entered probably the most difficult phase in June.  This is the portion labeled "Beam and Accelerator Improvement".  In the drive to get the beam up to 150 µA , the accelerator needed to be run at a higher duty cycle approaching the 2.5% design value.  A number of frustrating breakdowns of RF coupling loop windows occurred.  RF losses in the window caused overheating of the o-ring seal leading to vacuum failure.  The coupling loop window and o-ring seal were redesigned, fabricated and installed in all 425 RFQs and no further failure occurred.  The successive series of vacuum failures had a significant impact on RFQ cavity conditioning.  What normally could have been done in two weeks, took closer to twelve.  During this time the project also experienced a series of failures of various RF electronics modules.  These infant mortality type failures held up progress on increasing beam current until mid-August.

After the installation of the new RF coupler loop windows on July 24, rapid progress in conditioning the RF cavities occurred.  A beam current of 100 µA  was achieved by early September.  This was followed by detailed HEBT tuning to create a homogeneous distribution of beam on the target window. The next targetry session began September 24. The higher power of the beam caused overheating of one of the HEBT collimator jaws and a water leak in one of the cooling channels forced the removal of the target vacuum vessel that contained the collimators. A tungsten aperture plate was installed at the B & C RFQ junction in an attempt to stop beam from hitting the RFQ C vanes at the same time. It was hoped that this would reduce the radiation emitted from this location.  The plate did intercept beam current, but did not reduce the radiation at that junction by a commensurate amount.  The test was unsuccessful as can be seen in figure 7.7, and the plate was removed after the test.

The final phase of accelerator commissioning was installation and commissioning of the new 212 RFQ. First 1 MeV beam through the new RFQ occurred on October 16. Repairs to the HEBT collimator system were completed and the target diagnostics system was reinstalled by October 31.  HEBT scans resumed on November 9 and a targetry session began on November 10.  Results of this short session indicated we had made progress on the accelerator.  Current levels and stability were improved.

Targetry sessions began in earnest on 12/11.  We experienced a window break early in this session.  Our fast valve, designed to prevent foil from migrating into RFQ C, was not armed at the time.  The fast valve sensor was too sensitive for the type of target we were using.  We were getting premature triggering of the fast valve due to outgassing from the targets and decided to run with it disarmed.  Foil contamination in C caused excessive sparking which limited the accelerator's performance for the rest of this session.  Plans were made after this session to reconfigure the fast valve sensor system to make it less sensitive.

Our current and final phase of accelerator operations started in 1998.  This is the PET chemistry phase.  The original planned configuration of the accelerator is complete.  Our primary focus now is to provide beam as needed for the radiochemists.  Modifications and adjustments to the accelerator are done based on results of chemistry sessions.  We've had three chemistry sessions in 1998....all of them relatively successful.  Improvements to the accelerator this year to date include reconfiguring the fast valve sensor system to make it less sensitive, overhauling the water skid to fix a series of control problems, and installation of mechanical tuning paddles in the 212 and A and B cavities.  The paddles have had a marked improvement on machine stability.

1995

1996

11/7

6/26

OLD PET CONFIG./STRIPPER STUDIES

1st accelerated beam with old pet config.  12/20

window break tests

start stripper tests  3/15

discover burned vanes in 425A  6/18

complete source and stripper tests  6/26

discover corrosion leaks in 212 vanes 9/26

10/4

12/10

START NEW CONFIG./1 MeV SYSTEM ON-LINE

new source on line   10/14

1 MeV beam   12/5

stripper tests started 12/10

1997

1/20

2/9

3/1

MEBT COMMISSIONING

MEBT installation complete  1/27

MEBT beam  1/27

MEBT studies

Install 425A

3/21

4/10

425A COMMISSIONING

5 MeV beam  3/11

MEBT & 425A tuning studies

Install 425 B & C

4/30

5/20

425 B & C COMMISSIONING

10.5 MeV beam  4/17

Accelerator tuning and beam studies

HEBT installed  4/28

Beam to vault  5/2

1st targetry session  5/21

50 µA beam  5/23

RF window failure on 425 A (1st of several)

6/9

6/29

7/18

8/7

8/27

9/16

10/6

BEAM & ACCELERATOR IMPROVEMENT

RF window seal system redesign / silicone o-rings installed  6/19

target diagnostics installed 7/3

series of failures in RF electronics modules / redesign successful

targetry session

major source of radiation at 425 B-C interface verified  7/16

new RF window system installed  7/24

cavities finally condition to 360 Hz

HEBT beam scans restarted 7/25

rapid increase in current levels

beam tuning studies

beam to 100 µA level

chemistry session  9/24 - 9/27

collimator failure

tungsten aperture installed 9/29 removed 10/7

10/26

11/15

12/5

NEW 212 COMMISSIONING

new 212 on line  10/13

HEBT repairs completed

new HEBT scans started  11/9

targetry session  11/10 - 11/13

120 µA current with new 212

targetry session 12/11 - 12/16

1998

1/13

1/28

2/10

2/24

2/27

3/16

3/23

3/31

PET CHEMISTRY EXPERIMENTS

maintenance week on vacuum. systems

RF window failure in C

new fast valve configuration in

new 4616 tube installed in 425 A PA

successful chemistry run (2/10-2/15)

60 µA  on target/some stability problems

mechanical tuning paddles installed in 425 A & B

series of tuning studies started...18 mA out of 212

Fermi operator support underway

HEBT repairs completed

new HEBT scans started  11/9

targetry session  3/16 - 3/20

accelerator performance much improved

tuning paddles installed in 212

125 µA  current, improved stability

targetry session (3/31 - 4/4)

Fig. 7.1  PET Accelerator Development History

The accelerator's performance in March has been vastly improved.  Current levels, stability, and reliability have all gone up. Installation of the mechanical paddle tuning system solved the resonance control problems.  Fermi's operations group assigned two operators to help support PET in late Feb.  The additional staff support has enabled us to run longer hours and recover more quickly from occasional problems that come up.  We also now have a broader base of trained operators available.

Figure 7.2 shows blocks of time allocated to the major phases of the accelerator's development.  Interspersed within these large blocks of time are shorter tasks devoted to repairing and maintaining hardware already installed.  For example, an average of four days minimum per month were spent working on the ion source.  These overhead type tasks are discussed below under reliability.

Accelerator Performance

Beam Current

The project goal was a minimum of 150 µA  average beam current.  Figure 7.3 shows progress toward that value.  As noted in the figure,  increasing beam current at 10.5 MeV took place in three stages.  After rapid initial progress, a period of hardening systems and conditioning the RF cavities occurred.  Progress resumed in late August with 120 µA of beam achieved readily.  Commissioning the new 212 RFQ involved conditioning a new cavity and, in essence, meant starting the commissioning process for the accelerator all over. The new 1 MeV beam needed to be properly matched into the MEBT.   Progress again was fairly rapid with sustained average current above 100 µA.  We've continued to make improvements to the accelerator between beam chemistry sessions.   Beam stability at higher current levels is much improved.   We're now able to run regularly at 120 µA  at around a 70 usec. pulse.  It appears that we should be able to obtain in excess of 130 µA  at full RF pulse width of 80 usec.

Figure 7.2. Operations weeks expended on major PET project tasks.

Figure 7.3  Evolution of average beam current versus time.

Operations at higher current levels revealed a constant problem with resonance control.  Sparking in one of the cavities often caused a loss of resonance in that cavity.  This in turn changed the beam loading in cavities downstream resulting in loss of resonance in them as well.  Resonance control problems would migrate through the 425 chain, interrupting beam.  We decided to install mechanical tuning paddles developed by SAIC during the San Diego phase of the project.  These paddles would act as a fast response system, adjusting cavity resonance quickly in the event of sparks or major changes in beam loading.  We completed installation of paddles in 425 A and B by Feb. 24.  The accelerator recovered quickly, with marked improvement in performance.   Our chemistry session the week of 3/16 was the best ever, as a result of these improvements.  We installed a paddle in the 212 RFQ the week of 3/23 and plan to complete the sequence with a paddle in RFQ C in mid April.

Beam Quality

The major function of the HEBT is to take the beam that emerges from the 425 C RFQ and shape it into a form useful for targetry.  The nominal target size is 2 x 10 cm with a goal of +/- 25% maximum beam current density over that area. Beam hot spots shorten the life of the target windows. The density distribution is controlled by two magnets in the HEBT.  A quadrupole controls the horizontal distribution and a multipole controls the vertical. Fig. 7.4 presents the best current distribution achieved to date, with  +/- 50% uniformity. The actual target window occupies the zone from 3.5 to 6.5  cm on the horizontal scale and 1 to 11 cm on the vertical scale.  This distribution in the target zone runs roughly from 20 to 100 in scaled units.

Figure 7.4 .  Beam distribution on the 2 x 10 cm target window.

Accelerator Reliability

Reliability is another critical measure of the accelerator's potential utility.  The reliability data presented here is based on daily operations reports and log book entries starting June 2, 1997.  By this date, most of the critical systems had been commissioned.  Fig. 7.5 shows days per month of beam on vs. scheduled maintenance and unscheduled maintenance.  Unscheduled maintenance represents down time due to system failures.  Scheduled maintenance includes items such as planned upgrades and installation of new equipment.  Two days per month were allocated to the ion source for planned maintenance. Figure 7.6 shows beam available as a percent of operating time for the month. The dip in October being due mostly to recommissioning involved with the new 212 RFQ.  It was also during this period that daily operations and trouble shooting was delegated to the SAIC staff on site.

month

| BEAM ON | SCHEDULED MAINTENANCE | UNSCHEDULED MAINTENANCE |
| --- | --- | --- |

| TOTAL |
| --- |
| June 97 | 3.5 | 5.5 | 11 | 20 |
| July 97 | 8 | 9 | 7 | 24 |
| August 97 | 9.5 | 2.5 | 8 | 20 |
| Sept. 97 | 10.5 | 2.5 | 6 | 19 |
| Oct. 97 | 8 | 9 | 8 | 25 |
| Nov. 97 | 8.5 | 1.5 | 10 | 20 |
| Dec. 97 | 8 | 2 | 3 | 13 |
| Jan. 98 | 7 | 6 | 7 | 20 |
| Feb. 98 | 7.5 | 5.5 | 8 | 21 |
| Mar. 98 | 13.5 | 3 | 5.5 | 22 |
| total | 84 | 46.5 | 73.5 | 204 |

Fig. 7.5 Beam available in days per month.

Figure 7.6. Percentage of Òbeam onÓ time per month.. (Beam on/(Total-Sched Maint))

Improving accelerator reliability involves assessing where  problems exist.  The unscheduled maintenance noted above breaks down as follows:

Ion Source	19.5

High Level RF	17

HEBT	6

Water cooling skids	  8

RFQ hardware	6

Vacuum Systems	  5

Neslab Chillers	  4.5

Controls/Software	  4

Low Level RF	_3.5__

73.5

This data is not meant as a criticism of the design or efforts of any particular group.  It is more a reflection of the complexity of the various subsystems and the time and resources available for getting them on line.   Also, significant improvements have been made in all of these areas over the past year.

Beam current is shown as a function of pulse width for three different accelerator configurations in figure 7.7.  The middle curve (labeled Old 212 RFQ) represents the original configuration in effect until September 29, 1997.  The tungsten aperture data was described earlier. The  curve labeled New 212 RFQ represents current performance.

Figure 7.7.  Average beam current versus pulse width for three operating conditions.

Optimizing beam current and beam quality are a major part of operations. Beam current improvements are made through tuning routines, i.e. magnet settings, phases and cavity gradients are systematically adjusted while watching overall beam current and stability.  The process requires successive iterations. Targeted beam quality improvements are accomplished by doing HEBT scans, involving setting up the four collimator jaws in the HEBT so a small (typically 7 mm x 4 mm) pixel is formed.  Beam transmitted through this open rectangle is collected in a faraday cup and the integrated value is recorded in a database.  Scan data over a target sized zone provides a picture (such as Figure 7.4) of the beam's current density across the window.

Operations Radiation Safety Procedures

Accelerator operations are conducted in full compliance with FermilabÕs safety procedures and are monitored by the projectÕs Radiation Safety Officer (RSO). Operations staff are radiation worker trained and have had crew chief training.   There is a designated crew chief whenever the beam is up.  Daily operations plans are listed on  a white board in the control room.  Operations progress reports are e-mailed to the collaboration daily.  Lockout-tagout procedures as relevant are part of everyday activities.  Staff is trained and competent in handling radiation monitoring equipment such as the Ludlams, wallflowers, and friskers.  Parts and equipment removed from the accelerator and taken out of the enclosure are checked with friskers on site for contamination.

Operations Staff

The on site SAIC staff took over solo operations in mid-October 1997 after the new 212 MHz RFQ went on-line.  SAIC's operations group includes an electrical engineer (also site manager),  a full time operator, and a physicist here about 2/3 time.  In addition a full time mechanical engineer is available to support targetry work and mechanical engineering related items, plus  part time support from an engineering-physicist who is experienced in RFQ technology.  Members of this team have an average of about seven years experience in accelerator projects.  Three members were principals in the highly successful implementation of the Loma Linda project.

Fermi operations staff began supporting PET in late Feb.  Currently two trained Fermi operators are assigned to PET on a rotating basis.  Shifts include day (8 to 4) and evening (4 to midnight).  Control room operators on duty over the owl shift (midnight to 8 am) monitor RF and vacuum system performance on monitors in the control room.

Targetry Sessions

There have been eight sessions of targetry experiments with the PET accelerator to date.  The first five sessions, taking place in 1997, were limited in results by the accelerator's uncertain performance and incomplete development. The first and second target sessions (May 21, 1997 & July 9, 1997) consisted of a shakedown of the control/hardware systems and initial foil irradiations.  The foil irradiations are a means of cross checking the beam density distribution. Beam current levels were 30 µA  average.

The third session  (September 23, 1997) was planned to be the first chemistry session with the accelerator fully operational.  Beam currents approaching 100 µA were available, but it was also during this period that the HEBT sprang a water leak due to overheating. The vacuum problem caused by the leak was overcome in a couple of days and testing of Havar target windows was initiated.  It was apparent that more HEBT tuning was necessary due to excessive hot spots on the target window.

The fourth targetry session began November 10, 1997.  The new 212 RFQ was installed at this time, but beam currents approaching 100 µA had not yet been reestablished (60 µA was delivered). The radiochemists completed three carbon foil counts during this period to characterize the HEBT beam.  After some adjustments in the HEBT, beam uniformity measured by radiating foils was comparable with HEBT collimator scans.  A new gridded target window support structure was also tested successfully.

We started the fifth chemistry session on 12/11.  We had 80 µA  of beam current available initially.  A foil window break resulted in contamination of RFQ C with some bits of conductive foil which led to severe sparking in C.  This limited the accelerator's performance for the duration of this session.  We were able to collect data for a gas target and complete several tests of different types of foils.

The three sessions held so far (Jan. through Mar.) in 1998 have been much more productive.  We've generally been able to supply beam in the amounts needed, as needed, with much improved beam stability.  The chemists have successfully tested a variety of gas, solid, and water targets and proceeded with successful isotope yield studies and extraction.

Summary

The effort to date on building the accelerator has exceeded the original estimate by six to eight months and about $2 million.  As has been discussed in the report, numerous difficulties unforeseen at the outset of the program have caused this delay and extra expense.  The team's constant efforts and improvements to the accelerator appear to have produced good progress over the past few months.  The accelerator's performance and reliability have  improved significantly.  At this point we fully expect to be able to successfully support the radiochemistry program.

8. Beam Instrumentation and Diagnostics Systems

Introduction

The machine as delivered to Fermilab in 1995 included little beam instrumentation equipment deemed suitable for this project. The only beamline components recovered were three Pearson transformers for measuring beam current. Of the limited signal processing electronics provided, only the beam current integrating instrument for Òbeam on targetÓ was compatible with the machine requirements and suitable for integration into the control system. The beam instrumentation systems have been completely re-built as a part of this project.

System Design at Fermilab

Considerations and Requirements

Uncertainties in the expected performance of individual RFQs, novel charge stripper and MEBT designs, limited space in the machine layout for important diagnostics, and beam power capable of damaging certain instrumentation devices necessitated a staged beam commissioning process. This presented a wide variety of overall beam instrumentation requirements.

Transverse emittance measurements were desired at 20ÊkeV, 1ÊMeV, and 5ÊMeV. Energy and charge state characterization of the 1 MeV beams out of the 212 MHz RFQ and the charge stripper were required. MEBT commissioning required transverse beam profile and position measurements at several locations and a longitudinal bunch length diagnostic at the MEBT downstream end. HEBT and target commissioning called for detailed transverse beam current distribution measurements of the full power 10.5 MeV beam. A calibrated Faraday Cup/beam stop is necessary for operational tune-up and to protect the chemistÕs target during tune-up and between runs. An accurate Òdose on targetÓ measurement capability is required for chemistry experiments. Beam current measurement throughout the accelerator was important at all stages.

Design Decisions

Assessment of the perceived requirements in conjunction with budget and scheduling considerations led to a plan for provision of beam instrumentation and diagnostic systems.

Non-intercepting beam current transformers would be permanently installed along the machine where appropriate and space allowed.

A water cooled charge collector/beam stop suitable as a temporary fixed diagnostic for full current at any of the beam energies of concern would be built for the project.

Transverse emittance measurements would be accomplished utilizing a system borrowed from the Fermilab ion source development lab.

A simple 1 MeV spectrometer using a borrowed Fermilab magnet would be fabricated.

Multiwire or harp style monitors would be designed and fabricated for transverse beam profile measurements at 1 MeV in and following the MEBT. These would not be actively cooled and therefore would be useful only at low beam pulse repetition rates (<= 10 Hz).

Faraday apertures, beamline apertures constructed of segmented charge collecting electrodes, would be used as non-destructive beam size and position indicators at numerous locations in the machine.

The MEBT would be constructed with three insertion locations designed to accept either a dual plane multiwire profile monitor assembly for commissioning or a Faraday aperture assembly for high duty cycle operations.

A beam intercepting wire would be used as the source for relative longitudinal bunching signals at the output of the MEBT.

No room exists between the three 425 MHz RFQs in the final layout for any type of beam instrumentation device.

A collimator with four water cooled, independently and remotely controlled, isolated charge collecting jaws would be designed and built to be installed at the end of the HEBT for 10.5 MeV beam collimation and diagnostics.

A properly designed Faraday Cup would be built to be located between the collimator and the chemistry target.

New signal processing electronics designs and fabrication would be kept to a minimum.

Beam instrumentation signals would interface directly with the existing Control System Internet Rack Monitor analog input hardware.

System Descriptions and Operational Performance

Beam Current Measurement

Five current transformers are installed - at the ion source output, at the 212 MHz RFQ output, at the charge stripper output, at the 425 MHz RFQA input, and in the HEBT. Pearson Model 2100 transformers, 0.5 mV/mA into 50 ohms, are used throughout. Signals are processed by the toroid and charge collector electronics described below.

A credible ion source beam current measurement is obtained when the source magnet is at a nominal current and the LEBT solenoid and steering magnets are de-energized. With the LEBT magnets energized and the source magnet adjusted for maximum beam current at 1 MeV from the 212 MHz RFQ, the ion source transformer signal becomes distorted and its calibration ambiguous.  This is believed to be due to stray magnetic fields and/or to electron currents due to beam striking the transformer. Even under these conditions the signal is a useful diagnostic always on display on an oscilloscope in the control room.

The remaining transformers provide reliable signals accurate to within 1 milliamp over a wide range of normal operating conditions.

Emittance Measurement

A slit and collector emittance measurement system, including actuator and control and signal processing electronics, was borrowed from the Fermilab ion source development lab. This was used to make measurements on the PET machine beam at 20ÊkeV, at 1ÊMeV (with and without the charge stripper and before and after the MEBT), and at 5ÊMeV (with only 425 MHz RFQA in place). Only minor mechanical modification to the slit and collector head and to the vacuum interfaces was required. All emittance measurements required dedicated mechanical and vacuum setups of the machine. No emittance measurement capability remains in the operational accelerator. Results of the emittance measurements are published elsewhere1. The internal papers section of the PET Web page2 contains several other articles on the emittance measurements.

Spectrometer

A specially designed fan shaped vacuum chamber coupled with a borrowed Fermilab magnet served as a spectrometer to make measurements of the 1 MeV beam. The chamber was terminated with three isolated disks serving as Faraday charge collectors and two isolated vertical wires between the Faraday collectors. The disks, each sized to accept the full beam spot, were placed at angles of 0, 11.5 and 23.6 degrees. Installed downstream of the charge stripper, this spectrometer arrangement permitted measurement of straight-ahead beam with the magnet de-energized and simultaneous measurement of singly and doubly charged helium beams with the charge stripper and analyzing magnet operating.

Signals from the Faraday collectors facilitated energy analysis and charge stripper efficiency measurements. Signals from the vertical wires provided horizontal beam profile measurements as the beams were scanned across the wires with the analyzing magnet. This proved valuable to watch for beam blowup during stripper development using different gases and at different pressures.

A diagram of the spectrometer and additional information can be found elsewhere in this report3.

Profile Measurement

Multiwire (harp) beam profile monitors were specially built for use during MEBT commissioning. Each monitor provides for both horizontal and vertical measurements with nine 0.002Ó gold plated tungsten wires in each plane. These monitors were located at the entrance to the first MEBT alpha magnet, at symmetrical locations in the MEBT cross-over arm between alpha magnets, and at the RFQA match point downstream of the MEBT.

Space in the MEBT is extremely tight, limiting design options of the profile monitors. Wire heating due to absorbed beam energy was also a serious concern. A compact wire mounting scheme with built-in tensioning lever arms was conceived and implemented to limit wire sag and distortion at elevated temperatures. The design was tested by heating wires to >1000 K with electrical current. Beam operation was limited to 10 Hz pulse repetition rate while the profile monitors were installed. In spite of these precautions, considerable discoloration of the wires was observed when the monitors were removed and several wires were found broken.

Signal wiring was arranged to utilize the same multi-channel electronics as the emittance measurement system. Up to four planes of profile monitoring could be processed simultaneously. The profile measurement capability proved invaluable for commissioning and tune-up of the novel MEBT beamline.

Faraday Apertures

Each Faraday aperture consists of four isolated electrodes (top, bottom, right, and left) which form an aperture limit in the local beamline. Signals from the electrodes in conjunction with steering and focusing scans of appropriate magnets provide some information on beam size and position. These appeared attractive as small, simple, inexpensive devices which would provide important diagnostic capability. Apertures were designed for the input of the 212 MHz RFQ, the input of first MEBT alpha magnet, two symmetrical locations in the MEBT cross-over arm between alpha magnets, and the input of the 425 MHz RFQA.

Originally, it was thought that this type of device alone might be sufficient for MEBT commissioning. Fortunately, further consideration led to the decision to construct the MEBT with three insertion locations designed to accept either a multiwire profile monitor assembly or a Faraday aperture assembly. As it turned out, the Faraday apertures alone would have been woefully inadequate to provide the diagnostics required for MEBT commissioning. Even after commissioning, the Faraday aperture upstream of the 212 MHz RFQ and the three in the MEBT have been of limited value.

The Faraday aperture immediately upstream of the 425 MHz RFQA, however, has proved operationally essential for a reason not imagined during the machine design. During commissioning it became apparent that the beam path length and therefore transit time through the MEBT is extremely sensitive to MEBT tuning. Phasing between the 1 MeV beam bunches and the 425 MHz RFQs was tightly coupled to MEBT magnet adjustments. A 0.1% change in alpha magnet current resulted in a 90 degree relative phase shift between the beam and the 425 MHz RF. This coupling made tune-up quite difficult.

The Faraday aperture provides a solution. The small fraction of the beam impinging on the aperture yields a 212.5 MHz signal which represents the beam phase entering 425 MHz RFQA. This must be held constant relative to the 425 MHz RFQ cavity voltage. The 212.5ÊMHz signal is amplified, frequency doubled and phase compared to a sample of the 425 MHz RF. The result is used as feedback to adjust the 212 MHz RFQ phase and thus stabilize the beam phase entering 425 MHz RFQA. A trombone delay line in the beam RF signal path facilitates setting the desired operating point.

This aperture arguably has served another purpose. The electrodes were originally made of copper. During the rebuild of MEBT Q5 magnet, the electrodes were exposed for inspection. It was learned that the electrode on the right side, as the beam sees it, had at some time been heated to the point of puddling the copper and causing a short circuit of that one electrode to ground. Investigation using information in the datalogger showed a dramatic change in that electrodeÕs signal during a period in which beam had been run at 360 Hz with some MEBT quadrupole magnets not energized. The aperture may have protected the RFQ from damage. Subsequently the copper electrodes of this aperture were replaced with ones made of tungsten.

In addition to the RF signal processing used for phase feedback control, each Faraday aperture electrode at each location is served by a channel of the toroid and charge collector electronics.

Longitudinal Measurement

The MEBT is designed to reflect at its output the longitudinal phase space parameters of the input beam. The degree to which this imaging is achieved is sensitive to MEBT magnet strengths. Commissioning thus required a longitudinal diagnostic to determine relative bunch length at the 425 MHz RFQA match point to confirm design performance and to find the correct operating point.

Field spreading due to the low velocity of the 1 MeV beam rules out the use of non-intercepting monitors for the required high frequency measurement. An intercepting wire which provides prompt signals from some combination of secondary emission and charge absorption is suitable. Flat response over a large bandwidth is not required for relative bunch length measurements. The relative amplitude of the 212.5 MHz signal and one or more harmonics can be measured with a spectrum analyzer under different MEBT tuning conditions and the relative bunch lengths of each condition inferred.

A dedicated intercepting wire was originally planned for this purpose, though it was found during commissioning that a suitable signal was available from the multiwire profile monitor installed downstream of the MEBT. It was also found that the wideband response of this device was adequate to provide a time domain signal which yielded unambiguous bunch length information when viewed on an oscilloscope.  The network analyzer and oscilloscope methods produced results in agreement with each other and both were used to set up the MEBT.

Collimator and Faraday Cup

The HEBT collimator and Faraday cup are located immediately upstream of the target vacuum isolation valve at the end of the HEBT. The primary function of the collimator is to limit the beam spot size on the chemistry target. The Faraday cup serves as a full power beam absorber and a calibrated beam current monitor. In combination, the collimator and Faraday cup serve as a sort of pinhole camera diagnostic to measure the beam current density distribution directed at the chemistry target.

The collimator consists of four flat rectangular jaws each fabricated as a sandwich consisting of a thin tantalum face plate and thicker copper back plate. To minimize neutron production, only the tantalum is exposed to the beam. The back plate has machined channels for cooling water and is soft soldered to the face plate.

Each jaw is independently and remotely controlled with a stepper motor and is equipped with a position readout potentiometer. The right/left jaws are situated slightly upstream of the top/bottom jaws to avoid mechanical interference and permit either pair to be nearly fully closed. Electrical limit switches prevent opposing jaws from colliding. Each jaw is electrically isolated to allow electrical biasing and to provide a beam charge collection signal. Thermocouples on each jaw provide for temperature measurement.

The Faraday cup is a water cooled, concave rectangular box-shaped beam stop. Like the collimator, it is fabricated of sandwiched tantalum and copper though the bonding method is different4. The back plate provides channels for water cooling. The cup is pneumatically actuated for insertion into and withdrawal from the beamline. Redundant microswitches provide position status to the control system and to the radiation safety system. A thermocouple provides for temperature monitoring. The cup is electrically isolated to allow electrical biasing and provide the beam charge collection signal. A separate electron suppresser diaphragm is installed immediately upstream of the Faraday cup to improve the cupÕs charge collection efficiency and accuracy.

The collimator and Faraday cup are housed in a common vacuum chamber. This assembly is a complicated mechanical design with moving parts, cooling water hoses, switches, instrumentation, and electrically isolated elements all in a compact volume which must operate under high vacuum. It is the product of a considerable and careful mechanical design effort.

For machine commissioning the Faraday cup served as the primary high energy beam absorber and beam current monitor.

Beam current density distribution measurements, necessary to commission the HEBT for targetry work, are made by stopping the collimator down to an aperture small relative to the beam size and measuring the transmitted beam current on the Faraday cup. As the aperture is moved across the beam, the current distribution can be mapped out. A Labview application running on the control system computer provided coordinated aperture scanning control and Faraday cup signal acquisition. This fully automated method provides for quick and clean first order measurements of beam distribution as a function of HEBT magnet settings. A great deal of time was saved and personnel radiation exposure was significantly reduced over the alternative beam density determination method of cutting and counting the activation of a carbon foil exposed to the beam. Initial specifications for the collimator called only for variable horizontal and vertical aperture with fixed center position. The decision to adopt the more flexible design was well rewarded in the reduced HEBT commissioning efforts.

For chemistry experiment operation, the Faraday cup is used as the beam stop for tune-up and protects the chemistÕs target from exposure during tune-up and between runs.

Chemistry Target

With the exception of electrical biasing and charge integration electronics, target instrumentation is provided by the radiochemists.

A plastic interface ring, attached to the vacuum valve at the end of the HEBT, is provided for target mounting. This ring also provides electrical isolation of the target and contains an electron suppresser electrode. Accurate collection of the beam charge striking the target is important to the radiochemists for recording target dose. The suppresser electrode serves to reflect electrons which may otherwise scatter off the target and reduce the charge capture efficiency. The suppresser connects to a channel of the toroid and charge collector electronics and receives from that a negative 45 volt bias.

The electrically isolated target connects to a commercial current integrator, the BIC5, which presents a low impedance input. A box containing two 45 volt batteries connects in series with the BIC input to provide a positive 90 volt bias on the target. Beam current measurement agreement among the BIC, Faraday cup, and HEBT current transformer is better than 5%.

Toroid and charge collector electronics

A single electronics module design6 was conceived to handle signals both from beam current transformers and from charge collecting electrodes including Faraday apertures, collimator jaws, and the Faraday Cup. Each NIM format module contains eight channels, four dedicated to charge collecting electrode signals and four which may be configured at time of board loading for either charge collector or transformer signals.

A current transformer signal channel provides 46 dB gain with ³Ê100 KHz bandwidth to amplify signals up to levels suitable for control system IRM sample and holds and digitizers. Output is scaled to 100 mV/mA for Pearson Model 2100 transformers.

A charge collecting electrode signal channel provides DC coupled charge amplification. A current-limited, user-selectable polarity, electrode bias voltage is provided by optional batteries housed within the module, e.g. the 45 volt Eveready Type 415. Two signal outputs are generated - a wideband (> 1 MHz) output scaled at 250 mV/mA for monitoring signal modulation during the beam pulse and a narrow band (0.5 Hz) output scaled at 20 mV/µAmps for monitoring average electrode current. A user-activated 10 µAmps current source is included for test/calibration purposes.

Present Status

Figures 8.1 and 8.2 show the location of beam instrumentation devices in the low energy end of the machine and in the HEBT respectively. No beam instrumentation exists between the upstream end of 425 MHz RFQA and the downstream end of 425 MHz RFQC.

All beam current transformers and electronics are fully operational and integrated into the control system.

All emittance measurements require dedicated mechanical and vacuum setups of the machine. No emittance measurement capability remains in the operational accelerator. The hardware and electronics has been returned to the Fermilab ion source development lab. It remains available if needed for any reason at a later date.

The spectrometer setup has been dismantled and the magnet returned. The fan shaped vacuum chamber, Faraday collector disks, and associated hardware remains with the PET project.

No profile measurement capability exists in the operating machine. The multiwire monitors have had any broken wires repaired and, along with the signal cables, remain with the PET project. The signal processing electronics used was part of the emittance measurement system and has been returned to the Fermilab ion source development lab. It remains available if needed for any reason at a later date.

The Faraday apertures at the locations described are fully operational and integrated into the control system. Experience has shown them to be of little utility for their intended purpose. The Faraday aperture immediately upstream of the 425 MHz RFQA remains crucial to stable machine operation serving as a beam RF phase pickup. The phase signal processing and phase detection circuitry in the present operating machine remains a poorly organized and packaged assemblage of cables and components. For now the system performs satisfactorily in spite of its state, however it requires further attention before the machine should be declared finished.

Aside from the Faraday aperture used as the phase pickup, the operating machine has no dedicated longitudinal beam measurement systems.

The collimator and Faraday cup are currently being re-installed in the machine following a failure of one of the collimator plates. Apparently the plate was over-heated by the beam due to lack of cooling. The soft solder joint between the tantalum and copper gave way creating a leak from the water channel to the vacuum. This leak has been repaired. Changes are being implemented to assure adequate cooling water flow, to assure better temperature monitoring, and to provide suitable interlocks. At the same time, several other mechanical changes including new water fittings have been implemented to improve reliability. When this assembly was removed for repair it was also observed that the Faraday cup had experienced some extreme conditions. The tantalum surface showed signs of superficial melting or sputtering. Circumstances which may have caused this have not been determined; it is conceivable that the beam may have been run with the cooling water to the cup valved off. Flow interlocks are to be installed to prevent this possibility in the future.  However, since the circumstances under which the damage occurred are not

Figure 8.1   Low Energy and MEBT Beam Instrumentation Layout

(MIM supports either Segmented Faraday Aperture or Multiwire Profile Monitor)

Figure 8.2  HEBT Beam Instrumentation Layout

definitely known, the condition of the Faraday cup surface should continue to be monitored.

The BIC target current integrator, target electron suppresser electrode, biasing and signal processing electronics are fully operational as described and integrated into the control system as required.

The Toroid and Charge Collector electronics is performing as designed and as required. Four modules serve the needs of the operational machine. One spare module resides with the project.

All beam instrumentation required for normal operation of the machine is presently operational and integrated into the control system. The instrumentation is functioning satisfactorily and, with the exception of the beam phase circuitry, is in a desirable final state. The special commissioning instrumentation has been returned to its rightful owner or set aside for future use in the PET project. If the machine is relocated and must go through extensive re-commissioning this instrumentation remains available.

References

1.  E. McCrory, M. Popovic, C. W. Schmidt and P. Young, Emittance Measurement Techniques Used in the 1 MeV RFQ for the PET Isotope Linac at Fermilab, submitted to the 1996 International Linac Conference in Geneva, Switzerland, Aug. 26-30, 1996.

2. http://www-linac.fnal.gov/pet

3.  See the ÒCharge DoublerÓ section in Chapter 6 of this report.

4.  See the ÒHEBTÓ section in Chapter 12 of this report.

5. Model 1000C Current Integrator, serial number 3845, Brookhaven Instruments Corporation, Austin, Texas.

6.  Fermilab drawing #9700-EC-348015.

9. Equipment Interlocks

Introduction

This report covers the equipment interlocks for vacuum systems,  power supplies and other related systems.  Personnel safety issues such as electrical protection and radiation interlocks are covered in other reports.

System Overview

The PET Accelerator contains a wide variety of equipment encompassing many different requirements for control and status signals.  Two main areas requiring reliable intelligent control are the vacuum systems and the magnet power supplies.  Information on water conductivity and temperature are needed by a variety of systems.  Other signals just need a simple interface to the control system.  In order to provide maximum flexibility and ease of installation and use, an industrial programmable logic controller (PLC) was chosen for these tasks.

Reasons for using a PLC

Commercial Availability

This project provided an opportunity to use many commercially available products.  The PET accelerator is small compared to other installations at Fermilab so the trade-offs between purchased and custom built solutions were easy to calculate.  The possibility of transferring the accelerator to another institution required that the installation and maintenance utilize standardized, readily available parts and equipment.

Variety of Devices and Signals

Each section of the accelerator has a complete vacuum system consisting of a roughing pump, thermocouple gauge, foreline valve, turbomolecular pump and full range gauge (FRG).  The gauges provide analog signals, the valves are controlled by 24 VDC solenoids, the pumps require 24 VDC signals or relay contacts for control and provide 24 VDC signals or relays contact for status.  The five different types of turbo pump controllers require different combinations of 24 VDC signal and relay contacts for control and status even though the units all perform the same general function.  The PLC allows each vacuum system to be presented to the control system in a uniform fashion.

The power supplies require relay contacts or DC voltage to permit operation.  Each of the magnets is protected against over-temperature and some are water cooled.  One signal representing the water conductivity affects many power supplies and RF systems.

Other signals which require conditioning or distribution by the PLC include operator switches, water flow, water temperature and other assorted thermocouple readings.

PLC Systems Requirements

Analog Inputs

The vacuum controls require 40 analog input channels in addition to the variety of 24 VDC and relay signals.  The selection of a PLC for this project was partially driven by availability of analog input modules.  The 405 series by PLC Direct1 has appropriate analog input modules at reasonable cost.

Communications protocol

The PLCs must be remotely controllable and readable through the standard parameter pages and graphics pages of the PET control system.  This dictated that at least one Fermilab Internet Rack Monitor computer (IRM) be able to communicate with the PLCs.  The non-proprietary DirectNET protocol2 used by the PLC Direct products was well suited to be incorporated as an IRM routine.  Many other PLC manufacturers have proprietary protocols which require special hardware or software for external communications.

Vacuum PLC

Electrical Distribution

The variety of sensors, relays and solenoids require distribution of 24 VDC power either directly to the sensor or to the PLC contacts to activate the device.  The typical vacuum valve actuator requires 150 mA for activation.  The vent valve solenoids require almost 1 ampere each.  Each vacuum PLC chassis has a bulk 10 ampere 24 VDC supply to provide the necessary power.  Since all of the wiring to field devices uses 24 gauge wire, the distribution of 24 volts to the actuators is protected against overload by positive temperature coefficient (PTC) resettable fuses.  Each branch is limited to less than 2 amps.  A separate 1.75 amp 24 VDC supply is used at each PLC to provide clean power for the full range gauges.

Types of Equipment

The roughing pumps have no provision for remote control and no status.  Although solid state relays were originally installed for controlling the pumps, it was found that only the target roughing pump needed to be controlled.  The thermocouple gauges on the roughing line provide indirect status on the state of the roughing pump.  The foreline valves require 24 VDC control and have either one or two limit switches for status.  The turbo pumps have On/Off control and return status for On and >80% nominal speed.  The turbo valves have 24 VDC control and two limit switches for status. Full range gauges require 24 VDC power and provide log scaled analog voltage reading of the pressure.  The isolation valves have 24 VDC control and two switch readback.  Vent valves have only 24 VDC control.  The fast valve requires 3 relays for control; Open, Close and Arm, and provides status for Open/Closed, Local/Remote and Tripped/Ready.

Modules used

Since the central accelerator racks were designed to be separated for shipment, the vacuum PLC uses two chassis.  The main chassis in rack PETR07 contains the CPU, two 32 bit 24 VDC input modules, one 32 bit 24 VDC output module,  two 8 channel relay modules, two 8 channel analog input modules and a master module for remote chassis communications.  The slave chassis in PETR15 contains the slave remote I/O module, one 32 bit 24 VDC input module, one 32 bit 24 VDC output module,  three 8 channel relay modules, one 8 channel analog input module, one 8 channel type J thermocouple input module and one 8 channel type K thermocouple input module.

Communications

The vacuum PLC has a 19,200 baud serial port connection with IRM node 586.  40 words of analog status and 16 words of digital status are read during each transfer.

Communications with the power supply PLC involve exchange of just a few bits.  Water conductivity, heartbeat bits and RF Permit use 24 VDC signals on a multiconductor cable between the two PLCs.

PLC Logic

Traditional relay ladder logic and more advanced state machine functions are used.  The full logic diagram is available on the PET Web site 3. In addition to the status of the individual devices in the vacuum systems, the operator receives an indication of the present state of the pumping sequence.  The PLC states are; Off, Roughing Pump Check, Turbo Accelerating, Waiting to Pump, Pumping Down, Vacuum OK, and Venting.  The sequence of operation of the vacuum pumps and valves depend upon the state of the vacuum in the section of interest.  Given the command to pump down, the PLC must first determine the level of the vacuum in the chamber.  The full range gauge (FRG) provides a voltage output proportional to the log of the pressure and is the primary means by which the PLC measures the vacuum.

If the chamber pressure is above about 10-3 Torr, the system can be rough pumped without concern about back streaming.  First the roughing pump is checked by looking at the thermocouple gauge voltage.  When the foreline vacuum is within the proper range the foreline valve is opened and the turbo pump is started.  The vacuum is considered normal when the turbo is above 80% of nominal speed, the valve and roughing status are correct and the chamber pressure is below a predetermined limit.

If the chamber pressure is below what the roughing pump can provide, the turbo pump is started and the foreline valve is not opened until the turbo is above 80% of nominal speed and the roughing pressure is correct.  This assures that there will be no back streaming of oil or other contaminants from the roughing lines.

Many of the vacuum sections in the accelerator are not isolated from each other and require coordination of the vacuum pumping sequence to provide proper pumping and to prevent damage to the pumps or oil contamination of the accelerator components.  The three beam line valves not only isolate the vacuum in the accelerator but can also intercept the beam.  Proper sequencing of the valves offers equipment protection and reduction of prompt radiation during a vacuum fault.

A mild pressure rise in an RFQ, possibly due to sparking, will cause the PLC to remove the low level RF permit until the vacuum recovers.  A general vacuum fault, due to a pump tripping off or a leak, will be reflected in the status from the turbo pump or the rise in pressure.  The PLC will close the appropriate valves to isolate the section.  If the pumping system status returns to normal or an operator resets the system, the PLC will attempt to restart the pump-down sequence.

In the event of a target vacuum fault that causes the fast valve to close, the PLC will issue a fast beam inhibit to the low level RF system until the source isolation valve is closed.  This reduces the amount of 10.5 MeV beam deposited on the fast valve.  The PLC also stops the water flow to the target diagnostics and closes all the vacuum valves in the target and HEBT.

The entire vacuum logic uses 1562 words of the 15K available.  Typical scan times are 25 mSec.

Power Supply and Water Skid PLC

Types of Equipment

Thermal switches (klixons) are on the eight water cooled magnets.  The IRM provides a beam inhibit signal. The beam permit switch comes in from the control room.  Seven status contacts come from the water skid.  Power supply status is reported from the IRM over the serial link.

Modules used

Two 16 bit 24 VDC input modules, one 16 bit 24 VDC output module and two 8 channel relay modules are used.

Communications

The power supply PLC has a 19,200 baud serial port connection with IRM node 587. 16 words of digital status are read during each transfer.  Power supply status changes are written into the PLC by the IRM.  A few bits are exchanged with the vacuum PLC over a multiconductor cable.

PLC Logic

Ladder logic is used for the power supplies and water systems.  The full logic diagram is available on the PET Web site4.  The entire power supply and water skid logic uses 652 words of the 15K available.  Typical scan times are 17 mSec.

Power Supply Operation

The primary requirement for magnet power supply control is protection of the magnets from over temperature.  In addition, ground fault detection and water flow protection are provided by the combination of the IRM and the PLC.  The IRM handles monitoring of the magnet current and ground fault voltage.  Fine resolution current regulation loops run in the IRM. The PLC continuously monitors a heartbeat bit from the IRM to assure that the IRM is operating correctly.  The heartbeat bit is read from the PLC serial port by the IRM and returned over a hardware connection.  Loss of the heartbeat for more than 30 seconds will cause the PLC to shut down the power supplies.  The PLC also provides a convenient method of transferring overall power supply status to the control system.

Water Systems

Even though the water skid is capable of stand-alone operation, the ON/OFF control and general status are routed through the power supply PLC to provide a uniform interface to the control system. The PLCs also monitor water flow in the RFQs and LCW conductivity and temperature.  If flow or vacuum are out of limits for a particular RFQ, the vacuum PLC will inhibit the RF power amplifier.  The vacuum PLC will inhibit operation of the RF power amplifiers and the power supply PLC will inhibit magnet power supplies if the LCW conductivity is out of tolerance.

Other Functions

The power supply PLC provides a beam permit to the low level RF system.  The vacuum PLC can quickly inhibit the RF using this bit in cases of poor vacuum in the RFQs or if the fast valve closes.  This beam permit can also be removed by any of the IRMs or by flipping a switch in the control room.

Operational Experience

The PLC systems were easy to install and connect.  In general, cable routing and terminal block crowding were the areas requiring the most attention.  The ribbon cable connections to the 32 bit I/O modules helped alleviate some of the cabling congestion although with the added cost of the transition terminal blocks. Indicators on the front of the digital modules provides an easy means for monitoring input and output bit status.  No PLC hardware has failed.

PLC programming was easy to learn.  The ladder logic and state machine functions evolved during the installation and testing of the various sections of the accelerator.  The software allows real time monitoring of the internal bit values which helps in debugging the PLC logic.  The ability to change programming without shutting down the PLC has been extremely helpful in keeping the machine running smoothly.  It is interesting to note that the vacuum PLC logic requires over 40 pages to print out but consumes only about 10% of the available PLC program space.

Summary

The equipment interlocks in the PET accelerator require reliable, intelligent control beyond what can be provided by simple circuitry or external high level computer monitoring.  The use of inexpensive commercially available programmable logic controllers provides a flexible means of sequencing vacuum systems and monitoring power supply and water parameters.  The PLC modules are able to handle the variety of signal types needed to control and monitor the accelerator systems.  Additional functionality is easily added without the need for rewiring in hardware.  The programming of the PLC is relatively simple and provides for ladder logic and state machine representations.

References

1.  PLC Direct, 3505 Hutchinson Road, Cumming, GA 30040.  Phone : 800-633-0405 Web address : http://www.plcdirect.com

2.   http://garlic.fnal.gov/LINAC/software/locsys/localapp/DirectNETPLCAccess.html

3.   http://garlic.fnal.gov/pet/papers/plc_stuff/VacuumLadder.pdf

4.   http://garlic.fnal.gov/pet/papers/plc_stuff/PowerLadder.pdf

10.  Radiation Safety & Shielding

Introduction and Background

The original PET RFQ accelerator beam energy was 8 MeV.  It was thought that the 8 MeV PET RFQ accelerator would produce little radiation (BI, 1994)1, and thus radiation safety and shielding would not be major issues.  In fact, the original accelerator was to be located at BRF on the second floor of a building with little shielding.  Furthermore, the desire was to have continuous occupancy in the room that contained the accelerator.  This would require minimal beam losses along the length of the accelerator.  Transmission efficiencies for this initial 8 MeV design were predicted to be 97% and thus beam losses might be small enough.

When the PET RFQ Project was resumed at Fermilab, the collaboration decided to increase the beam energy to 10.5 MeV.  The issue of shielding had to be revisited for this higher beam energy.  A significant amount of time was spent trying to determine what the beam on target and accelerator loss radiation levels might be.  The RFQ vanes were composed of copper plated aluminum, and no published cross sections could be found for 10 MeV 3He incident on copper or aluminum.  Few published cross sections existed in literature for low energy 3He incident on any metals.  At the same time transmission efficiencies were being determined for the 10.5 MeV accelerator design.  Indications were that 20% of the beam would be lost in each RFQ, a number significantly higher than the initial designÕs predicted 97% transmission for the entire accelerator.  If losses were near 20% in the final RFQ, where the beam energy was at least 8 MeV, dose equivalent rates due to neutron production could be high (GR, 1997)2. Further study of the 10.5 MeV PET RFQ accelerator (GR, 1997)2 showed that the target vault would need to be sizable also.

Fortunately, Lab G, where the accelerator was to be located at Fermilab, already had a significant amount of shielding in place.  There was a concrete wall at least 6' thick between the accelerator location and the Control Room.  In addition, the accelerator location is surrounded by at least 3' of concrete on three sides and has a large steel magnet on the fourth side, thus making shielding outside the accelerator enclosure not much of an issue at Fermilab.  Previously the Lab G accelerator area had also been interlocked.  If the dose equivalent rates exceeded 100 mrem/hr  (FRCM, 1998)5, adding interlocks to the accelerator area would not be too difficult.  Due to lack of published cross sections for this beam energy and type, it was decided that frequent measurements would need to be made during commissioning to determine the extent of the radiation levels due to both beam on the targets and beam losses in the accelerator.

While the calculations of the accelerator and target radiation levels were being performed and studied, the first RFQ (212 MHz) was being commissioned with RF.  Measurements of x-ray production from the RFQs at SAIC had shown that 1/8Ó of lead was sufficient to reduce the rates below 2.5 mrem/hr at one foot.  At the time, it was not clear what the exact parameters of the RF were when these measurements were taken, or what instrument was used.  It was clear that some shielding would be needed at Fermilab if the collaboration wanted to have the accelerator room be a continuous occupancy area.  The x-ray radiation levels at maximum RF power and duty cycle were found to be very high.  Several layers of lead blankets and interlocked detectors were used to ensure personnel safety.  It was decided that the RFQs would all be encased in thick (~1.3 inches) stainless steel vacuum vessels to keep the x-ray levels below 1 mrem/hr at one foot.

Another issue that complicated the shielding and interlocks for Lab G was that the radiochemists wanted to be able to enter the accelerator enclosure with the beam hitting a molybdenum Faraday cup just upstream of their target.  Indications were that the dose rates from full beam on molybdenum might be quite high.  The high coulomb barrier of tantalum and the fact that the Faraday cup could be made out of tantalum, made tantalum seem a good alternative material.  It was hoped that the radiation levels on the tantalum would be below 20 mrem/hr at one foot, the maximum dose equivalent rate allowed for beam on access at Fermilab.  Only the chemists would be allowed to enter under these conditions, and interlocked detectors in the area would remove the beam if dose rates became too high.  The allowed beam on dose equivalent rate for personnel access based on the LA Regulations (LAC, 1996)4 appeared to be 100 mrem/hr.  Thus even if beam on access were not possible at Fermilab, it could be at BRF.

The accelerator continued to be commissioned at Lab G.  Preliminary measurements were made of the x-ray energy spectrum (GRO, 1997)3 in order to help understand both the shielding and the 212 MHz RFQ acceleration.  These measurements indicated a higher x-ray spectrum than was initially expected, with the maximum x-ray energy being near 90 keV.  Once the RFQs were encased in the steel cans, the x-ray level dropped as predicted.  Beam was slowly commissioned and the first neutron radiation was seen at 5 MeV, at the end of RFQ A.  It was decided at that point to add RFQ B and C at the same time, rather than commission 8 MeV beam with RFQ B only, thus jumping from 5 MeV to 10.5 MeV.  The neutron levels at 5 MeV were high enough to indicate that the area would most likely need to be interlocked for 10.5 MeV beam.  At that point the accelerator enclosure interlocks and gates were installed.  The three interlocked radiation detectors around the accelerator, that were used during commissioning to ensure personnel safety, were left in place to be used as beam-on interlocked detectors.  The three enclosure area interlocked radiation detectors near the doors and fence would always be active, those near the accelerator would only remove beam when personnel were on access in the accelerator area.

10.5 MeV beam was commissioned and many measurements were made at low beam currents (4 to 25 µA average) to determine if Lab G was sufficiently shielded (mainly the Control Room) and how one would shield the accelerator at BRF.  The dose equivalent rates at the RFQ interfaces were quite high.  At the RFQ B & C interface, rates were generally 1 mrem/hr per µA.  It was clear that the accelerator area could not be a continuous occupancy area, even when beam was hitting the tantalum faraday cup, unless a significant amount of localized shielding could be placed around the RFQ interfaces.  Measurements have also shown that a significant amount of shielding is needed for the target vault, if it is to be located at BRF.  The following sections elaborate on these issues.  Section 10.2 describes the initial issues with x-ray radiation and the eventual solution.  Section 10.3 describes the shielding assessment report (GR, 1997)2. The shielding requirements for BRF are based on the LA Regulations (LAC, 1996)4 that state that the dose equivalent rate to the public must be less than 50 mrem/year and less than 2 mrem in any hour. The shielding requirements for Fermilab are based on a maximum dose equivalent rate of 0.25 mrem/hr in generally occupied Controlled Areas (the Lab G Control Room) and less than 5 mrem/hr (and that no one exceeds 100 mrem/year) in minimally occupied Controlled Areas. These requirements are based on the Fermilab Radiological Control Manual (FRCM, 1998)5 which implements 10 CFR 8356.

Subsequent sections describe interlocks used at FNAL, extensive neutron and gamma measurements made at FNAL, and suggestions for BRF shielding based on measurements at FNAL. Many different instruments were used in order to try to separate the neutron and gamma dose equivalent rates as accurately as possible. The shielding needed to reduce the neutron dose equivalent rates was found to be sufficient to also reduce the gamma dose equivalent rates and thus the main thrust was on neutron measurements. The general layout for the accelerator at BRF and the concrete vault design is shown in Figure 10.1. Figure 10.2 shows the layout at Fermilab's Lab G.

Dose Rates Due to X-RAYS From the RF

Indications were that 1/8Ó of lead would be sufficient to shield the x-rays from the RFQs (based on measurements made at SAIC) down to below 2.5 mrem/hr at 1 foot.  Extensive x-ray measurements were made when the 212 MHz RFQ was turned on (GRO, 1997) using a Smart Ion survey meter.  This instrument is 80% to 100% efficient for measuring x-rays with energy down to 10 keV.  As the RFQ conditioned, the radiation levels decreased, and, as expected, the dose equivalent rate depended on the RF duty cycle and power.  After conditioning, dose equivalent rates up to 20 rem/hr were seen on contact with the RFQ.  Three to four layers of lead blankets were needed to reduce the dose equivalent rate to below 2.5 mrem/hr.

With steel shielding next to the RFQ, the dose equivalent rate was found to vary linearly with duty cycle and as RFQ power5.4.  Attenuation of the x-rays in steel and measurements with a high purity germanium detector indicated that the maximum x-ray energy was approximately 90 keV.  Very few x-rays had energies below 50 keV.  The RFQs were going to be encased in steel cans, and thus measurements were made to determine how much steel would be needed to reduce the rate to 2.5 mrem/hr.  (It was not clear at that point that the Louisiana regulations required less than 2 mrem/hr.)  Assuming a 2.3% duty cycle and 120 kW of RF power, it was determined that ~1.3Ó of steel should reduce the dose equivalent rate to ~1 mrem/hr at 1 foot.  This provided a good margin of safety.

The 212 MHz RFQ was the first RFQ encased.  The stainless steel vacuum vessel was machined a final thickness of 1.312 inches to fit the RFQ.  Survey measurements showed localized higher radiation levels at the downstream flange and at the turbo pump.  The rate in these areas at full power (120 kWatts) and duty cycle was projected to be 5 to 10 mrem/hr at one foot. Along the RFQ body, the highest dose rate seen at one foot was projected to be 2.5 mrem/hr at full power and maximum duty cycle.  The 425 MHz RFQs were encased in 1.375Ó of steel, due to constraints with the RFQ structure.  At 100 kW, the highest dose equivalent rate at one foot was seen at the interface between RFQ B and RFQ C.  This rate was 0.6 mrem/hr, which projects to ~1.6 mrem/hr at full power and maximum duty cycle.

All of these measurements indicated that (with the steel cans) the x-ray dose equivalent rate would be less than 2.5 mrem/hr at one foot everywhere.  It was hoped that, with time, this level would decrease due to the conditioning of the RFQs. Recent measurements have been made of the x-ray radiation at 90-100 kW of power and show dose equivalent rates comparable to background around the 425 MHz RFQs.

Summary of the Shielding Assessment Report

This section summarizes the report "Shielding Assessment for the PET RFQ Accelerator at Fermilab" (GR, 1997)2 which discusses the anticipated radiation shielding issues associated with a 10.5 MeV, 300 µAmps 3He PET RFQ accelerator.

Figure 10.2: 	Fermilab PET RFQ Accelerator and Vault Layout.  (Dose equivalent rates are predictions based on FNAL measurements.)

Dose Rates due to Beam Loss in the Accelerator

Radiation levels due to accelerator losses were very difficult to predict.  Cross sections for neutron production on aluminum, molybdenum and tantalum could not be found in published literature for 10 MeV (or less) 3He.  One had to extrapolate from the available data.  Also accelerator losses were not well known.  One had to use beam optics calculation predictions, rather than measurements.  It was clear that as the accelerator was commissioned, many radiation measurements would need to be made to determine what shielding would be needed at BRF.  Reference (SAD, 1997)7 has a more complete discussion of these issues.

Normal Operational Losses

During normal operation, according to beam optics calculations, the majority of the beam loss occurs within the first 20% of each RFQ.  Most of this beam loss should not produce neutron radiation since the beam energy is too low relative to the Coulomb barrier of copper and aluminum, the materials that line the RFQs. (The Coulomb barrier energies for Cu and Al are 12.8 MeV and 7.0 MeV, respectively.)  Most likely, little neutron radiation would occur until the beam energy reached 8 MeV.  Thus losses in RFQ C and on the beam absorber were considered the main issues.

Beam optics calculations estimated that 24% of the beam would be lost in RFQ C.  At 300 µA, this corresponds to 70 µAmps of 8 MeV 3He.  The cross section for neutron production from 8 MeV 3He on copper was found in published literature.  Though the coulomb barrier is 12.8 MeV for Cu, it is not an absolute cut off and some neutron production occurs at 8 MeV.  The dose equivalent rate for copper was estimated to be about 20 mrem/hr (at 300 µA) at a distance of one foot.  For aluminum the dose equivalent rate would most likely be much higher due to its lower coulomb barrier.  An interlocked detector would have to be placed in this area or the entire area would need to be interlocked.

Initially the idea was to use a molybdenum beam absorber just upstream of the target area.  This would allow the radiochemists to enter the vault without stopping the beam.  It was estimated that the dose equivalent rate from neutrons produced by 300 µAmps of 10.5 MeV 3He on molybdenum was 9 rem/hr per millibarn.  The cross section for neutron production on molybdenum with 19 MeV 3He was published as 30 millibarn/sr at  0o.  This suggests that the dose equivalent rate due to beam on the molybdenum beam absorber (at 10.5 MeV) could be quite high, not permitting beam on access by the radiochemists.  The coulomb barrier for tantalum is significantly higher than that of molybdenum.  Thus it was decided that a tantalum beam absorber would be used.

Off - Normal Operational Losses

For accident scenarios there are two failure modes that could cause short term radiation problems.  One scenario is full beam loss in RFQ C, when the power to RFQ C is lost.  The dose equivalent rate due to this failure mode should be about three times that estimated for normal operational losses in RFQ C.  The second scenario is loss of all the beam in the HEBT due to mis-steering.  This is 10.5 MeV beam on a heavy material such as tantalum and thus would be similar to the losses one might expect from beam hitting the tantalum beam stop.  To protect against high radiation levels from these conditions, an interlocked detector would have to be placed in this area or the entire area would need to be interlocked.

Shielding of Accelerator

Due to the extensive amount of concrete shielding already in place at Lab G, additional shielding for the accelerator would most likely not be needed.  It was decided that we would wait and measure the radiation levels due to losses on the accelerator at Fermilab before trying to estimate the amount of shielding that might be needed at BRF.

Dose Rates due to Beam on the Target

Source Terms

Unshielded gamma ray and neutron dose equivalent rates were measured by K. Krohn and J. Link  for various target materials and beam energies with a 1 to 2 µAmps 3He beam.  A summary of the results most relevant to the discussions here are shown in Table 10.1, extrapolated to 300 µA.  It is assumed that the 10.5 MeV 3He beam loses 1 MeV in the target window. The neutron dose equivalent rate at 90 degrees to the beam axis was seen to be about 30% to 50% lower for the C, N2 and O2 targets and 40%  lower for the Be target.  These results were used to estimate the target vault shielding.  C, N2 and O2 targets were anticipated to be used at Fermilab and BRF.  Be was being considered as a target at Fermilab, depending on the anticipated amount of radiation produced and the difficulty with the associated shielding.

| Radiation Type | C | Be | N2 | O2 |
| --- | --- | --- | --- | --- |
| Gamma-ray Dose Rate (rad/hr) | 1.83 | 6.06 | 0.77 | 0.93 |
| Neutron Dose Equivalent Rate (rem/hr) | 10.1 | 103 | 6.54 | 6.33 |

Table 10.1.  Gamma-ray dose rates (rad/hr) and neutron dose equivalent rates (rem/hr) for 300 microamps (electric) of 9.5 MeV 3He2+ ions on various targets at a distance of 10 feet (3.05 m) along the beam axis (axial).

Shielding Requirements

Reference (GR, 1997) discusses both an initial concrete vault and a lead, polyethylene vault.  Only the concrete vaults for Fermilab and BRF will be discussed here.  Calculations were done for a carbon target (considered the "typical" target) and a beryllium target (worst case target), using the source terms in Table 10.1.  The goal was to achieve 2.5 mrem/hr gamma and 2.5 mrem/hr neutron dose equivalent rates at 10 feet from the target.  This was initially thought to be the requirement in order to be able to locate the accelerator on the second floor at BRF.

Based on the estimated concrete thickness needed, the available space at BRF and Fermilab, and the available concrete block sizes, the vaults shown in Figures 10.1 and 10.2 were designed for the BRF and Fermilab sites, respectively.  It was estimated that 42 (50) inches of concrete would be needed at 0 degrees and 38 (46) inches of concrete at 90 degrees for a carbon (beryllium) target.  Figure 10.3 shows the estimated dose equivalent rates around the vault at 300 µAmps (the original goal at BRF), based on the shielding assessment calculations.  The BRF vault is nearly the same design as the FNAL vault, except it is made with much smaller blocks ~8Ó thick.  The BRF vault is 48Ó thick on the north and west sides (1 foot thicker than the FNAL vault).  Both designs have an 18Ó thick roof and south side wall and use the same lead/polyethylene wall around the HEBT.

Figure 10.3: 	Fermilab PET RFQ Accelerator and Vault Layout with Dose Equivalent Rates Based on Shielding Assessment Calculations. (Does not include radiation due to accelerator losses.)

Even in the concrete design, it was decided that a lead and poly wall would be built around the HEBT region to reduce back streaming radiation.  Calculations for the carbon target suggested that about 16 inches of borated polyethylene and 7 inches of lead would be needed. However, because of the space limitation between the end of the HEBT and the entrance to the target, the final design had only 11.25 inches of polyethylene and 5.5 inches of lead.  It was clear that this region might need more shielding at BRF.  Measurements at FNAL would clarify this issue.

The labyrinth door was to be built of polyethylene and lead.  Calculations for the carbon target estimated it should be made of 0.71 inches of borated polyethylene and 0.5 inches of lead.  Due to the difficulty of structurally supporting 0.5 inches of lead, and recognizing that full beam current would not be possible for some time, the entrance door was initially designed to be 0.25 inches of lead and 1 inch of borated polyethylene.  It was to be designed to support an additional 0.25 inches of lead.  Calculations showed that extra shielding would most likely not be needed for the 6 inch wide cable access hole above the vault door.

In determining the amount of necessary shielding for the labyrinth door, the neutrons were assumed to be mostly thermalized before reaching the door.  Actually, this is likely not the case because it is possible, in the present shielding vault design, that some neutrons scatter only once or twice before striking the door.  These neutrons are energetic and would require additional shielding (mainly polyethylene) to reduce the dose rates to more acceptable levels.  The consequences resulting from the present design are discussed later.

Finally, the issue of the radiation back streaming through the accelerator was addressed.  Estimates suggested that this radiation might reach 10 rem/hr at the alpha magnets with the beryllium target or a few rem/hr with the carbon target.  It was decided that an interlocked radiation detector would be placed in this area to monitor these rates.

Interlocks at FNAL

When the high x-ray dose equivalent rates were seen, a chipmunk detector was placed outside the lead blankets (at the highest dose equivalent rate area) and set to trip off the RFQ power at 5 mrem/hr.  When 1 MeV beam was imminent, a second detector was placed at the end of the accelerator and set to trip off the RFQ power at 5 mrem/hr.  No beam induced radiation was seen above background at 1 MeV.  Initial measurements with 5 MeV beam hitting a tantalum beam stop showed neutron dose equivalent rates of 1.5 mrem/hr at an estimated beam current of 2.5 µAmps (2.5 mA out of the ion source).  The FRCM (Fermilab Radiological Control Manual) does not allow beam-on access if the dose equivalent rate is above 20 mrem/hr.  Thus it was determined that the accelerator area would need to be interlocked before 8 or 10.5 MeV beam was allowed since cross sections for neutron production could be considerably higher at these energies.

The interlock system was designed to allow beam-on access.  This was initially a requirement for quick access to the vault for the radiochemists and for the initial tuning of the accelerator.  Due to this need for beam-on access, two interlock systems were used.  The enclosure interlock system (see Figure 10.4, detectors 4, 5 & 6) consists of three chipmunk detectors located near the highest accessible dose rate areas.  These detectors are set to trip (which means they cause the tantalum faraday cup to be inserted, and, if necessary, the ion source gate valve) at dose equivalent rates that correspond to 5 mrem/hr, conservatively, at accessible locations outside the accelerator enclosure.  The beam-on access system consists of three detectors located near the accelerator (see Figure 10.4, detectors 1, 2 & 3) that close the ion source gate valve if the dose equivalent rate exceeds 20 mrem/hr.  The interlock system does not allow beam-on access unless the tantalum faraday cup (or equivalent) is in place.  The beam-on access detectors are active for tripping the ion source gate valve only when someone has entered the enclosure.

When higher current levels were achieved, the dose rates due to losses at the RFQ B/C interface were getting high on the west side of the vault.  The area behind the vault and magnet was fenced off and posted as a radiation area.  This allowed dose rates near the west side fence and detector to exceed 5 mrem/hr.

Figure 10.4: 	Fermilab PET RFQ Accelerator Interlocks and Detectors.

Neutron and Gamma Measurements at FNAL

Target Materials

Aluminum and tantalum targets were used in order to determine how much radiation was due to accelerator losses and how much was due to beam on the target.  Later a copper target was used to try to determine if the loss of copper plating on the RFQs could be the reason the accelerator dose equivalent rates at the RFQ B/C interface appeared to be increasing with time.

Tantalum was naturally a good target as its high coulomb barrier should cause it to produce little radiation when irradiated by the 10.5 MeV 3He beam.  This would allow one to determine losses along the RFQs with little interference from radiation due to beam hitting the target.  When radiochemistry was not occurring, this would be a good beam absorber because it would keep dose rates in the area low.

Aluminum was used because it was easily obtained and published measurements at higher energies (19 MeV) suggest that the cross sections for 3He on carbon and aluminum were approximately equal.  Thus it would give an indication of what the radiation levels might be when the radiochemists started bombarding their target materials.  Indications were that, if anything, the dose equivalent rate from beam hitting aluminum should be higher compared to beam striking carbon. Unfortunately, due to the back streaming radiation from beam hitting the aluminum target, surveys near the HEBT and RFQ C will contain components from losses on the accelerator and on the target.

Survey Instrumentation

Several instruments were used for surveys.  Each had its own response to neutrons and gamma rays.  The snoopy is an Anderson/Braun type moderated BF3 counter, with thermalizing polyethylene and a boron loaded sleeve (to improve energy response), that is only sensitive to neutrons.  It displays the results in mrem/hr with the correct quality factor.  It was estimated, using the Bonner sphere measurements, that the snoopy over-responded by approximately a factor of 2 in the neutron energy range appropriate for the PET RFQ measurements.  Another detector used, the chipmunk, is a tissue equivalent ion chamber, sensitive to both neutrons and gamma rays (down to 100 keV).  It measures in mrem/hr with a quality factor that is preset by the user.  Two other instruments, the HPI 1010 and the Smart Ion, were also used.  The HPI 1010 is a tissue equivalent proportional chamber sensitive to both neutrons and photons and measures in mrad.  Based on previous studies (KR 1990)8, an 80% response for neutrons was assumed and a 95% response for gamma rays.  The Smart Ion is an unsealed air equivalent ion chamber and thus it was assumed to have a similar response to a Cutie Pie (see KR, 1990).  For the Smart Ion a 15% response for neutrons was assumed and a 100% response for gamma rays.

A set of Bonner Spheres was used to determine both the neutron energy spectrum and the quality factor.  The quality factor is the conversion factor from mrad/hr to mrem/hr.  It is one for gamma rays, but energy dependent for neutrons.  The Fermilab Bonner sphere system uses eight 6LiI scintillators for detectors.  One detector is bare while the other 7 are surrounded by polyethylene spheres of varying sizes, up to 12Ó in diameter.

Determination of Neutron and Gamma Dose Equivalent Rates

Unless otherwise specified, the neutron dose equivalent rate was determined from measurements obtained with the snoopy, dividing by a factor of 2 in order to compensate for its over response.  The gamma ray dose equivalent rate is more difficult to determine.  In most cases it was found by subtracting the neutron rate from the chipmunk rate.  This requires one to know the quality factor of the neutrons.  Initially it was assumed to be 10 in order to be conservative.  Later, Bonner sphere measurements showed it to vary from 4 to 9, depending upon where the measurement was taken.  Results quoted here assume the quality factor measured by the Bonner spheres at the most appropriate location (see Tables 10.2 and 10.3, shown later).

In some cases measurements were made with the HPI 1010 and the Smart Ion.  In those cases, two equations with two unknowns (the unknowns being the gamma ray and neutron dose equivalent rates) were solved using the response functions mentioned above.  Here, also, an educated guess was made at the quality factor based on the Bonner sphere measurements.

Dose equivalent rates are usually extrapolated to 150 µA, a beam current considered acceptable for reasonable radiochemistry production rates.  The neutron dose measurements are good to within a factor of 2. This uncertainty should improve when measurements at higher current are performed.  Uncertainties on the gamma ray dose rates are quite large due to the uncertainties in the neutron quality factor.  Values quoted are most likely over estimates.  These uncertainties do not include the day to day differences due to different operating conditions within the accelerator.  These variations were on the order of a factor of 2.

Initial Measurements with 10.5 MeV Beam

Difficulties Encountered

Initial measurements were very hard to quantify.  The beam stability was poor and many variables affected the radiation rates.  Also, consistent methods needed to be developed for determining the power in each RFQ and the beam current.  The RFQs sparked frequently and it was not clear how much of an effect this would have on the survey measurements.  Later it was determined that this had little effect on the survey measurements, as long as they were intermittent.  It was clear that the radiation levels next to RFQ B and C were much higher when the RFQs were not running at optimum power.  Measurements had to be made near 90 to 100 kW, the calculated optimum power.  Also, initial measurements were made at 4 to 20 µAmps and thus linear extrapolations to 100 µAmps introduced some uncertainty.

Linearity vs. Duty Cycle and Current

The dose rate increased to within 20% of linearity when the current was doubled (4 - 8 µAmps and 10 - 20 µA).  Higher current dose equivalent rates were generally less than expected due to a linear extrapolation.  The same was found to be true for dose equivalent rate versus duty cycle.  These measurements were done using the aluminum target and thus do not clearly look at the losses along the 425 MHz RFQ chain.

Initial Neutron and Gamma Dose Equivalent Rates

The highest dose rate areas around the vault with the aluminum target were found to be at the lead/polyethylene wall around the HEBT region and just outside the vault door.  This is what was expected from the shielding assessment calculations.  Surveys were also performed, with the aluminum target, at the cracks in the vault wall, at the cable access hole, and on all sides of the vault.  It was found that the cracks in the wall and the cable access hole were not problem areas.  After the HEBT lead/polyethylene wall and the vault door, behind the vault and the vault roof were the next highest dose rate areas.

Surveys were also performed to see how the neutron dose equivalent rate fell with distance from the vault.  It was found to generally drop off as 1/r on all sides of the vault, if one assumed that the source was the target.  Measurements were not made beneath the vault as this area is inaccessible at Fermilab.  Three locations around the vault did not follow a 1/r or 1/r2 rule, if one assumed the source was the target.  These locations were the vault door, the cable access hole above the vault door, and behind the vault.  The vault door showed that the dose equivalent rate decreased by a factor of 4,  four feet from the vault door.  Measurements made at the cable access hole showed that the dose equivalent rate decreased by a factor of 2.4 in three feet.  Behind the vault the rate dropped by a factor of 6 in 3 feet.

Next the RFQs were surveyed, with beam hitting the tantalum target.  The neutron dose equivalent rates outside the HEBT lead/poly wall and vault door were small, thus confirming that the radiation produced by the beam hitting the tantalum target was significantly less than that from the aluminum target.  Figure 10.5 shows the results of these surveys.  Measurements inside the vault with the tantalum target, and later with the tantalum faraday cup, showed neutron dose equivalent rates of 40 to 80 mrem/hr (extrapolated to 100 µA).  The regulatory requirement for Louisiana is no personnel access for areas with the dose equivalent rate above 100 mrem/hr at one foot, therefore indications are that beam-on access would be possible at these current levels.  A detector would be needed, though, to remove beam if the levels exceeded 100 mrem/hr.  These measurements were made with 10 to 30 µAmps of beam current.  At present, beam on access to the target vault is not allowed or necessary for the current experimental program.

Further Study: Accelerator Losses

Neutrons, Bonner Sphere Measurements

One good set of Bonner sphere measurements was taken next to RFQ C with about 10 µAmps of beam on the tantalum target.  The average neutron energy was found to be 1.36 MeV with the peak between 2 and 3 MeV.  The quality factor was found to be 9.3.  Figure 10.6 shows the neutron spectrum.  The dose equivalent rate determined by this Bonner sphere measurement agreed with the snoopy neutron dose equivalent rate if one assumed an over response of two.  Thus this is what lead to the use of the factor of 2 correction to the snoopy neutron measurements.

Figure 10.5: 	Neutron Dose Equivalent Rates Along the RFQ Chain (5/97). Units in boxes are mrem/hour at one foot for the corresponding beam current.

Figure 10.6: 	Neutron Spectrum next to RFQ C.

Later, Bonner sphere measurements were made with both the aluminum and tantalum target at 6 locations.  Unfortunately it was later discovered that the beam was scraping in the HEBT region and one Bonner sphere was damaged.  Also the measurements with the aluminum target were not completed.  Despite this, the tantalum results were analyzed, correcting for the damaged sphere.  These results are summarized in Table 10.2. The results for the spectrum at RFQ C differ from those measured earlier due to the scraping in the higher energy HEBT region.

Table 10.2:  Bonner Sphere Results with the Tantalum Target

| location | neutrons/cm2 per µcoulomb |
| --- | --- |

mrem/hr

| (150 µA) | Quality Factor |
| --- | --- |

Average Energy

| (MeV) |
| --- |
| outside vault door | 3.3 | 33 | 8.5 | 1.3 |
| inside vault door | 1.26 | 10 | 8.8 | 0.6 |
| HEBT | 4.0 | 36 | 8.5 | 1.1 |
| RFQ C | 13.2 | 205 | 7.4 | 4.0 |
| east side at 13 feet | 2.0 | 19 | 9.4 | 0.6 |
| east side vault wall | 0.7 | 2 | 6.7 | 0.3 |

Neutron dose Equivalent Rates along the RFQs and HEBT

Chipmunk dose equivalent rates per microCoulomb at the B/C interface seemed to have increased with time.  At times significant beam losses had occurred in the HEBT and this chipmunk would see these losses also.  In order to isolate the radiation sources along the 425 MHz RFQ chain, a polyethylene enclosure with one end exposed (doghouse) was made for the snoopy and measurements were taken about every 6Ó along the accelerator back to the MEBT (with the tantalum target in place).  The results of this survey are shown in Figure 10.7. These measurements showed that radiation from the HEBT was insignificant.  They also showed that the dose equivalent rate at the B/C and A/B interfaces had significantly increased since previous measurements (see Figure 10.5). After these measurements were performed, inspection of the RFQ vanes showed some copper plating loss on the RFQ vane tips.

An unshielded snoopy was used to determine the attenuation of the neutron dose equivalent rates with distance from the accelerator.  At 6 feet the attenuation varied greatly due to scattering of the neutrons off the various structures near the RFQ.  Measurements at 12 feet were more consistent and the attenuation was 1/r at worst.

Figure 10.7: 	Neutron Dose Equivalent Rates Along the RFQ Chain (7/97).

Neutron Dose Equivalent Rate Dependence on Power in RFQ C

Snoopy measurements were made at the B/C interface, using the polyethylene doghouse, as the power in RFQ C was varied.  The results are shown in Figure 10.8. The three curves in Figure 10.8 are the losses in RFQ C at the entrance end, center, and exit (downstream) end of the RFQ.  Losses in RFQ C increased as the RFQ power decreased below the optimum region, as suspected earlier.  During these measurements the beam current into RFQ C was not changed.

RFQ B/C Interface Neutron Attenuation in Polyethylene

Sheets of polyethylene were placed in front of the snoopy in the polyethylene doghouse at the B/C interface (tantalum target).  Six inches of polyethylene gave a factor of 10 attenuation.  This same result was obtained by applying polyethylene attenuation curves to the neutron spectrum determined from the Bonner sphere measurements made along RFQ C.

Figure 10.8:	Neutron Dose Equivalent Rate versus Power along RFQ C.

Loss of Copper Plating and the Tungsten Insert

The losses at the B/C and A/B interfaces appeared to be increasing with time.  Initial measurements (5/97-6/97) indicated approximately 1 mrem/hr per microamp of beam.  In July and early August dose equivalent rates were relatively consistently at levels of  4 to 6 mrem/hr per microamp of beam.  This was thought to be due to the loss of copper plating at the interface, thus beam was hitting more aluminum in the upstream end of RFQ C, where most of the beam loss was expected to occur.  More neutron production was expected from aluminum than from copper, due to the lower Coulomb barrier.  Neutron measurements made outside the vault door with an aluminum target and then a copper target indicated that aluminum produces approximately four times more neutrons.  A monitoring detector in the vault gave the same results.

Inspection of RFQ C has shown some flaking of copper from the vane tips.  A tungsten aperture plate was designed to be inserted at the B/C interface.  It was hoped that this plate would intercept the beam halo rather than allowing it to hit the aluminum in RFQ C.  The high coulomb barrier of tungsten, as compared to aluminum, should minimize neutron production due to beam loss.

When the tungsten plate was inserted, radiation surveys were performed.  Measurements were made at 15 to 30 µAmps of beam current.  Measurements of gamma and neutron dose equivalent rates were made with detectors positioned in the Control Room before and after the tungsten aperture plate was installed.  The neutron dose equivalent rate remained the same and the gamma ray dose equivalent rate was a factor of two higher with the tungsten plate.  It should be understood that dose rates can vary by a factor of two from one day to the next due to varying running conditions.

Measurements of separate gamma and neutron dose rates had not been made next to RFQ C since May.  Neutron measurements were made in July.  Comparison of chipmunk dose equivalent rates (the chipmunk next to RFQ C) suggested that the dose equivalent rate was the same or perhaps higher with the tungsten plate.  Before the tungsten plate was inserted, that chipmunk read from 120 to 600 mrem/hr for 100 µA (the lower value was from early July) and, after, the chipmunk read about 350 to 400 mrem/hr for 100 µA.   If either the ratio of gamma to neutron radiation has changed or the energy spectrum of the neutrons have changed considerably, then a direct comparison of the chipmunk rates is not valid.

Neutron and gamma measurements were made, with the tungsten plate in place, using an HPI 1010 and a Smart Ion survey meter in a lead and polyethylene doghouse.  The results agree with the readings on the chipmunk next to RFQ C.  The neutron dose equivalent rate does not appear any different than before the tungsten plate was installed.  The gamma ray dose rate is comparable to that measured in May of 1997 (within a factor of 3).  This agrees with what the direct before and after measurements in the Control Room implied. Beam losses in RFQ C were about a factor of two higher with the tungsten plate, and thus more beam needed to pass into the RFQs in order to obtain the same current at the faraday cup.  This may be why the tungsten plate did not help the neutron radiation problem.

The chipmunk detector next to the B/C interface is logged periodically as is the beam current.  Looking back over these logs for the last few months showed that even in May and June of 1997, fluctuations were seen up to 6 mrem/hr per microamp of beam.  And, more interestingly, recent measurements (8/29/97, 9/2/97 & 9/18/97) at 75 to 100 µAmps of beam showed levels back at 1 mrem/hr per microamp of beam.  To check this, measurements need to be made with the snoopy at the B/C interface at these higher currents.

Gamma Rays

Some measurements were made with a prototype ion detector which was insensitive to neutrons.  This detector was calibrated in a gamma ray energy range similar to what was expected outside the vault.  Assuming 100% response leads to agreement within a factor of 2 of gamma ray results deduced as described previously.  This lends validity to the method of determining gamma and neutron dose equivalent rates from chipmunk and snoopy data.

Measurements were also made, using a 60Co source, to determine the attenuation of gamma rays in polyethylene.  It was found that the dose equivalent rate (DER):

DER = (0.995) 10 -0.06(inches of poly).

Thus 6 inches of polyethylene would attenuate the gamma ray dose equivalent rate by at least a factor of two.

Recent High Current (~100 µA) Measurements with the Tantalum Target

Measurements were made at higher currents at locations near the interlocked enclosure in order to ensure that the interlocked detector trip levels were set appropriately.  Dose equivalent rates outside the enclosure must remain below 5 mrem/hr and dose equivalent rates in the control room should remain below 0.25 mrem/hr.  Surveys showed that the only locations that needed further measurements were at the magnetic enclosure door and in the Control Room.  Chipmunk and snoopy measurements were made with 100 µAmps of beam, inside and outside the magnetic enclosure door, in the Control Room, and in the Radiochemistry area.  These measurements showed that the Control Room and Radiochemistry area dose equivalent rates were about 0.30 mrem/hr (0.15 mrem/hr neutron, 0.15 mrem/hr gamma rays) at 100 µA.  Does equivalent rates at the door were about 0.8 mrem/hr at 100 µA.

Further Study: Beam on the Aluminum Target Measurements

Some measurements were made (aluminum target) placing various widths of polyethylene in front of the snoopy detector and placing the detector at the vault door and the HEBT lead/poly wall.  These measurements showed that 6 inches of polyethylene transmitted 33% of the neutrons at the HEBT.  Four inches of polyethylene at the vault door transmitted 40% of the neutrons.  These measurements were made at low currents (less than 20 µAmps) without a ÒdoghouseÓ.  They need to be redone at higher currents with a doghouse if the accelerator is to be located at BRF.

Bonner sphere measurements were made with the aluminum target, but not completed, in the same locations as shown in Table 10.2.  A modified analysis was used to correct for the missing Bonner sphere data.  These results give one a general idea of what the quality factor and average neutron energy might be at the various locations (see Table 10.3).  Since data from two or more spheres are missing from each measurement, and the beam was known to be scrapping in the HEBT when these measurements were made, they should only be read as an indication of what the real spectrum might be.

Table 10.3:  Bonner Sphere Results with the Aluminum Target

| location | neutrons/cm2 per µcoulomb |
| --- | --- |

mrem/hr

| (150 µA) | Quality Factor |
| --- | --- |

Average Energy

| (MeV) |
| --- |
| outside vault door | 5.3 | 60 | 7.8 | 2.0 |
| inside vault door | 168 | 470 | 4.7 | 2.3 |
| HEBT | 5.3 | 100 | 9.2 | 2.4 |
| RFQ C | 8.5 | 130 | 7.2 | 3.8 |
| east side at 13 feet | 4.1 | 20 | 7.6 | 0.4 |
| east side vault wall | 2.6 | 3 | 3.8 | 0.1 |

Another issue is the back streaming radiation, which appeared minimal at first (16 mrem/hr at the alpha magnets at 300 µA).  Recent (September 1997) chipmunk detector rates at 30 µAmps indicate dose equivalent rates of ~70 mrem/hr at 100 µAmps, back at the alpha magnets.

Conclusions for FNAL

Figure 10.2, shown earlier, gives the estimated gamma and neutron dose equivalent rates at Fermilab.  Values that are circled are calculated from the accelerator loss dose equivalent rates (rates measured using a tantalum target).  Values at the B/C interface assume a worst case of 6 mrem/hr per µAmps at 1 foot, while values in parenthesis are for rates of 1 mrem/hr per µAmps at 1 foot at the B/C interface.  Values in boxes are extrapolated from measurements made with the aluminum target.  Linear current extrapolations are used and 1/r distance extrapolations are used.  Uncertainties are a factor of 2-3 until high current (~ 100µA) measurements are made.

Eight inches of polyethylene (4' by 4' sheets) has been placed next to the RFQ B/C interface to keep the rate below 0.25 mrem/hr in the Control Room.  This has decreased the dose equivalent rate in the Control Room by a factor of 2.  Enough polyethylene has been purchased to build a second 4' by 4' by 6 inch wall.  This wall can be used next to the HEBT on the east side, depending on how high the dose equivalent rates get due to radiochemistry studies.

Updated Shielding Design for BRF

Figure 10.1, shown earlier, gives the expected dose equivalent rates at BRF at 150 µA.  Uncertainties are large until further measurements are made at high currents using the snoopy and chipmunk detectors.  It should be noted that the concrete vault at BRF has an additional foot of concrete on the south and the back walls as compared to the Fermilab vault (this is corrected for in the dose equivalent rates shown in Figure 10.1).

Interlocks would need to be used around the accelerator enclosure in a similar fashion to those at Fermilab.  The ceiling at BRF would also most likely need to be interlocked.  In order to decrease the amount of extra shielding needed, the south room and north ramp (outside the building an interlocked gate would need to be installed at the end of the ramp) would also be interlocked.  Additional shielding for the vault, door and HEBT lead/poly wall may not be needed with such an interlock system.  The main problems appear to be radiation from the B/C and A/B interfaces (due to accelerator beam losses) at the north wall, south wall and ceiling, and possibly the back streaming radiation.  Secondary issues are the dose rates from the door and the HEBT lead/poly wall (due to beam on target).  Indications are that the shielding for the neutrons will be sufficient to stop the gamma rays as well.  The following shielding design assumes one wants to obtain ~1-2 mrem/hr neutrons at locations accessible to the public.

The "worst case" shielding design for the accelerator would consist of polyethylene collars around the B/C and A/B interfaces and fixed and rolling polyethylene walls.  Depending on the results of higher current measurements at these interfaces, either 6 or 8 inch thick polyethylene collars could be machined to fit around both these interfaces.  This would decrease the dose equivalent rate by a factor of 10 (6") or 20 (8").  If the accelerator were moving to BRF, it would be best to make and install these collars at Fermilab.  This would allow measurements to be made to determine if any additional shielding would be needed around the accelerator.  If further shielding is needed a polyethylene wall system could be made relatively easily as shown in Figure 10.9.  This figure shows 6 to 8 inch thick walls in several locations.  With the polyethylene collars it is doubtful that this much additional shielding would be needed.  The rolling walls shown in Figure 10.9 can be used wherever they are necessary.  Whether additional shielding for the vault, vault door, back streaming radiation, or HEBT lead/poly wall would be needed (at BRF) could best be determined after the polyethylene collars were installed at Fermilab.

If the door shielding is found to be a problem, up to 6Ó of polyethylene (or borated polyethylene) could be added to the door before the weight would become an issue.  The hinge and opening mechanism would need to be designed appropriately. To reduce the flux of neutrons which scatter once or twice and exit the door, small amounts of concrete shielding could be stacked strategically within the vault near the target region.  The blocks would need to be placed in a location to reduce any interference with the radiochemistÕs work.   If additional shielding is needed around the lead/poly wall, a polyethylene wall on rollers could be set at an angle off the northeast corner of the vault.  If additional shielding is needed at the MEBT due to back streaming radiation, a rolling polyethylene wall could be placed there also.  If extra shielding is needed on the vault north and south sides, one row of the concrete blocks (or part of) on the north and south sides (inside the cave) could be replaced with 6 or 8" of polyethylene.

Lead shielding does not appear to be needed anywhere (at least for accelerator produced radiation) as the attenuation achieved with the polyethylene should be sufficient.

Summary

The biggest shielding issues with this accelerator are a result of the x rays from the RF and the neutron radiation emitted at the RFQ interfaces due to beam losses.  The x rays were "easily" mitigated with a steel casing on the RFQs.  The B/C losses might be mitigated by using vanes made of copper.  Additional measurements with a copper and aluminum target would need to be made to verify this.

Figures 10.1 and 10.2 show the estimated dose equivalent rates due to accelerator and beam on target radiation for Fermilab and BRF and Figure 10.9 shows a proposed possible solution for the BRF location.  If the accelerator were to move to BRF, additional measurements would need to be made at Fermilab at higher currents with both a tantalum target and aluminum target in order to determine how much of this shielding would be needed and if it were sufficient.  Until the determination to relocate the accelerator is made, further radiation measurements have been put on hold as they are unnecessary for operations at Fermilab.

Figure 10.9: 	Proposed Accelerator Shielding for BRF Layout.

References

1.  (BI, 1994) J. Bida, D. Finley, P. Young, K. Krohn, ÒProposal For A Pilot Program For Development of a 3He RFQ-Based System for Low Cost Production of PET Tracer Isotopes in a Clinical EnvironmentÓ, March 1994.

2.  (GR, 1997) N. Grossman and D. Holslin, ÒAssessment for the PET RFQ Accelerator at FermilabÓ, February 1997.

3.  (GRO, 1997) N. Grossman, K. Graden and F. Krueger, ÒRF, X Rays and Dose Equivalent Rate for the 212 MHz RFQÓ, February 1997.

4.  (LAC, 1996) Louisiana Department of Environmental Quality, Environmental Regulatory Code 33:XV

5.  (FRCM, 1998) Fermilab Radiological Control Manual, January 1998 edition.  This document contains Fermilab's policies for assuring worker safety and protection of the public and the environment from sources of ionizing radiation.  It is part of the Fermilab Environment, Safety, and Health Manual (see FESHM, 1998).

6.  (10 CFR 835) Code of Federal Regulations, Title 10, Part 835, "Occupational Radiation Protection".

7.  (SAD, 1997) ÒSAD Document for PET/RFQ Project at FermilabÓ, February 1997.

8.  (KR, 1990) F. Krueger, ÒDetermining the Fast Neutron Energy Response Characteristics of Fermilab InstrumentationÓ, RP Note 86, June 1990.

11. Magnet Power Supply Systems

System Description

The power supply system for the PET accelerator consists of 22 current- regulated DC power supplies that are used to drive  various magnet loads. Most of the units are commercial supplies. Some came with the project and some were purchased to complete the installation. The power supply circuits and their characteristics are listed in Fig.11.1.

LOAD		SUPPLY TYPE			RATING	REGULATION

Alpha		EMI ESS 80-125-2-10T-0806	80V/125A	0.1%

Alpht		Lambda LLS-50-60			60V/1.4A	1%

MEQ3		“

MEQ1		EMI EMS 10-200-5-D-10T-0806	10V/200A	0.1%

MEQ2		“

HEQ1		EMI EMS 40-50-5-D-10T-0806	40V/50A	0.1%

HEMP1	EMI-EMS 80-60-2-D-10T-0806	80V/60A	0.1%

MEQ4		EMI EMS 15-300-2-D-10T-0806	15V/300A	0.1%

MEQ5		“

Q1TRM	FERMI TRIM SUPPLY		+/- 20V/6A	1%

Q2TRM	“

D3VER	“

D3HOR	“

Q4TRM	“

Q5TRM	“

LES1		EMI BOSS 20/20/1			+/- 20V/20A	1%

LES2		“

HES1		“

HES2		“

SOLND	EMHP 30-600-12211			30V/600A	0.1%

METQ1	EMI EMS 30-20 1D-10/T		30V/20A	1%

METQ2	“

Figure 11.1.    PET Power Supply Ratings

The major engineering effort required was in integrating the power supplies into the PET control system so that they could be controlled and monitored. A variety of protection systems such as ground fault and over temperature detection trips were also designed in. The regulation stability of seven of the supplies was improved through the use of external current transductors and computer feedback loops.

General Approach to Control and Regulation.

In order to minimize the additional circuitry and expense required to integrate the power supplies into a complete system, it was decided to take full advantage of two of the control systems that were being built into PET: the PLC’s (programmable logic controllers) and the  IRM’s ( Internet rack monitors).

The PLC’s were already being used to interlock vacuum, RF power and other systems. Power supply interlocks were added to their list of functions.

The IRM’s house the A/D and D/A capability of the PET control system.  IRM channels and programming are utilized to perform interlock functions requiring analog monitoring. The IRM also performs slow P.I.D. feedback adjustments to enhance the stability of some of the power supply circuits.

Figure 11.2 is a block diagram of the control system for a typical power supply. It shows the interlocks for over current, ground fault and load over temperature as well as the circuit path for enhanced regulation stability.

Figure 11.2.   Typical Power Supply Controls

Enhanced Regulation Stability

In the PET project, seven of the circuits required 0.1% stability to meet their specifications.  Commercial power supplies are generally capable of maintaining 1% current regulation in the presence of normal line, load and temperature variations. The most severe limitation in these supplies is a temperature coefficient of 0.03%/degree C.

In a previous Fermilab project (the LINAC upgrade solenoid supplies), true 0.1% regulation was specified and went out for bids. The end result was specially modified units that had a long delivery time and cost almost twice the price of the standard supplies. For the PET project, it was decided to use the standard supplies and to monitor the load current with an external transductor of adequate stability.  The IRM computer makes small changes in the power supply reference to keep the external transductor signal within tolerance.

The external current monitor chosen was a LEM 205-S. This is a 200 amp Hall device transductor with a temperature stability of 0.002%/degree C, and a price of only $55.  The LEM’s require a power source and precision burden resistors to operate them, but these are also inexpensive items. In the circuits requiring significantly less than 200 amps, multiple turns were wound around the LEM monitoring head.

The IRM reads the LEM output at a repetition rate of 10 Hz. The MADC built into the IRM is a 16 bit device with good enough stability to easily handle the 0.1% regulation task. The IRM processor is set up with standard P.I.D. loop algorithms. For the power supply  loops it makes “integral” corrections, changing the power supply reference by 10% of the measured current error. The reference is produced by a 16 bit D/A output channel. The controls group installed a special 8-channel 16 bit D/A in the IRM to provide the resolution to smoothly make these corrections.

Over Current Trips

The commercial power supplies are not supplied with over current trip circuits. To protect the magnets from excess currents, the IRM system is employed. The load currents are already being monitored for either feedback or display purposes. The controls group has programmed the IRM to also compare the monitored value with a maximum current, and send a trip signal to the PLC if this level is crossed. The PLC latches the trip and turns the power supply OFF.

To guard against an IRM crash and loss of current checking, a ÒheartbeatÓ monitor has been installed.  If the IRM fails to send a 10 Hz pulse to the PLC, the PLC waits several seconds and then turns OFF all supplies. The IRM is programmed to send out its heartbeat directly after it has completed its power supply scan.

Ground Fault Detection

High power loads are protected with  ground fault detector circuits. The approach is to float the power supply output terminals and balance them with respect to ground using two 1k Ohm resistors. (See  Fig. 11.2. ). The summing point of the resistors is held at ground through a 100 Ohm monitoring resistor, and the voltage across the 100 Ohms is zero unless there is some external current going to ground. The summing resistor voltage in monitored by the IRM, which is programmed to trip the power supply if the voltage exceeds a preset level.

The advantage of this type of ground fault detection is that it keeps ground current below a milliamp even if the load has a dead short to ground. This protects both the load and operations personnel. The disadvantage of the approach is that it requires floating the power supply output terminals. Unfortunately, commercial supplies reference their remote signal inputs to one of the output terminals (usually the negative). Since the IRM reference is single ended, isolation amplifiers were added in the reference lines of these power supplies. The IRM monitors the ground fault signals in the same  way that it detects over currents. The integrity of both checks is protected by the heartbeat system.

Over Temperature Protection

The magnet loads are protected from over temperature conditions in a redundant manner. A 70 degree C thermal switch detects the problem and tells the PLC to turn OFF the power supply. As a backup, an 80 degree C switch is placed directly in the power supply hardware OFF circuit . In addition, the water-cooled loads are de-energized if the PLC detects that the pump system is not operational.

Safety

All of the power supplies but one are powered from the same 480 VAC feed. This feed can be LOTO’d at a safety switch, making the supplies safe for maintenance. Alternatively, the supplies may be individually locked out by putting a lock box on their power cords. The Solenoid supply, which is fed from a separate 480 VAC source, has a safety switch at which it may be locked and tagged . Hazardous terminals at the inputs and outputs of the power supplies have been protected .

Alpha Magnet Ramping

The Alpha magnets are constructed with a solid steel core rather than laminations. Due to the nature of the design, there was a concern that a rapid change in current may generate eddy currents sufficiently high to change the residual magnetic field at places in the magnet. To avoid this possibility, an electronic slew-rate-limiter circuit which slowly ramps the power supply reference to a newly entered value was installed. The circuit also ramps the reference to zero before turning OFF the supply in the event of a trip condition. This circuit cannot protect against all situations, such as a power failure, but it prevents inadvertent generation of high eddy currents.

The Alpha Trim Supply

The Alpha magnet system consists of two magnets that run at nearly the same current (approximately 90 Amps). The power supply system consists of a main supply to power both magnets in series, and a 1.4 Amp trim supply which sits piggy-backed across one of the magnets. A diode in series with the trim supply protects it from the main supply current. Some problems were anticipated by stemming from two supplies regulating parts of the same load, but the system functioned smoothly without any buffer impedances or other de-coupling mechanisms.

Spares

Each power supply in the PET accelerator has a spare of equal or greater capacity. One spare supply may be the backup for several different units. Use of a non-identical spare might require some temporary jerry rigging.

Commissioning Issues

The commissioning of the power supply system was relatively smooth, given the number of people who worked hard at getting all the cabling straight, the bits lined up and the algorithms checked out. The major technical problem was an instability in some of the floating supplies that used isolation amplifiers in line with their reference signals. It was discovered that the high frequency common- mode noise of the power supply was picked up and converted into erratic wobble by the isolation amplifiers.  The problem was solved by putting small chokes in the signal and common lines of the cables between the iso-amps and the power supplies.

Summary

The power supply system has run quite smoothly. Regulation stability has been adequate for stable machine operation and  reliability has been good.  A number of ground fault trips have been experienced due to the added noise of the operating accelerator.  These have been mitigated by increasing the trip levels with no compromise in system protection.

12. Mechanical and Vacuum Systems

General Mechanical Performance Issues

Accelerator Footprint /Physical Layout

The PET 3He++ accelerator physical layout is arranged to facilitate aisle access to all components, maximize support equipment packaging density, and minimize cable lead lengths.  To accommodate such requirements, an accelerator support tree is used to locate beamline components in a cantilever fashion, provide a centralized overhead equipment bay location for vacuum support hardware and power supplies, and provide equipment power service and cable tray instrumentation line routing (Figure 12-1).

The general accelerator component alignment criteria dictates that the ion source, RFQs, alpha magnets, and HEBT positional tolerance is maintained to within 0.010" of true position.  Additional requirements included provisions for easily changing solenoid position during beam on conditions to maximize LEBT transmission and the ability to easily change and monitor the location of the MEBT quadrupoles Q1-Q5.  When changing the position of the MEBT quads, dial indicators are used to monitor positional changes in increments as small as 0.001".

To meet alignment requirements, a rigid accelerator support system is necessary.  The accelerator tree is constructed of 6061-T6 Aluminum channel shapes.  The main horizontal channels are of sufficient cross-section to minimize vertical deflection in any single location to less that 0.005" with full accelerator component loading.  Individual beamline component stand legs and stands are fabricated primarily using mild steel box tubing.  The accelerator was constructed by first installing the support tree and overhead equipment bays and performing a survey to within 0.030".  Components were placed on their associated stands starting with the ion source, conducting an optical survey to within 0.010", and working down the beamline.  The support structure is proven to be rigid and functional, and components are easily placed well within alignment tolerance.

The overall accelerator footprint is designed and constructed in the Fermilab Lab G location with a footprint that is compatible with the area prepared at the Shreveport BRF facility.

Ion Source

The original ion source consists of a duoplasmatron ion source, electron trap, ground electrode, current toroid, and an x-y steering magnet mounted in an aluminum  vacuum housing.  The original hardware configuration existed from the previous PET accelerator project.

Efforts during the current phase of the project focus on reducing the longitudinal distance from the ion source plasma electrode to the exit of the housing while maintaining an adequate vacuum conductance path for mounting the internal source related components.

A new stainless steel vacuum housing was designed and constructed to accommodate the more compact longitudinal geometry. The new housing shortens the distance from the ion source plasma electrode to the exit of the housing by slightly more than 3 1/2 inches.  Additionally, the conductance of the vacuum pump connection port is slightly improved to increase the effective pumping speed at the chamber.  The new housing also allows for a compact connection to the LEBT (low energy beam transport) section.

Figure 12-1:  PET Accelerator Beamline Component Layout and Accelerator Tree Support Structure

LEBT

The LEBT section consists of a solenoid magnet, a vacuum beam pipe and diagnostic collectors located at the exit of the beam pipe.  All of these components are newly designed for this project.  The design of the LEBT section is a collaborative effort between the programÕs beam optics experts, FermilabÕs Technical Support Magnet Manufacturing Facility, and the mechanical design team.

The LEBT beam pipe interfaces with the ion source vacuum housing on the upstream end and with the 212.5 MHz RFQ on the downstream end.  Functional requirements include the ability to easily adjust the radial and longitudinal position of the solenoid to facilitate beamline tuning to maximize beam transmission and match to the 212.5 MHz RFQ.  In addition, beam position diagnostics are required at the exit of the beam pipe.

The solenoid magnet is designed with a 5.5 inch ID bore, a 16 inch OD housing, and an overall length of 8.8 inches.  The type 304 stainless steel vacuum beam pipe flanges interface with adjacent components using O-ring seals.  The original vacuum beam pipe allowed for nominal solenoid adjustments of ±1.6 inches longitudinally and 0.06 inches radially.  The exit beam position diagnostics consist of four copper collectors that essentially form a segmented Faraday aperture.

Upon completing fabrication of the solenoid, tests indicated that the magnetic center was displaced from the physical center by as much as 0.25 inches.  This discrepancy prevented proper alignment of the solenoid magnetic center with the beamline axis due to interference with the vacuum beam pipe.  To minimize schedule impact, a decision was made to fabricate an entirely new LEBT beam pipe with a smaller outside diameter.  The new LEBT vacuum beam pipe allows a nominal radial clearance of 0.5 inches.

212.5 MHz and 425 MHz RFQs

The accelerator system has four RFQ structures, a single RFQ operating at 212.5 MHz and three RFQs operating at 425 MHz.  The 212.5 MHz RFQ structure accelerates the singly charge He3+ beam from 22 keV to 1.0 MeV.  It is physically connected at the upstream end to the LEBT beam pipe and to the charge stripper on the downstream end.  The 425 RFQ chain accelerates the doubly charged He3++ beam from 1.0 MeV to 10.54 MeV.  Three separate RFQ cavities, referred to as 425 RFQs A, B, and C, are connected in series.  The 425 RFQ A interfaces with the MEBT (medium energy beam transport) on the upstream end and the 425 RFQ C interfaces with the HEBT (high energy beam transport) on the output end.

The original 212.5 MHz RFQ and two 425 MHz RFQs A and B existed from the 1992 project.  The additional 425 MHz RFQ C was newly designed and constructed for this project.  Each RFQ cavity assembly is made up of the following major components: a vane housing, four vanes, and 2 cavity end walls.  Each of the RFQ structures is enclosed in its own vacuum housing.  A series of separate events led ultimately to the replacement of the entire 212.5 MHz RFQ cavity assembly and the 425 MHz RFQ A and B vanes.

In addition, radiation shielding studies during initial testing indicated that the original vacuum housings provided inadequate radiation shielding during RF operation. The following discussion covers the above issues separately.

Replacement of Vacuum Housings

In December of 1995, 1 MeV test beam efforts were conducted using the original 212.5 MHz RFQ.  Additional off line (i.e., no beam loading) RF testing was performed using the original 425 MHz RFQ A from the 1992 project.  The test results indicated an unacceptable level of x-ray radiation produced by the cavity during operation with RF power levels sufficient to accelerate beam.  The requirement to maintain acceptable radiation levels adjacent to the accelerator for personnel occupancy dictated that some form of shielding would be necessary for all RFQs.

Since a more functional form of shielding is desirable (i.e., as opposed to lead blankets hanging over the accelerator structure), new type 321 stainless steel vacuum housings for all RFQ structures were fabricated incorporating a nominal wall thickness of 1.38" to replace the original aluminum vacuum housings featuring a 3/8" nominal wall thickness.  Subsequent operation of all RFQs indicate that the thick wall vessels provide adequate x-ray shielding during RF operation.  Further discussion of neutron shielding for beam loading conditions are found in the radiation section of this report.

Replacement of 425 RFQ A Vanes

In June of 1996 it was discovered that the vane tips of 425 RFQ A exhibited damage in the form of melted/pitted sections.  Investigation led to the conclusion that the damage most likely occurred during the RF testing performed in December of 1995.  Replacement vanes were procured.

Replacement of 425 RFQ B Vanes

The existing RFQ cavities are designed such that the vanes are separate from the tubular housing and when assembled they form the quadrupole cavity (reference Figure 12-2).  The physical geometry of the 7075-T6 aluminum vanes feature small ears that run along the length of the vane base to form a line contact with the inside diameter of the vane housing achieving an RF contact joint.  Threaded fasteners are used to hold the vanes in place and allow for adjustment of the cavity fields.  The forces created by the adjustment of these fasteners cause the ears of the vane base to act as a cantilever beam, thereby applying the necessary RF joint contact force.

In July of 1996, cracks were discovered in the spring ears of the 425 MHz RFQ B vanes.  During the 1992 project the 425 MHz RFQ A vanes exhibited the same failure mode and were replaced.  Finite element analysis conducted by the 1992 project team indicated that the stress in the vane spring ears was excessive, leading them to redesign the spring ears and replace the 425 MHz RFQ A vanes.  The original 425 MHz RFQ B vanes did not exhibit similar failure at that time and were not replaced.  The current project incorporates the redesign changes made on the 425 RFQ A vane spring ears in the new 425 RFQ B vanes.  Similar procurement specifications were applied in the fabrication of the new 425 MHz RFQ C vanes.

Figure 12-2:  Typical RFQ Cross-Section

Replacement of 212.5 MHz RFQ Vanes

In September of 1996 vacuum leaks were detected in the 212.5 MHz RFQ vane cooling water passages.  Thorough examination of the problem revealed that the cooling passages of the 7075-T6 aluminum vanes had corroded through the nominal wall thickness of 0.085 inch.  Since the procurement cycle to obtain new vanes is several months, a short term solution was required to continue operation and commissioning of the low energy section of the accelerator. The short term fix consisted of pressure impregnation of the individual vanes to seal the leaking water to vacuum passages.  This procedure was performed at Casting Impregnators located in Skokie, IL, and featured a 90 psi impregnation using Locktite RTC anaerobic material.

The pressure impregnated 212.5 MHz RFQ vanes have subsequently  operated successfully for over 1 year, allowing accelerator commissioning to continue during fabrication of the new assembly with only minor schedule impact.  While the repaired 212.5 MHz vane/housing structure is still considered a functional assembly, long term concerns exist regarding the robustness of the corroded water passages.  Considering scheduling and reliability issues, the decision was made to replace the entire 212.5 MHz RFQ vane and housing structure.

A mild redesign of the 212.5 MHz RFQ vane/housing structure was conducted to replace the existing 212.5 MHz RFQ cavity with a new RFQ cavity that fits inside the original RFQs vacuum housing.  Several design improvements are incorporated.

The vane contour is modified from the original RFQ to provide an improved optics match with the entire accelerator system.

The location of the gun-drilled holes which provide for cooling passages within the body of the vanes are slightly relocated to improve manufacturability.

The hardware configuration for fastening the vanes to the vane housing is simplified which results in a more economic design and an improved tuning adjustment.

Water fittings are designed and fabricated which allow for an all-stainless steel RFQ vane to housing cooling circuit connection.  The original RFQ required the use of stainless steel fittings and soft copper tubing in this region, resulting in dissolved copper ions in the water system exacerbating the corrosion of the 7075-T6 vane water passages.

The vane housing cooling passages are redesigned and simplified so that all of the water connections to the vanes could be completed at the vane housing end flange.  The original 212.5 MHz RFQ design incorporated flange port feed throughs in the vacuum housing to deliver water to the vanes.  As an additional benefit, the manufacturability of the housing was improved as compared to the original design.

Prior to final assembly of the new 212.5 MHz vane/housing structure, He leak checks indicated small leaks on two of the four vanes.  The leak rates were found to be on the order of 10-7 atm-cc/sec.  The leaks were traced to water passage plug weld regions used in the fabrication of the vanes.  Since the vanes were copper plated with all general machining and welding complete, the only option outside of fabricating new vanes was to seal the leaks using the Locktite RTC impregnation procedure delineated above.

RFQ Vane Corrosion Considerations

An important point to note is that the 212.5 MHz RFQ vanes were replaced primarily due to corrosion of the water passages leading to a leakage path into the vacuum system.  Prior to fabrication of the new vanes, discussions focused on various configurations of redesigning the 212.5 MHz RFQ vanes whereby different materials less susceptible to corrosion could be used for the body of the vane and other materials with an appropriate modulus of elasticity could be used for the base of the vanes where the spring ears are located.  It was determined that a major redesign effort of the RFQ vanes was not feasible and that replacement vanes of similar construction to the current design would be procured.

The 7075 aluminum alloy used for the RFQ vanes contains copper, magnesium, and zinc.  While this alloy has the ideal structural mechanical properties for the vane design, it unfortunately is not stable in water.  Mixing yellow metal (copper or brass) and aluminum in a cooling system often results in local cell corrosion.  Copper ions that settle onto the aluminum water passage surface act as local cathodes resulting in a plating out of surrounding aluminum.  Pitting develops which increases the surface area and permits formation of localized acidic environments.  The process catalyzes itself.  With copper already present in the 7075 alloy, the corrosion cycle can take place even without other sources of copper in the cooling loop.  There is also evidence of zinc plating out of the alloy in a corrosion pattern known as white rust.

Several options are implemented to address the corrosion problem.  The long term solution includes the application of bonded Teflon to the water passage surfaces in all 16 of the newly fabricated RFQ vanes prior to assembly and operation.  The Teflon provides an electrically neutral barrier to protect the water passage surfaces.  The application of bonded Teflon involves a flow-through chemical process whereby approximately a 0.0001 inch thick layer of Teflon chemically bonds with the internal water passage surface.  Bonded Teflon, as opposed to typical commercial application of Teflon film, is not attacked by solvents such as MEK, and requires machining of the surface for removal.  A water passage test billet fabricated from 7075-T6 with a bonded Teflon passage is installed in the PET accelerator water system to monitor the efficacy of this barrier layer relative to corrosion.  Results indicate that this solution is effective in controlling corrosion of the RFQ vane water passages.

Additional monitoring is achieved by the installation and regular inspection of 1 micron filters in the RFQ water system.  The filter pores are small enough to trap aluminum particles and give a good indication of the amount of corrosion occurring.  Results show a major improvement with the bonded Teflon application but still some loss of aluminum.  It is believed that part of the filtered particulate comes from the 6061-T6 housings.  This alloy is comparatively much more stable in water than 7075-T6.  Since most of the RFQ housings that came with project were previously used and did not have virgin machined water passage surfaces, the decision was made not to Teflon coat the housing passages.  Additional experiments were conducted by mounting wafers consisting of different aluminum alloys in a flow chamber and monitoring weight loss.  The test results yield data on what to expect under various conditions.  Unprotected 7075 aluminum in our system was corroding at an average rate of 30 to 40 mils per year.  Thus a water passage with an 1/8 inch nominal wall thickness would last approximately three years.

The other major part of corrosion control is water chemistry.  A program has been implemented with a local vendor to add corrosion inhibitors and monitor water chemistry .  Sodium silicate is used to lower the corrosion potential of aluminum, tolytriazole to stabilize yellow metal, and carbonates to maintain a slightly basic pH.  Aluminum cooling loops need to be maintained at a pH of 8.5 to 9.  7075-T6 aluminum wafers (not Teflon coated) are mounted in each of the Neslab chillers.  The wafers are weighed before insertion.  The wafers are inspected at regular intervals to indicate how efficiently the water chemistry program protects uncoated aluminum.  It is believed that proper water chemistry coupled with the application of bonded Teflon will protect the aluminum for the duration of the project.

425 RFQ C Vane Housing leak

After installing the new 425 MHz RFQ C in the beamline a leak was discovered in the vane housing at a water passage weld joint.  It is believed that the cause of the leak was somehow related to the plating process, since the housing had been thoroughly leak checked prior to plating.  The housing consists of 6061-T6 aluminum alloy, which produces sound weldments using the Tungsten Inert Gas (TIG) welding process.  Aluminum parts with leak tight weld joints have in the past been noted to fail a leak check after plating.  Although the plating process does involve slight cleaning and etching of the aluminum base metal, it is not very aggressive but is still absolutely necessary.

The leak was isolated to a vacuum weld located at the downstream end face of the vane housing.  This face of the vane housing mates to the cavity end wall where an RF joint is formed (reference Figure 12-3).  This functional requirement complicates the fabrication process because it requires the surface to be machined after welding.  Re-welding this joint was not possible since the RFQ had already been plated, assembled, tuned, and installed into the beamline.  A flat viton gasket was designed and fabricated to fit between a groove machined in the cavity end wall and the face of the vane housing, while still allowing room to accomplish the required RF joint.  The fasteners used to assemble the cavity end wall to the vane housing provide the clamping force for the seal and RF joint.  The 425C RFQ has operated successfully with no deleterious effects as a result of this in-situ repair.

Figure 12-3:  RFQ 425 C Housing End Repair

Copper plating difficulty

During fabrication of all RFQ cavity components the largest difficulty was related to the copper plating, bright acid copper on aluminum base metal.  This plating process involves a cyanide copper strike followed by electroless nickel and finished with 1 to 3 mils of bright acid copper.  The supplier that had originally provided the plating services for the 1992 project team no longer has the size capability for all of the processes involved.  During fabrication of the 425 RFQ A and B vanes this supplier subcontracted out those processes which they could not do in-house.  Due to the control and time sensitivity of the steps involved in the plating process this subcontracting led to recurring adhesion problems.  The plating schedule effectively suffered a several month time delay due to such problems.

A new plating supplier was required for the new 212.5 MHz RFQ components.  The first challenge was to find a supplier that had large enough tanks ( almost 4 feet long) for all steps of the plating process.  An exhaustive search consisting of contacting dozens of suppliers throughout the nation was conducted.  A plating shop located in Chicago was identified.  The high degree of control required by the processes as well as the difficulty associated with these unusually large parts made the task a difficult one.  After several weeks of working with the vendor and providing input to accelerate the learning curve, the 212.5 MHz vanes and housing were plated successfully.

Charge Stripper

The beamline optics design allows a longitudinal space of approximately 11 inches for charge stripper installation.  Considering the adjacent 212.5 MHz RFQ vacuum requirements of 10-6 Torr for acceptable RF operation, stripping efficiency requirements exceeding 70%, and the respective gas load required to achieve acceptable gas molecule cross-section, a pulsed jet design is chosen.  The previous 1992 project used a Lasertechniques piezoelectric valve to control gas flow to a static cell charge stripper.  Analysis and investigation of the previous charge stripper design indicates that a static cell would not allow for optimal stripping efficiency and acceptable pressure in adjacent beamline elements.  In addition, the piezoelectric valve exhibits unacceptable leak rates exceeding of 10-5 atm-cc/sec as well as insufficient throughput to achieve proper gas cross-section for electron stripping.  Several automotive type fuel injectors were bench tested by using a piezoelectric pressure transducer to measure gas throughput and pressure rise time.

Additional efforts focused on refinement of the injector drive circuit.  A Nissan fuel injector P/N 1660-40F00 is found to provide acceptable rise time on the order of 200 µsec as well as exhibiting leak rates less than 10-7 atm-cc/sec.  The injector is found to be compatible with operation in vacuum.

The production charge stripper utilizes a single injector design.  Figure 12-4 shows a cross-section of the physical layout of the charge stripper.  Gas is delivered from the fuel injector at a stagnation pressure of 0.3 MPa to a converging/diverging nozzle featuring a 0.020 inch throat diameter.  The gas is expanded across the beam path to supersonic velocity .  The pressure in the strip region is calculated to be approximately 0.5 Torr over an interaction length of about 0.42 cm to achieve a stripping cross-section of approximately 3E16 molecules/cm2.  The high velocity gas is directed through an exit aperture into a scavenge section of the vacuum housing.  The scavenge section evacuates the gas molecules and segments the pressure from the vessel top (beamline) section, thereby preventing gas molecules from migrating toward the 212.5 MHz RFQ.  The average gas load is on the order of 13 Torr-l/sec, with a peak load of about 150 Torr-l/sec during the 240 µsec pulse width.

Multiple pumps are required to evacuate such a large gas load with the constraint that the assembly must physically fit into the available beamline space.  The scavenge section accommodates two Balzars 1500 l/sec turbomolecular drag pumps. The top portion of the vacuum housing features conductance limits to prevent the migration of stray gas in the scavenge section toward the upstream 212.5 MHz RFQ.  To assist in further evacuating stray gas in the top portion of the housing, two 500 l/s Balzars turbomolecular drag pumps are used.  A more detailed discussion delineating charge stripper and adjacent beamline element vacuum characteristics is found in the vacuum portion of this report.

The charge stripper has exhibited overall performance consistent with design analysis.  The fuel injectors survive in excess of 108 pulses and operate satisfactorily at 360 Hz operation (we have yet to fail a fuel injector due to excessive gas leakage or open circuit of solenoid windings after 1-1/2 year operation).  It is noted that during 360 Hz operation utilizing argon as a stripping gas, the scavenge section 1500 l/s pumps exhibit excessive heating as a result of the rather large 13 Torr-l/sec average gas load and resultant 5 mTorr scavenge pressure.  The stripping gas was changed to nitrogen at the expense of a few percent stripping efficiency.  The nitrogen gas molecule is lighter than the argon molecule and has better heat transfer characteristics, allowing for greater gas throughput than Argon while maintaining acceptable pump temperatures. The switch to nitrogen as a stripping gas is intended to increase the lifetime of the turbo pumps.

Figure 12-4:   Production Charge Stripper Cross-Sectional View

MEBT  Design Considerations

The MEBT section of the accelerator interfaces with the charge stripper at the upstream end and the 425 RFQ A at the downstream end.  This section of the accelerator consists of the many magnets, diagnostic elements and vacuum equipment which are shown in figure 12-5.  The goal of the design team was to integrate all of the necessary diagnostic and pumping elements with the magnet beam pipe structures.  Each magnet beam pipe must be non-magnetic and must not obstruct the beam.  This is complicated by the very large size transition of the beam as it travels from the entrance to the exit of the MEBT.  Additionally, the beam pipes must allow for sufficient adjustment of the magnets during the installation and commissioning stages of the project.

The design takes advantage of the drift space between the first and second alpha magnets to integrate most of the pumping and diagnostic elements into a major piece of the MEBT beamline called the MEBT Diagnostic Box.  The MEBT Diagnostic box utilizes the underside of the top cover and a removable false floor to mount most of the diagnostic elements which allows for bench-top assembly and servicing.  The floor of the box is used to hang the two MEBT vacuum pumps (reference vacuum section).  The large cross-sectional property of the MEBT box allows for a significant vacuum conductance path to facilitate pumping in the region adjacent to the small cross sectional alpha beam pipes.

The nonmagnetic requirement for the alpha beam pipe and wall thickness constraints dictates stainless steel construction.  Precautions were taken to address the magnetic issue before fabrication. However, testing showed that the areas of the welds were indeed found to be slightly magnetic.  This occurs due to the formation of precipitates and grain structure alignment during the resolidification of the molten metal.  A solution heat treating process was performed on the finished welded assemblies which restored the material to an acceptable condition.

Figure 12-5:  MEBT Plan View

HEBT

The HEBT (high energy beam transport) is the interface for targets to the accelerator.  Its design goals included the following:

a) Transport beam to the target with a uniform beam density over a 2 x 10  cm target zone

b) Provide for rapid exchange of targets by users

c) Control radiation in the vault so users could enter this area with beam on

d) Provide users with a means of shaping beam size and density

e) Protect the accelerator components from target implosions.

Figure 12-6 depicts an elevation view of the HEBT, which consists primarily of two parts: a beam transport section and a target diagnostics section.

Figure 12-6:  HEBT Elevation View

The HEBT beam transport design was based on various optics studies prepared by Dr.'s Schulze and Larson. The quad and multipole focusing magnets were inherited from the 1992 phase of the project.  The x-y steering magnet, consisting of pairs of wound flat plates, are similar to the steering magnet used in the MEBT.  A Pearson current toroid is located at the HEBT beamline focal point to monitor current into the target region.  An aperture plate is placed just upstream of the toroid to protect it from incident beam.  A debris baffle to deflect particulate in the event of a window failure is located downstream of the toroid.  The large 6 way cross in the center of the HEBT beamline provides a platform for the vacuum pump, a lodging area for target debris, and access for cleanout.

The target diagnostic area includes a pair of horizontal collimators, a pair of vertical collimators, an electron suppresser shield, the Faraday cup, an isolation gate valve, a spool piece with a target roughing pump port, an isolation flange with a target electron suppresser shield mounted in it, and an NW160 vacuum interface for targets.  The collimators are mounted on stepper motor driven vacuum feed throughs.  They are electrically isolated, biased, and water cooled.  The Faraday cup is pneumatically driven.  It is also electrically  isolated, biased, and water cooled.

The collimator and Faraday cup incident beam surfaces are comprised of tantalum.  A high Z material is selected to control neutron radiation in the vault.  These devices have copper water cooling jackets on the backside.  Attaching copper to tantalum was a significant design effort.

Solid tantalum plates forming the Faraday cup beam surface are furnace brazed to a copper back plate using a platinum silver foil at a braze temperature of about 1200 C.  Operational experience indicates that this design appears to function well.

The collimators consist of a .012 inch thick tantalum layer explosion bonded to an 1/8 inch copper back plate.  The original fabrication scheme called for furnace brazing the explosion bonded material to a copper back plate.  Due to differential rates of thermal expansion, the strips curled (i.e., acting like a bimetallic strip) and the braze joint failed.  This approach could probably be made to work with a lengthy test effort and more elaborate clamping fixtures.  However, due to schedule constraints, soldering the copper backed tantalum to the cooling plates with a 320 C silver solder foil in an inert gas chamber was selected.  While this approach successfully joined the explosion bonded material to the copper cooling plates, it leaves the collimators vulnerable to damage if they overheat.  One solder joint failure has already occurred, resulting in a water leak into the vacuum system.

Enough experience with the HEBT operation exists to evaluate its performance in terms of the design goals.

a) Transport uniform beam to the target:  The optics studies using TURTLE and TRACE 3D do indeed correctly predict beam behavior in the HEBT.  The beamline and internal aperture plates and baffles also successfully fit the beam path.  The performance spec projecting +/- 25% beam uniformity has not yet been met.  Beam uniformity to this degree appears only possible if we throw away 40 to 50% of the beam.  The HEBT quad and multipole do not appear to be up to this performance level.  Our best efforts to date would allow for about 50 µAmps of actual +/- 25% uniform beam, or about 80 µAmps of +/- 40% uniformity.  Ongoing studies continue to address the beam uniformity specification.

b) Rapid target exchange by users:  The mechanical interface seems to be working well.  The radiochemists can install their targets quickly and commence pump down with a roughing pump switch in the vault.  Difficulties have arisen with outgassing from the targets.  The fast valve system requires a local pressure less than the high 10-5 Torr range.  Outgassing from the targets can generate transients as high as the 10-2 Torr range.  This effect has caused a number of complications in getting the HEBT vacuum under control quickly after a target exchange.  One solution implemented is the addition of a cold trap in series with the target roughing pump to increase pumping speeds below 10-3 Torr before opening the target isolation gate valve.  Also under consideration is the ability to maintain the radiochemistry targets and foils under vacuum prior to use to minimize outgassing and assist in controlling the high HEBT pressures noted during initial radiochemistry.

c) Control radiation in the vault to permit beam on access:  Considerable design effort went in to making sure the beam entering the HEBT would strike only the tantalum surfaces on the collimators or Faraday cup.  Off axis beam would be intercepted outside the vault.  This effort has been successful.  The choice of tantalum greatly assists in meeting such requirements.  While radiation data in the vault are incomplete, it appears that one may expect 40 to 60 mrem/hr with the Faraday cup intercepting 100 µAmps of beam.  Such radiation levels are within the radiochemist's realm of experience.

The Faraday cup operates as designed.  One failure was noted when water cooling was left off briefly while beam was incident on the Faraday cup surface.  Upon restarting water flow, an initial surge of pressure in the HEBT was noted.  The leak was traced to a Swagelock fitting and quickly repaired.

Ironically, the levels of radiation outside the vault (due primarily to neutron production during beam loading conditions in the 425 MHz RFQs) are typically higher than those found in the vault.  The original design goal of vault access during beam on conditions may no longer be applicable due to the high levels of radiation adjacent to the 425 MHz B and C RFQs.

d) Provide users control over beam size and density:  The collimators have proven successful at shaping beam assuming the incident power levels are maintained at reasonably low levels.  At higher power levels (e.g., more than 100 watts or so per blade) the collimator overheats.  This leads to major failure in the form of a failed solder joint and subsequent water leaks into the vacuum system.

The collimator system is packaged in an extremely small space, thereby restricting the use of more sizable cooling lines, fittings, and water channels.  The radiochemistry requirements called for keeping the collimators as close as possible to the target.  Additional design options become available if more space is provided for the collimators.  The system would become more reliable and more easily serviced if the collimators could be located in short, rectangular beam tubes with bellows to isolate water and electrical feed throughs from the vacuum system.

The current method of scanning to measure beam density patterns involves moving the collimators across the beam in a pixel by pixel pattern.  This technique has worked but is limited to lower power beams to avoid overheating.  Due to space limitations, the collimators are mounted with a single bearing at each end.  The resulting mechanical play in the system limits the spatial resolution.  Wobble in the blades results in at least +/- .5 mm variation.  While this is not a major problem, it would be desirable to improve the resolution.

The software designed for this system and the diagnostic electronics have operated quite well.  Some jitter exists in the position readback requiring the software to iterate to position the collimators at the correct location.  Again, while not a major problem, it would be desirable to improve the resolution.

e) Protect the accelerator from target window failure:  The fast valve system is designed to isolate the accelerator (in particular the RFQs) in the event of target failure.  Current operation calls for disarming the fast valve trigger system due to high outgassing rates from radiochemistry targets.  The fast valve system currently installed in the HEBT uses a cold cathode vacuum sensor that is limited to pressures in the 10-5 Torr range or lower.  As a result of the large radiochemistry target outgassing loads, pressures in the 10-3 Torr regime have been noted.  The end result is that disarming the fast valve defeats the protection the system provides to the RFQs.  A new fast valve sensor system is on order that will tolerate pressures as high as 10-2 Torr without tripping.  The new desensitized system should be installed prior to the next radiochemistry session.  A request by the radiochemists to allow for operation of the fast valve with some sort of "knob" control over sensitivity is under investigation.

Additional measures are implemented to prevent target debris from migrating into the RFQ.  Prior HEBT bench tests indicate that if turbulence could be created in the flow pattern as debris moved downstream after a window rupture, debris would move off axis.  The HEBT beamline transitions rapidly at several points from small to large volumes.

Also implemented are strategically placed baffles and apertures.  This system has worked well to prevent migration of fractured window particulate into the RFQ cavities.  Roughly 75% of the debris settles out in the target diagnostics chamber, with the remaining material stopped by upstream baffles or settling out in the HEBT cross.  Clean out apertures in the HEBT beamline also have proven to provide an adequate means for clean up of window debris.  Clean up techniques are improving as more operational experience is gained.

In summary, HEBT performance is mixed.  Radiation control and debris control have largely been successful.  However, specifications for beam uniformity on target have yet to be met and work is ongoing to improve the collimator system.

Vacuum System Performance Issues

General Layout

The vacuum system design is driven by four main requirements:

a) maintain acceptable pressure to minimize sparking in the RFQ cavities during operation

b)provide adequate gas cross-section to strip electrons from He3+ to form He3++ in the charge strip region

c) control gas flow in the ion source and evacuating excess He3 molecules to prevent excessive LEBT/212.5 MHz RFQ pressure

d) ensure the vacuum system operates reliably to maintain clean RF surfaces with minimal oil back streaming

The requirements for items (a) through (c) are addressed by analyzing gas loads in the system, providing adequate pumping to maintain acceptable pressures and evacuate gas molecules efficiently, and providing a thorough mechanical cleaning prior to assembly.  Item (d) is addressed by utilizing an industrial type PLC controller to monitor pressure and control isolation valves during pump down cycles, normal running operation and fault conditions, and vent cycles.

The lowest pressure requirement is found in the RFQs, where it is desirable to maintain pressures below about 2x10-6 Torr.  With such requirements, an unbaked system primarily utilizing O-ring seals for ease of assembly and maintenance is acceptable.  Turbomolecular pumps are selected for this pressure regime since they evacuate larger gas loads from the system efficiently (as opposed to gas capture pumps such as cryopumps which may require frequent regeneration) and allow for clean operation with little risk of oil back streaming into the system (e.g., as compared to diffusion pumps).  Several Balzars horizontal turbomolecular pumps were inherited from the previous phase of the project and are used in the 425 MHz RFQ cavities, ion source, topside of the 212.5 MHz RFQ, and a portion of the MEBT.  New Balzars turbomolecular drag pumps were purchased for the lower pumping port on the 212.5 MHz RFQ, charge stripper, MEBT, and HEBT.  The drag style pumps are selected for their greatly reduced foreline requirements as compared to conventional style turbos.  This results in a cost and space savings, allowing the purchase of smaller throughput roughing pumps to maintain foreline pressures on the order of 1 Torr for drag style pumps as compared to the 50 mTorr requirements of conventional style turbos.

Since the accelerator space for packaging support instrumentation (such as vacuum gauge controllers) is limited, Balzars PKR 250 Full Range Gauges are selected.  These gauges feature a Pirani gauge coupled with a cold cathode gauge.  All gauge electronics are packaged in the gauge head.  These gauges indicate pressure from 1000 mbar down to 5x10-9 mbar.  They read back a linear voltage signal vs. log pressure over the noted range, and are easily interfaced with the PLC.

The PLC minimizes roughing pump back streaming by monitoring beamline pressures and closing foreline valves in the event of pump or pressure alarms.  The hardware is configured for normally closed operation to ensure closing valves in the event of power outages.  The accelerator has been subjected to spurious site-wide power outages during operation and the vacuum system has exhibited safe shutdown and restart in all cases.

A general schematic of the vacuum system is found in Figure 12-7.

Comparison of Measured Pressures with Design/Analysis Pressures

Since the largest accelerator gas load of 13 Torr-l/sec in the charge stripper occurs  adjacent to the 212.5 MHz RFQ, efforts focused on modeling this area and specifying appropriate pumping capacity and conductance limits to meet the requirements of stripping cross-section and acceptable RFQ operational pressures.

To simplify such calculations, the charge stripper and adjacent beamline elements were modeled using analogous systems and the commercially available finite element code ANSYS¨.  For most vacuum systems in molecular flow the following equation applies:

q=Sp + V dp/dt   	where  q= gas source, Torr-l/sec

S= effective pump speed, l/sec

p= pressure, Torr

V= system volume liters

Figure 12-7:  PET Accelerator Vacuum Schematic

Gas flow in the molecular flow regime between two points at steady state is given as:

q=C(p2 - p1)

where  C= conductance, l/sec.  A steady state one-dimensional thermal conduction network satisfying Fourier's law of Q=- (kA) dT/dx where Q is heat, k is thermal conductivity, A is cross-sectional area, T is temperature, and x is linear path length (L), is as follows :

A thermal nodal network such as depicted above is easily modeled using finite element methods.  An analogous molecular flow vacuum system may be similarly modeled using the following relations:

Thermal Network				Analogous Gas flow Network

Q=ÆT/Rt					q=CÆp

Q (heat flow)					q (gas throughput)

Æ T (temperature)				Æ p (pressure)

Thermal Resistance (L/kA)			1/C (set C=k;  L,A=1)

Pumps are effectively modeled by setting the element value of conductance equal to the pump speed and the terminating node boundary condition temperature equal to 0.  The system has been modeled for both a prototype charge stripper used in the 1 MeV test beam and the production charge stripper.  The theoretical and measured values at 4 locations (212.5 MHz RFQ, charge stripper scavenge, charge stripper top sections, and MEBT entrance) are presented as follows in Figure 12-8, where an enlarged view of the gas jet nozzle and stripping region are depicted.  The numbered points in Figure 12-8 represent node numbers used in the ANSYS¨ model.  Note that the 1 MeV tests were conducted at a rep rate of 60 Hz.  Pressures at similar points in the system resulting from 360 Hz operation of the production charge stripper are found in Table 12-9.

Table 12-9 lists the design pressure goal in various portions of the accelerator as well as the associated gas loads from both surface outgassing and point gas loads introduced into the vacuum enclosure.  The nominal operational pressure values are typical ranges and are dependent upon accelerator rep rate (higher pressures are associated with 360 Hz operation) and source and charge stripper gas loading conditions.

Examination of Table 12-9 indicates that the majority of gas load results from charge stripper operation at 360 Hz rep rate (total gas into system is 13 Torr-l/sec average, 150 T-l/s peak).  Of the 13 Torr-l/sec that enters the charge stripper, over 95% of the gas is directed and removed by the scavenge section of the cell.  The nominal operational pressures are within the general bounds of design/analysis values.  The 360 Hz operational pressures slightly exceed design goals (i.e., ion source and charge stripper top section) but have not proven to be detrimental to accelerator operations.

Review of Vacuum System Problems

The only examples of hardware failure relative to vacuum have been associated with the full range gauges and the HEBT turbomolecular pump.  An additional problem arose in the 425 MHz RFQ coupling loop vacuum seal when first commissioning the accelerator at 360 Hz rep rate.

Five examples of gauge failure have occurred:  one associated with the HEBT as a result of radiochemistry window failure leading to gauge contamination from Havar window debris, two on the 425 MHz A RFQ, and two as a result of operating in the higher pressure region of the charge stripper.  In all cases, the remedy was a simple field cleaning of the cold cathode portion of the gauge (a 30 minute operation) and returning the gauge to service.  Gauge replacement in the event of a window failure may prove to be a standard operational condition.  In such instances, a spare gauge may be installed at the expense of approximately 5 minutes time.  The gauge associated with the window failure could then be cleaned off line.

Figure 12-8:  Enlarged View of Charge Stripper Interaction Region and Theoretical vs. Measured Pressure

Table 12-9:  Comparison of Design vs. Operational Pressure

Accelerator Location

Design Pressure

(Torr)

Nominal Operational Pressure

(Torr)

Gas Loading

| (Torr-l/sec) |
| --- |
| Ion Source/LEBT | 1x10-6 | 1x10-6 to 5x10-6 | 2.5x10-2 |
| 212.5 MHz RFQ | < 2x10-6 | 7x10-7 to 1x10-6 | 6.55x10-4 |
| Charge Stripper Scavenge | 5.5x 10-3 (max.) | 3x10-3 to 5.5x10-3 | 12.9 |
| Charge Stripper Top | 1x10-5 | 5x10-5 to 1x10-4 | 0.065 |
| MEBT | 1x10-4 (max.) | 2x10-5 max. | 2.88x10-3 |
| 425 RFQs | < 2x10-6 | 7x10-7 to 1x10-6 | 4.76x10-5 |
| HEBT | 10-5(max.) - 10-6 | 3x10-6 (No gas loading conditions from radiochemistry targets) | 2.63x10-5 |

The HEBT turbomolecular pump failure occurred most likely as a result of contact with fractured Havar foil window chards.  The pump is topside mounted and is protected with a fine splinter shield and a gate valve that closes in the event of fault conditions.  This may prove to be inadequate protection in the event of window failure.  More operational experience is required to confirm or deny this issue.  A possible solution to recurring turbomolecular pump failure in the HEBT would be to use a small cryo pump as an alternative to the turbo pump.  An additional benefit to installing a cryo pump to replace the turbo is that a larger pump could be selected to control the higher HEBT pressures associated with real radiochemistry targets.

The original RF coupling loops which provide input power to each of the RFQs were designed by the 1992 project team.  They utilize a disc-like rexolite window and viton o-rings to provide the vacuum isolation.  The original windows seal on the center conductor of the loop using a piston seal design with the o-ring groove machined in the window.  The window seals the outer conductor utilizing a crush type seal.  Operation using the original drive loops was satisfactory at the lower duty cycles (e.g., 120 Hz or less) run during the early commissioning phases of this project.  However, once the RFQs were operated at 360 Hz vacuum leak failures were occurring at the inner conductor seal.  Modeling showed that the RF power deposited in the viton o-ring was significant enough to cause the seal to fail thermally.  Alternate seal material with lower loss tangent properties such as silicone were investigated for an immediate solution.  Analysis indicates that the dominant factor in the power deposited in the o-rings is the location of the seal.  Modeling indicates that by transferring the seal gland from the rexolite window to the inner conductor, the RF power deposited in the seal is greatly reduced.  Figure 12-10 shows the original design and the new coupling loop configuration.  New center conductors and rexolite windows were fabricated and installed.  Operations at 360 Hz have been conducted for months with no o-ring failures or evidence of excessive heating.

Figure 12-10:  RF Coupling Loop Redesign

13.  Pet Water Systems

Introduction

The cooling of the PET accelerator components is primarily accomplished with a water system composed of three major components:

1)	Low Conductivity Water (LCW) at 90 F provided by the LCW skid.

2)	Clean filtered water at 25 C provided by individual NESLAB portable chillers.

3)	Glycol-water mixture at 45 F provided by chilled water skid and air-cooled chiller.

Figure 13.1 Basic layout of the various systems with respect to the accelerator.

Figure 13.2 Schematic of the LCW and chilled water systems.

Figure 13.3 Water system specifications

All three of the components are closed loop systems with plate heat exchangers supplying the interface where the heat transfer occurs.  The LCW is used by the ion source, solenoid, alpha magnets, water cooled quads (Q1, Q2, Q4, Q5), HEBT magnets and diagnostics, and RF power amplifiers.  Four individual NESLAB portable chiller units supply cooling to each of the RFQs.  The chilled water is a 50/50 glycol-water closed loop system used by the LCW and NESLAB systems to remove the heat to an outdoor air-cooled chiller.  Figure 13.3 shows the heat load on the cooling system from the accelerator components.

Each of these components will be further described in the following sections.

LCW Skid

The LCW skid provides cooling water to the accelerator systems mentioned above.  Components are mounted to a rigid frame such that a minimum amount of space is occupied and the skid can be relocated via a fork lift truck when necessary.

A  20 hp pump is used to pump approximately 60 gallons per minute (gpm) at a supply pressure of 110 pound per square inch (psi) and a return pressure of 10 psi.  Flow is measured with a paddle wheel type flow meter on the return side of the piping system.  Pressure gages, thermocouples, and resistivity probes are installed at key locations throughout the system to monitor the performance of the system.

The conductivity is maintained at 5 Mohm-cm.  This is accomplished via a normally closed solenoid valve on a polishing loop with a portable deionizer bottle and filter.  When the conductivity of the water leaving the LCW skid reaches a level below 5 megaohm-cm, the solenoid valve opens and allows approximately 5 gpm of the system to flow through the polishing loop.  The valve closes once the conductivity reaches approximately 5.25 megaohm-cm.  A second conductivity probe is installed in the polishing loop to periodically check the condition of the deionizer bottle.  The conductivity meter has the capability to switch readings from one probe to another.

The temperature of the supply water is maintained by use of a three way valve with an electric actuator.  A temperature controller monitors a thermocouple readback at the supply header leaving the skid.  The three way valve is proportionally adjusted to direct flow either through or to by-pass the heat exchanger based on this temperature.  The desired temperature is set at 90 F on the controller.

An eighty gallon expansion tank is situated on the low pressure side of the pump to provide a constant suction head to the pump, allow for thermal expansion of the water, and act as a reserve supply of water in case of leaks.  A level indicator is mounted on the side of the tank with switches.  One switch is used for high level indication and one is used for low level indication.  These two switches are used in the interlock system.  An intermediate switch is used to activate an audible alarm if the level of the tank falls below the set level.  Interlocks are not affected by this intermediate switch.

RFQ Water System

Individual NESLAB portable chillers are used to cool the RFQs.  Approximately 4 gpm is supplied at a 60 psi supply pressure.  Individual flows for the vanes and housing of each RFQ are monitored via rotameter type flow meters.  A throttle valve is available to adjust the flows.

Distilled water is initially used and strainers along with string wound filters keep the circulating water clean. The temperature of the supply water is set to 25 C via the control panel on the front of the chiller units.

Chilled Water System

The chilled water system provides the cooling water for both the LCW skid and the four NESLAB units.  A 50/50 glycol-water mixture is used to prevent freezing in the pipes running to the outdoor chiller.  All components are mounted to a rigid frame separate from the LCW skid.

A 7.5 hp pump is used to pump approximately 100 gpm at a supply pressure of 60 psi and with a return pressure of 5 psi.  Flow is measured with a paddle wheel type flow meter on the discharge side of the pump.  Pressure gauges and thermocouples are installed at key locations throughout the system.

After the water/glycol is pumped to the LCW skid and to the NESLAB chillers for heat removal via their heat exchangers, it is routed to an outdoor air-cooled chiller.  This chiller is capable of handling 45 tons of refrigeration.  The controllers within the outdoor chiller maintain the water at approximately 55 F.

An eighty gallon expansion tank is situated on the low pressure side of the pump and provides the same function and interlock capability as the LCW system described earlier.

Water System Protection Interlocks

Shuts down LCW skid:

LCW flow too high or low  -  major leak may have occurred

Chilled water flow too low  -  insufficient cooling will be available

LCW supply temperature too high  -  problems with chilled water or control system

LCW expansion tank level too low  -  leaks in system

LCW expansion tank level too high  -  overfill of system

Shuts down Chiller skid

Chilled water flow too high or low -  major leak may have occurred

Chilled water temperature too high -  problems with air cooled chiller or control system

Chilled water expansion tank level too low  -  leaks in system

Chilled water expansion tank too high  -  overfill of system

Performance Characteristics and Concerns

The PET water system has performed fairly well once a few early operational problems were fixed.  It is not expected to have any future problems except for the usual maintenance issues concerning components that simply wear out.  The problems encountered and the fixes incorporated to date are as follows:

Problem:  Temperature controller not regulating the temperature of the LCW correctly.  This would cause the temperature of the water to rise beyond the high level trip point for the interlocks and the system would shut down.  The auto tune feature of the controller was not setting the parameters correctly and when the accelerator was operational, the controller did not respond fast enough to cool the water sufficiently.

Solution:  Parameters for controller were set manually.

Problem:  Chilled water flow meter broke.  This was probably due to a defective shaft on the paddle wheel.  The flow meter had been in use for approximately 6 months.  The flow meter is also positioned at the discharge of the pump where considerable turbulence is expected.  The original design had the flow meter situated on the return side, but due to space limitations, the paddle sensor was installed on the discharge side.

Solution:   Flow meter was replaced with spare.  Relocation of flow meter will be considered if another failure occurs in near future.

Problem:  NESLAB portable chillersÕ pump shafts wore out and little or no flow was experienced.  Three of the units in operation were part of the original SDIO project and had a considerable number of hours of operation. This problem was due to typical wear and tear on the units.

Solution:  Chillers were refurbished with new pumps, motors, and shafts.

14. Control System Hardware

Overview

The control system for the PET project consists of a networked group of Internet Rack Monitors (IRMs), connected to an Ethernet network.  Consoles attached to the network can request data and make settings to parameters that are read and controlled by the IRMs. Because the PET accelerator was  intended to be relocated to Shreveport, Louisiana, the control system does not rely on the traditional Fermilab ACNET system.  Software in the IRM causes it to read input data, maintain a data base of current values, return data requested by remote requesters via the network, monitor the analog and digital input data so as to alarm on out-of-tolerance analog values and digital data found to be in the wrong state.  Messages are issued on the network to report alarm conditions.  Because IRMs are Internet nodes, it is possible to access them from anywhere on Internet.

Internet Rack Monitors

The IRM is a chassis that serves as a small stand-alone control system. Each IRM contains a Motorola MVME-162 computer card and the interface for 64 analog input channels, 8 bytes of digital I/O, 8 analog output channels.  The I/O capability may be expanded by adding IndustryPack Modules and VMEbus interface cards. A complete description of IRMs is given in www-linac.fnal.gov/irm/.   IRMs for this project were purchased from Bi-Ra Corp. of Albuquerque, NM.

Nine IRMs are used for the PET project; one for each of the four RF systems and one IRM each for power supplies, the ion source, vacuum/PLC, Low Level RF, and Target Diagnostics.  One VMEbus crate containing the same MVME-162 CPU running the same software, controls the accelerator Repetition Rate Generator, the Tevatron-style event clock generator,  and several delay timers.

IRM Software system

Software in the PET IRMs is the same as that described in www-linac.fnal.gov/irm/.   For the PET project, Local Applications were added to communicate with PLCs supplied by PLC-Direct , and to operate PID control loops.

Network

All front end computers of the PET control system are connected to an Ethernet network.  Locally, each node connects to a high speed switch that in turn connects via fiber optic cable to an Ethernet switch in the Cross Gallery.  This arrangement provides connectivity to the PET control system from Internet.

Consoles and Applications

A variety of operator consoles are used to operate the PET accelerator.   These include Macintoshes, PCs, and Sun workstations.  Application programs written for PET are described in the control software chapter of this PET Report.

Goals and Performance

The goal of the control system was to provide a system that assists the operators in commissioning and operating the PET facility.  We believe the goal has been met. The system outlined here, combined with the control system application software described elsewhere, has been in daily use and has operated reliably for the past several months.  This is partly due to the fact that front end hardware and software is the same as that used in other parts of the Lab such as the Linac, DZero detector, and the Booster high level RF, and the A0 Photoinjector.

15. Control Software

Software Development Issues

The control software for the 10.5 MeV PET isotope accelerator must facilitate the following aspects of operating the machine:

¥ The reliable operation of the system within equipment specifications,

¥ The day-to-day operation of the machine by the SAIC operations personnel and

¥ The day-to-day experiments conducted by experimenters.

To accomplish these goals, software meeting the unique needs of this machine has been written or adapted at all levels of the control system.  Imbedded systems software to ensure that equipment operates within its specifications,  user-level application software to automate various operating procedures,  display software to tune, observe and diagnose the operation of the machine, software to continually collect data , and alarms both for archiving and for diagnostics are part of the package.  Finally, a World Wide Web interface to the documentation and selected machine data has been constructed.

Minimizing the amount of newly developed software was an important consideration in the selection of a control system.  Use of off-the-shelf hardware and software was essential to provide a serviceable control system within time and budget constraints.  To this end the control system is based upon commercially available hardware and off-the-shelf software components.  Newly developed software is written using efficient high level programming tools including TCL/TK and LabVIEW.

The commercial control system hardware consists of nine distributed Internet Rack Monitors (IRM) from Bi-Ra Systems, two Programmable Logic Controllers (PLC) from PLC Direct, a SPARC-5 workstation from Sun Microsystems and a Macintosh desktop computer from Apple Computer.  The IRMs provide robust real-time analog and digital data acquisition and local control system functionality at the equipment level.  All controls information is gathered through queries of the IRMs.  The PLCs are slaved to IRMs and mimic conventional hard-wired interlock logic for operating vacuum, water, DC power and conventional interlock systems.  The Sun workstation supports high level non real-time control system functions and the Macintosh provides the primary control console for the machine.  The control system hardware architecture is described in detail in the Control System Hardware chapter 14.

The off-the-shelf control system software consists of programs for the IRM, Sun and Macintosh computers that was previously developed for the Fermilab Linac control system. The Linac software provides a fully operational data acquisition and low level control system.  Thus subsystem development and commissioning is supported essentially from the moment the control system hardware is available. The Linac control system software is described in the World Wide Web based documentation located at http://www-linac.fnal.gov/linac_controls/software/software.html

Software for the control system is generally classified as "application" or as "embedded" level code.  Application software runs on the Sun and Apple computers and adds high level functionality to the basic IRM based system.  Embedded software runs in the IRMs to extend their low level real-time control capabilities or to meet special machine requirements.  Newly developed application and embedded software is described in the sections below; the PLC ladder logic software is described in the Interlocks chapter 9.

Application Software

The off-the-shelf control system application software consists of various maintenance and utility programs and run-time libraries which run on the Sun workstation, and a "Parameter Page" and plotting program which runs on the Macintosh.  These programs provide basic control system maintenance tools and a human interface which supports direct access to control system functions and machine data and control points.

Higher level control system functions such as alarm display, data logging and archiving and parameter save/restore were developed for the project.  A human interface program was developed to supplement the parameter page data display by presenting machine status and control point information in a more intuitive graphical manner.  Additional software was developed to access logged machine data, operational status and project documentation via the World Wide Web.

Alarm Display

A pair of very simple programs on the Sun workstation are used to monitor the alarms information for the PET control system.  One program listens to the Internet protocol multicast channel that contains the alarm information generated by the IRMs.  It writes files on the local disk representing all devices currently in alarm state.  The second program simply reads this file at a regular interval and displays the alarm information.  The first program is written in the C, the second is written in the TCL/TK scripting language.

The IRMs determine that an alarm state exists as follows.  For each device that has alarms enabled the present reading is checked against that deviceÕs nominal and tolerance.  If it is outside of the range Ònominal ± toleranceÓ, then an alarm message is generated.  No further alarm messages are generated for this device until the reading goes within the range "nominal ± 0.5 * tolerance".  At this point an Òalarm has clearedÓ message is generated.  A tolerance of zero is valid, but only occasionally useful.

Data Logging and Archiving

There are two web documents that describe the data logging software.  The most detailed is http://www-linac.fnal.gov/~mccrory/memos/PET_datalogging/datalogging.html.

Another document containing slides for an introductory data logger presentation is at http://www-linac.fnal.gov/~mccrory/memos/datalog-talk.

Briefly, the data logger system is a suite of programs and UNIX system directives that collects and maintains archival information on the devices in the IRM-based control system.  The suite is composed of programs that control data collection, data storage, data display and system integrity checks.  The logging system is kept in the petcon2 file directory /home/pet/data-logging.  The logged data are stored in the subdirectory /data, the programs are stored in the subdirectory /scripts and database files that index the logged data are stored in the main data logging directory.

Data are collected in multiple, parallel UNIX processes. There are two basic schemes for logging.  The first scheme collects and archives data on all the devices in the control system at a very slow rate: once per two hours.  It takes five separate processes to collect data from all devices for this archive.  In the second scheme the user specifies any number of devices to be logged at any rate up to and including 1 Hz.  The user can also specify the data collection period making experiment-specific logging possible.  A unique process is created for each specified set of devices and one UNIX file contains the data for each logging process, be it an archive process or a user-defined process.

A pair of databases is maintained that allows access to the data for a specified device.  The first database uses the device name as a key and returns the number of files containing data for the specified device.  The second database uses the device name and the index number obtained from the first database as keys (e.g., DEVICE_0 for the first place where data are stored for DEVICE).  A database access returns the full filename of the file and the column number within the file that contains the requested data.  Many programs exist that manipulate these databases.  The databases are regenerated twice per day to ensure that all data are readily available to the user.  The data files are backed up to tape on a regular schedule, currently, twice a week.

Logged data can be displayed on an X terminal screen using a TCL/TK program.  Among other things, the user can specify the frequency of the data that s/he wants plotted.  All data for the device(s) is read, including archive data, and the points closest to the specified frequency are plotted.  Up to eight devices may be plotted simultaneously.

UNIX jobs which check the integrity and timeliness of data storage are started at regular intervals via the UNIX cron command to ensure that the data collection is proceeding normally.  These Òcron jobs" can restart a userÕs data log collection process if it is determined that collection has stopped prematurely.  Another cron job is used to make sure that the data in each binary data file is readable.

Save/Restore

A program is provided on the Sun workstation that allows the user to save the set points for devices in the control system.  These set points are:

¥ the analog device setting (D/A value, if appropriate),

¥ the nominal and tolerance values for the alarms on this device and

¥ the alarms flags.

This information is stored in a file on the local disk in ASCII format.  The user may specify a list of devices to be saved (e.g., the MEBT magnets), or  may request that all devices be saved. The user may at any time restore the set points for a list of devices from any file.

The main interactive program is a TCL/TK script which launches one of several C++ programs to perform the requested task.  As mentioned above, there are two types of files maintained here: the list of devices that the user has made for her/his own purposes and the saved set points.  These files are kept in separate directories in the petcon2 directory /home/pet/save-restore: devices and savefiles.

Graphical Human Interface

A family of graphical display programs developed with LabVIEW implements the primary machine console interface.  LabVIEW was chosen as the programming language because it supports the required graphical display types and it is available on the Macintosh and Sun computers thereby allowing the software to run on either computer without modification.  The graphical programs provide an intuitive display of machine status and easy to use control fields for adjustable parameters.  The human interface is based upon a model where machine elements are displayed on the screen in a schematic or a block diagram format, and data points are displayed using graphical indicators such as lights, switches and meters.  For adjustable parameters these graphical indicators may be manipulated by the operator using the mouse and keyboard.

The human interface software consists of several "Subsystem" programs each addressing a particular support subsystem of the machine, a "Status and Control" program which displays machine status broken down by accelerator stage and several special purpose "Application" programs which support machine commissioning.

The "Subsystem" programs are oriented toward the requirements of the engineering staff and display status of the various machine subsystems.  Seven programs cover:

¥ Control System,

¥ DC Power System,

¥ Instrumentation System,

¥ RF Systems:

- High Level RF

- Low Level RF

- Resonance/Frequency Control,

¥ Timing System,

¥ Vacuum System and

¥ Water System.

A typical subsystem program (Fig. 15.1) provides a bird's-eye view of the status of an entire machine subsystem.

Vacuum Subsystem Program

Figure 15.1  Vacuum subsystem LabView Display.

The "Status and Control" program is hierarchical with each level displaying more detailed views of the status of the various accelerator stages.  The highest level (Fig. 15.2) displays the overall machine status using simple numeric, digital and status summary indicators.  Clicking on a status summary indicator causes a detailed view of the associated machine stage to pop-up.  The ten machine stages which can be displayed include:

¥ Ion Source,

¥ LEBT,

¥ 212.5 RFQ,

¥ Stripper,

¥ MEBT,

¥ 425-A RFQ,

¥ 425-B RFQ,

¥ 425-C RFQ,

¥ HEBT and

¥ Target.

Status & Control Program

Figure 15.2 Status and Control LabView Display.

A typical stage pop-up (Figure 15.3) contains detailed status for all related critical machine data and may optionally allow control of related parameters.

An additional feature of the stage pop-ups is that they may contain links to the various subsystem programs so that the operator can trace an error indication directly to the related support subsystem.

The "Application" programs perform specialized functions in support of machine commissioning or operations.  These programs typically automate some measurement or process which would otherwise be tedious or time consuming.  Four such programs have been developed including:

¥ PLC Diagnostics,

¥ Collimator Control,

¥ Automated Parameter Sweep and

¥ Radiochemistry Status and Control.

A typical application program (Fig. 15.4) has the visual appearance of the front panel of an instrument that one could imagine designing to make the related measurement or to control the related process.

212.5 RFQ Stage Status Display

Figure 15.3 RFQ subsystem LabView Display.

WWW Interface

There are two relevant web home pages available on the PET project: http://www-linac.fnal.gov/pet and http://petcon2.fnal.gov.  The first provides access to PET project resources, including a description of the project, detailed project documentation, links to collaboratorsÕ web pages, links to other relevant information and an executive summary of the PET web pages.  The second URL points to the Sun/UNIX computer situated in the PET control room and provides access to selected on-line data.

Data logger data are available on-line at http://petcon2.fnal.gov/datalog.html and http://petcon2.fnal.gov/dump_datafile.html.  These two web pages, respectively, allow one to see archived data for a single device for a specified time period, or to see all of the data from a single data logger data file.

A list of all the analog devices defined in the PET control system is maintained and available on the web.  The lists are updated several times per day, so the list is almost always up to date.  They are organized by the IRM Ònode number.Ó  These lists are accessed from the web page: http://petcon2.fnal.gov.

Embedded Software

The IRMs execute off-the-shelf generic data acquisition, alarm and control scans and make the associated data available to clients such as the Sun and Apple computers through the local area network.  They also support customized  "local application" programs which may be used to perform feedback control of the equipment.  Five such local applications were developed or adapted from Linac software for the project.

Collimator Control

Figure 15.4   Collimator control subsystem LabView Display.

LLRF Interface Control

The DSP based RF equipment described in the 'Low Level RF' chapter resides in the LLRF IRM.  The DSP performs all LLRF functions autonomously in real-time but is configured by two IRM local applications programs which make DSP data and parameters available to the basic control system.  Local application LOOPLODR downloads the DSP software into the VXI modules while LOOPLLRF manages the transfer of LLRF data and parameters between the control system and the DSP.  Two copies of each program, one for each LLRF module, are continuously running in the IRM.

At power-up LOOPLODR downloads the DSP program into its associated LLRF module, sends a signal to LOOPLLRF indicating the download has completed successfully and then loops waiting for another download request.  In this way a download of new DSP code may be accomplished without disturbing the operation of the host IRM node.  Copies of the latest DSP object code files are stored within the IRM local file system.  Updating the DSP program involves transferring the object code from the DSP development environment into the IRM's file system and then restarting LOOPLODR to load the code into the DSP's memory.

LOOPLLRF waits for LOOPLODRÕs message indicating that the DSP has been loaded successfully.  At this point LOOPLLRF begins regular 10 Hz execution of a parameter update routine, a data read routine, a LLRF amplitude control routine and an error detection routine.  The parameter update routine transfers LLRF parameter settings from IRM channels into DSP control structures.  In the process of this transfer values are converted from the IRM scaled integer type to real values in engineering units and, if necessary, compared against reasonable bounds.  The data read routine transfers DSP generated RF values from the DSP structures into IRM channels and into waveform memory where it can be accessed by the control system.  In the process of this transfer values are converted from real engineering units into the IRM scaled integer type.  The amplitude control routine monitors the LLRF spark detection data and adjusts the RF amplitude as sparking in the RFQs increases or decreases.  If excessive sparking occurs the RF level is set to zero and an error is signaled.  Finally the error detection routine checks for RF system errors and causes a shutdown if required.  System status conditions that are monitored include:

¥ LLRF On/Off control,

¥ RFQ Excessive Sparking,

¥ High Level RF Operational,

¥ RFQ Tuning System Operational,

¥ Vacuum Below Threshold,

¥ Software Errors and

¥ Communications Errors.

Any error can cause an LLRF shutdown.  Configuration masking bits are provided to individually enable/disable each status condition from the scan.

PLC Status And Control Communications

Communication of PLC data for PET is via an RS-232 connection running from the IRM to the PLC.  Two nodes of the nine have such interfaces to PLC controllers.  An area of memory in the PLC, about 50 words in size, is interrogated by the IRM every two or three 10 Hz cycles, using the standard DirectNET protocol. This data represents a data pool of analog and digital data words that are mapped into the IRM data pool for access by host computers. When a control action is to be performed, whether analog or digital, a part of this memory is modified; the PLC acts on the change to control the appropriate hardware device. Only a single control action may be performed between successive data acquisitions; any additional control actions are queued. The communication logic is contained within the local application named LOOPDNET that runs in the IRM.

Power Supply Control

While the PLC monitors the digital logic of the power supplies, watching for interlock trips and other digital status, it can monitor neither over currents nor ground faults. Support software for the power supplies provides monitoring for over currents and ground faults, because the PLC does not have analog interfaces to the power supplies. The digitized readings of the power supply currents and ground fault currents, however, are interfaced directly to the IRM via its own A/D controller. The LOOPPETP local application performs the necessary checks every 10 Hz cycle on over currents for 22 supplies, and it checks on ground faults for 8 supplies. Based upon what it finds, it maintains a status bit for each of the 30 tests that is passed to the PLC controller, thus enabling the PLC to be aware of it. Node 587 operates this logic, including the heartbeat protection described in the next paragraph. The time required for all of the analog checking logic is about 1.5 ms each 10 Hz cycle.

A heartbeat scheme is used to assure the PLC that the analog checking described above is operating so that the PLC can rely upon its digital status output. The PLC controls a bit that is part of the digital data periodically collected by the IRM, toggling its state every half second. The heartbeat logic watches these bit transitions and reflects the current state to a control line that is wired directly to a PLC digital input. As long as this line is seen by the PLC to be toggling regularly, the PLC can be assured that the IRM is working, that the LOOPDNET data acquisition is operational, and that the LOOPPETP analog checking logic described above is being performed. This heartbeat logic is used in node 587. Two additional heartbeats are monitored in node 586, although there is no associated analog checking being done in that node, so that the PLC in that case need only be assured that the IRM is working and that LOOPDNET communications is operational.

Power Supply Regulation

A new piece of imbedded system software is the PID control loops, which are used to regulate the MEBT magnets and the RF system frequency and temperature.  This software is described and documented on the web page at http://www-linac.fnal.gov/~McCrory/memos/PID_description/PID_description.html.  Briefly, PID stands for ÒProportional, Integral and Differential.Ó  These quantities are calculated from an Òerror signal,Ó in the appropriate way. A PID loop is a feedback loop, the output of the feedback loop is proportional to expert-defined coefficients times each of the three pieces, P, I and D.

The critical magnets in the HEBT are regulated by the IRM using the PID control loop called LOOPPIDM.  The magnets being regulated with this PID loop are:

1.	ALPHA, the Alpha magnet pair

2.	MEQ1, the first quad in the MEBT

3.	MEQ2, the second quad in the MEBT

4.	MEQ4, the fourth quad in the MEBT

5.	MEQ5, the fifth quad in the MEBT

6.	HEQ1, the first quad in the HEBT

7.	HEMP, the multipole magnet in the HEBT.

The effect of this loop is to increase the overall regulation of these magnets to close to 0.1%.  Mostly, this loop removes long-term drifts in the current through the magnet.

RF / Temperature Control

All four of the RF cavities are controlled in the steady state and during transients by a suite of five PID loops called LOOPPIDC.  These loops are variants of the PID loops described in the Power Supply Regulation section above.  Additionally, there is a control loop running in the IRM that orchestrates when each loop runs and whether or not the RF drive comes from the line or from a local voltage-controlled oscillator; this loop is called LOOPOVCO.  These five PID loops are described in the 'RF Tuning Systems' chapter and are referred to as the:

1.	Average power loop,

2.	VCO Resonance control loop,

3.	VCO control loop,

4.	Temperature control loop and the

5.	Master resonance control loop.

FERMILAB

August 30, 1996

3He++ RFQ PET Isotope Production Project

BRF, Fermilab, SAIC, University of Washington

Phase 1 Accelerator Performance Parameters

Introduction

This document defines performance parameters of the 3He++ accelerator which are to be met and demonstrated at Fermilab before shipment of the machine to the Biomedical Research Institute (BRI) in Shreveport, Louisiana.

Beam Current

The accelerator shall be capable of delivering, through the HEBT, l50 microamperes of l0.5 MeV 3He++ beam current (10 second, time averaged electrical current). The machine control system shall provide for adjustment of this average beam current in steps of 5% or smaller. It is expected that the nominal pulse current is fixed and that the average current is controlled by pulse gating. Pulse-to-pulse current fluctuations over a 30 minute interval shall not result in pulses at a current greater than 12O% of the nominal pulse current chosen for that run.

Beam Parameters Available at Chemistry Target

A beam size of 2.5 cm (horizontal) by 14 cm (vertical) shall be available at the target window. At that location, the beam current distribution over a 2 cm by 10 cm area shall be uniform to within +/-25% of the mean value in all 2 mm by 2 mm regions as determined by foil activation experiments. Neighboring regions within this area shall be uniform to +/-10%. Measurements shall be performed to demonstrate that the required uniformity is repeatable from run to run.

Beam Availability and Reliability

Beam availability and machine reliability shall be demonstrated by operation during 5 pre-scheduled 8 hour running periods within a two week time interval. operation shall be at a nominal l50 microampere electrical beam current on target or on Faraday Cup with less than 25% downtime (target/window failures excluded). During these periods the machine shall be operated by SAIC personnel who are expected to perform this function at BRI. Machine turn-on time of less than one hour from cold start (systems under vacuum; RF filaments hot; ion source, RFQ cavity water systems, and all magnet power supplies off) to stable beam on Faraday Cup shall be demonstrated. Availability of stable beam on the Faraday Cup in less than 30 minutes following a normal target vault access shall be demonstrated.

revision date: 8/30/96

revision: 2 printed: 9/4/96

PAGE 1 oF 2

Target Studies

Target and related studies shall be performed to confirm beam parameters at the target location and to assure that the HEBT, target, and shielding designs are acceptable for machine operation at BRI. Specific targetry goals at Fermilab include: 1) learn how to tune beam onto and extract heat from the target while maintaining target window integrity with gas cooling and with water cooling, 2) measure radiation dose rates, both beta/gamma and neutron, and evaluate shielding performance, 3) learn what isotope quantities will be produced by the beam, and 4) learn in what radiochemical form these isotopes will be produced and extracted from the targets.

Radiation Safety and Radiation Shielding Measurements

The goal is to operate the machine safely at Fermilab and to ensure that the machine, as delivered to and assembled at BRI, can be operated there in a manner consistent with all applicable regulations and safety codes. All necessary measures shall be taken to conform to Department of Energy (DOE) and Fermilab radiation shielding, exposure, and monitoring regulations while the machine operates at Fermilab. All necessary measures shall be taken to assure that the machine and target station design facilitates compliance with radiation safety regulations applicable at BRI. In particular, radiation dose and radiation shielding effectiveness measurements shall be performed at Fermilab to a degree sufficient to determine design modifications, administrative measures, and operational procedures necessary to satisfy requirements at BRI.

Electrical and Conventional Safety

Passive safety devices and active safety interlocks shall meet the requirements of applicable DOE and Fermilab standards and of safety codes applicable at BRI.

Jerry Bida, Biomedical Research Foundation	Ken Krohn, University of Washington

Ralph Pasquinelli, Fermilab	Phil Young, SAIC

revision date: 8/3O/96 revision: 2

PAGE 2 oF 2		panted: 9/4/96