## Temperature-NV
CHAPTER 2. PREDICTING HOT GAS LAYER TEMPERATURE AND SMOKE
LAYER HEIGHT IN A ROOM FIRE WITH NATURAL VENTILATION
COMPARTMENT WITH THERMALLY THICK/THIN BOUNDARIES
Version 1805.0
The following calculations estimate the hot gas layer temperature and smoke layer height in enclosure fire.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Material Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input
parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cell(s).
The chapter in the NUREG should be read before an analysis is made.
INPUT PARAMETERS
COMPARTMENT INFORMATION
| Compartment Width (wc) |  |  |  | 15 | ft | 4.572 | m
| Compartment Length (lc) |  |  |  | 15 | ft | 4.572 | m
| Compartment Height (hc) |  |  |  | 10 | ft | 3.048 | m
STOP - VT ≥ hv
| Vent Width (wv) |  |  |  | 4 | ft | 1.2192 | m
| Vent Height (hv) |  |  |  | 6 | ft | 1.8288 | m
| Top of Vent from Floor (VT) |  |  |  | 6 | ft | 1.8288 | m
| Interior Lining Thickness (d) |  |  |  | 12 | in | 0.3048 | m | STOP - d > 1 inch
AMBIENT CONDITIONS
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F | 25 | °C
[7 empty] | 298 | K
| Specific Heat of Air (cp) |  |  |  | 1 | kJ/kg-K
| Ambient Air Density (ra) |  |  |  | 1.1846 | kg/m3
THERMAL PROPERTIES OF COMPARTMENT ENCLOSING SURFACES FOR
| Interior Lining Thermal Inertia (krc) |  |  |  | 2.9 | (kW/m2-K)2-sec
| Interior Lining Thermal Conductivity (k) |  |  |  | 0.0016 | kW/m-K
| Interior Lining Specific Heat (c) |  |  |  | 0.75 | kJ/kg-K
| Interior Lining Density (r) |  |  |  | 2400 | kg/m3
Note: Air density will automatically correct with Ambient Air Temperature (Ta) Input
EXPERIMENTAL THERMAL PROPERTIES FOR COMMON INTERIOR LINING MATERIALS
| Material |  | krc | k | c | r | Select Material
|  |  | (kW/m2-K)2-sec | (kW/m-K) | (kJ/kg-K) | (kg/m3)
| Aluminum (pure) |  | 500 | 0.206 | 0.895 | 2710 | Scroll to desired material then
| Steel (0.5% Carbon) |  | 197 | 0.054 | 0.465 | 7850 | Click the selection
| Concrete |  | 2.9 | 0.0016 | 0.75 | 2400
| Brick |  | 1.7 | 0.0008 | 0.8 | 2600
| Glass, Plate |  | 1.6 | 0.00076 | 0.8 | 2710
| Brick/Concrete Block |  | 1.2 | 0.00073 | 0.84 | 1900
| Gypsum Board |  | 0.18 | 0.00017 | 1.1 | 960
| Plywood |  | 0.16 | 0.00012 | 2.5 | 540
| Fiber Insulation Board |  | 0.16 | 0.00053 | 1.25 | 240
| Chipboard |  | 0.15 | 0.00015 | 1.25 | 800
| Aerated Concrete |  | 0.12 | 0.00026 | 0.96 | 500
| Plasterboard |  | 0.12 | 0.00016 | 0.84 | 950
| Calcium Silicate Board |  | 0.098 | 0.00013 | 1.12 | 700
| Alumina Silicate Block |  | 0.036 | 0.00014 | 1 | 260
| Glass Fiber Insulation |  | 0.0018 | 3.7e-05 | 0.8 | 60
| Expanded Polystyrene |  | 0.001 | 3.4e-05 | 1.5 | 20
| User Specified Value |  | Enter Value | Enter Value | Enter Value | Enter Value
Reference: Klote, J., J. Milke, Principles of Smoke Management, 2002, Page 270.
FIRE SPECIFICATIONS
| Fire Heat Release Rate (Q) |  |  |  | 500 | kW
Calculate
METHOD OF McCAFFREY, QUINTIERE, AND HARKLEROAD (MQH)
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-175.
DTg = 6.85 [Q2/(Av(hv)1/2) (AThk)]1/3
| Where | DTg = Tg - Ta = upper layer gas temperature rise above ambient (K)
Q = heat release rate of the fire (kW)
Av = area of ventilation opening (m2)
hv = height of ventilation opening (m)
hk = convective heat transfer coefficient (kW/m2-K)
AT = total area of the compartment enclosing surface boundaries excluding area of vent openings (m2)
Area of Ventilation Opening Calculation
| Av = | (wv) (hv)
| Where | Av = area of ventilation opening (m2)
wv = vent width (m)
hv = vent height (m)
| Av = | 2.2297 | m2
Thermal Penetration Time Calculation
| tp = | (rcp/k) (d/2)2
| Where | tp = thermal penetration time (sec)
r = interior construction density (kg/m3)
cp = interior construction heat capacity (kJ/kg-K)
k = interior construction thermal conductivity (kW/m-K)
d = interior construction thickness (m)
| tp = | 26128.98 | sec
Heat Transfer Coefficient Calculation
| hk = | √(krc/t) | for t < tp | or (k/d) | for t > tp
| Where | hk = heat transfer coefficient (kW/m2-K)
krc = interior construction thermal inertia (kW/m2-K)2-sec
(a thermal property of material responsible for the rate of temperature rise)
t = time after ignition (sec)
See table below for results
Area of Compartment Enclosing Surface Boundaries
| AT = | [2(wc x lc) + 2(hc x wc) + 2(hc x lc)] - Av
| Where | AT = total area of the compartment enclosing surface boundaries excluding area of vent openings (m2)
wc = compartment width (m)
lc = compartment length (m)
hc = compartment height (m)
Av = area of ventilation opening (m2)
| AT = | 95.3185 | m2
Compartment Hot Gas Layer Temperature With Natural Ventilation
DTg = 6.85 [Q2/(Av(hv)1/2) (AThk)]1/3
| DTg = | Tg - Ta
| Tg = | DTg + Ta
| Time After Ignition (t) |  | hk | DTg | Tg | Tg | Tg |  | STOP - DO NOT USE THIS WORKSHEET IF HOT
| (min) | (sec) | (kW/m2-K) | (K) | (K) | (°C) | (°F) |  | GAS LAYER TEMPERATURE EXCEED 1112 °F
| 0 | 0 | - | - | 298 | 25 | 77
| 1 | 60 | 0.21985 | 108.3417 | 406.3417 | 133.3417 | 272.015
| 2 | 120 | 0.15546 | 121.6094 | 419.6094 | 146.6094 | 295.897
| 3 | 180 | 0.12693 | 130.1115 | 428.1115 | 155.1115 | 311.2008
| 4 | 240 | 0.10992 | 136.502 | 434.502 | 161.502 | 322.7036
| 5 | 300 | 0.098319 | 141.6741 | 439.6741 | 166.6741 | 332.0135
| 10 | 600 | 0.069522 | 159.0238 | 457.0238 | 184.0238 | 363.2429
| 15 | 900 | 0.056765 | 170.1417 | 468.1417 | 195.1417 | 383.2551
| 20 | 1200 | 0.04916 | 178.4982 | 476.4982 | 203.4982 | 398.2968
| 25 | 1500 | 0.04397 | 185.2617 | 483.2617 | 210.2617 | 410.471
| 30 | 1800 | 0.040139 | 190.9776 | 488.9776 | 215.9776 | 420.7597
| 35 | 2100 | 0.037161 | 195.9477 | 493.9477 | 220.9477 | 429.7059
| 40 | 2400 | 0.034761 | 200.3575 | 498.3575 | 225.3575 | 437.6435
| 45 | 2700 | 0.032773 | 204.3295 | 502.3295 | 229.3295 | 444.7931
| 50 | 3000 | 0.031091 | 207.9492 | 505.9492 | 232.9492 | 451.3086
| 55 | 3300 | 0.029644 | 211.2789 | 509.2789 | 236.2789 | 457.3019
| 60 | 3600 | 0.028382 | 214.3651 | 512.3651 | 239.3651 | 462.8572
ESTIMATING SMOKE LAYER HEIGHT
METHOD OF YAMANA AND TANAKA
z = ((2kQ1/3t/3Ac) + (1/hc(2/3)))-3/2
| Where | z = smoke layer height (m)
Q = heat release rate of the fire (kW)
t = time after ignition (sec)
hc = compartment height (m)
Ac = compartment floor area (m2)
k = a constant given by k = 0.076/rg
rg = hot gas layer density (kg/m3)
rg is given by rg = 353/Tg
Tg = hot gas layer temperature (K)
Compartment Area Calculation
| Ac = | (wc) (lc)
| Where | Ac = compartment floor area (m2)
wc = compartment width (m)
lc = compartment length (m)
| Ac = | 20.9032 | m2
Hot Gas Layer Density Calculation
| rg = | 353/Tg
Calculation for Constant K
| k = | 0.076/rg
Smoke Gas Layer Height With Natural Ventilation
| z = | [(2kQ1/3t/3Ac] + (1/hc2/3))-3/2
Caution! The smoke layer height is a conservative estimate and is only
intended to provide an indication where the hot gas layer is located. Calculated
smoke layer height below the vent height are not creditable since the calculation
is not accounting for the smoke exiting the vent.
|  | Time | rg | Constant (k) | Smoke Layer height | Smoke Layer height
|  | (min) | (kg/m3) | (kW/m-K) | z (m) | z (ft)
|  | 0 | 1.1846 | 0.064159 | 3.048 | 10
|  | 1 | 0.86873 | 0.087484 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 2 | 0.84126 | 0.090341 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 3 | 0.82455 | 0.092171 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 4 | 0.81242 | 0.093547 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 5 | 0.80287 | 0.094661 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 10 | 0.77239 | 0.098396 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 15 | 0.75405 | 0.10079 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 20 | 0.74082 | 0.10259 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 25 | 0.73045 | 0.10405 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 30 | 0.72191 | 0.10528 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 35 | 0.71465 | 0.10635 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 40 | 0.70833 | 0.1073 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 45 | 0.70273 | 0.10815 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 50 | 0.6977 | 0.10893 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 55 | 0.69314 | 0.10965 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 60 | 0.68896 | 0.11031 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
The above calculations are based on principles developed in the SFPE Handbook of Fire
| Protection Engineering, 3rd Edition, 2002. | [7 empty] | STOP - IF Z ≥ VT, SMOKE EXITING VENT
Calculations are based on certain assumptions and have inherent limitations. The results of such
calculations may or may not have reasonable predictive capabilities for a given situation, and should
only be interpreted by an informed user.
Although each calculation in the spreadsheet has been verified with the results of hand calculation,
there is no absolute guarantee of the accuracy of these calculations.
Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheet,
please send an email to nxi@nrc.gov. or mxs3@nrc.gov
Prepared by: |  | Date |  | Organization
Checked by: |  | Date |  | Organization
Additional Information
Revision Log | Description of Revision | [5 empty] | Date
1805.0 | Original issue with final text. | [5 empty] | January 2005
Note on F26: This default value (1.00) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.