# Energy Star Performance

NOTE:  as of March 2002, the commercial spaces for which an Energy Star label can be obtained include:  offices, K-12 schools, Supermarket / Grocery, Hotel / Motel, and Hospitals.

Energy efficiency performance will be determined using the Energy Star Target Finder rating tool for new building designs.  During design an estimate of annual energy use by fuel type for each portion of a building that can be handled by the tool: office,  etc., must be developed in order to obtain a design rating.

Planned building characteristics required for use in the Energy Star rating tool are required as input to calculate the expected Energy Star rating.  For office buildings these characteristics include gross floor area that is:  office, computer center, attached/unattached-ventilated/unventilated parking garage.  The on-line forms must be run through to verify the data needed.

A rating of 75 or higher is required to achieve an Energy Star label.  The recommended rating of the design is 85, as actual performance is often less than design, and achieving a design level of 85 helps assure a rating of 75 in use.  Actual energy performance must be tracked to submit for an Energy Star label following occupancy.  The Energy Star performance rating of the occupied building can provide some evaluation of design team, construction team, and commissioning team performance.

Sometimes, a building may have spaces that are not typical for an office or other covered building type, or only a portion of a building has such space in it.  In such cases, consideration should be given to submetering of either the atypical spaces or the applicable space to arrive at a net energy use for the applicable space.  The energy use for this space is referred to as the net energy use below.

Net energy use equals total energy use for the building minus energy use for atypical spaces, such as large process energy use in major computer data centers that are very energy intensive.  Gross floor area for the typical space equals gross floor area of the entire building minus the gross floor area of the atypical spaces.  Remaining gross floor area that consists of more typical computer centers or parking garages (and type), which the tool can adjust for, must also be known.  Total annual net building energy use for each fuel is entered in the Energy Star Target Finder rating tool, together with the required characteristics, to obtain a rating:

http://yosemite1.epa.gov/estar/business.nsf/content/nbd_targetfinder.htm

(click on the Enter Target Finder icon on the right after familiarizing)

An estimate of Energy Star performance should be obtained for each stage of design (e.g., conceptual, schematic, design development stages).

Key mechanical considerations relative to an Energy Star rating include:

Enthalpy or heat recovery in the IAQ/exhaust/pressurization system

Effective zoning of the IAQ/exhaust/pressurization and heating / cooling systems

Minimization of fan power requirements and use (small, local, single-zone systems for heating/cooling systems and smaller, effectively zoned systems for IAQ)

Occupancy-based control of heating and cooling, with systems off when unoccupied

Key electrical considerations include:

Effective integration and use of daylighting to increase quality and offset electrical lighting

Occupancy control of lighting and daylighting

Efficient lighting sources and lighting power densities below 1 Watt per square foot

Effective integration of occupancy, daylighting, and central system control

Efficient and not excessive outdoor lighting

Efficiency of LAN/WAN operation so power can be switched lower as use lowers

Energy Star computers, equipment, and appliances, with energy-saving features activated and minimal number of computer workstations that have to be left activated 24/7 (meaning that workstations actually power off when not in use for 45-60 minutes, and this also means a boot procedure that does not take excessive time)

Effective selection of any required data transfer procedures to minimize number of 24/7 workstations

Efficient motors and transformers, well matched to requirements and well integrated with mechanical systems efficiency needs as required

Separate metering of process energy and exterior security lighting energy so it can be subtracted from total energy for an Energy Star label

If LEED energy credit 1 points are desired, consider:

In addition to the Energy Star rating, the design is required to obtain 2 credit points under Energy Credit 1 of the LEED rating system, which means that the proposed design will use 20% less energy than a base compliance (minimally compliant) building, generally using the Energy Cost Budget method in ASHRAE Std 90.1-1999, Section 11.  The energy values used to calculate the percent reduction are:  building energy equal to total simulated building energy use minus simulated computer use and other plug load use.  Any process energy should also be excluded when calculating the percentage reductions.

The features and approaches that lead to an Energy Star rating will differ somewhat from those that allow the 2 credit points under LEED Energy Credit 1.

Download this document from:  http://eber.ed.ornl.gov/commercialproducts/Design.htm

This document is not necessarily definitive, and comments are appreciated.

Email:  macdonaldjm@ornl.gov