COMBINED HEAT AND POWER

IN MULTIFAMILY HOUSING

USER MANUAL

for

HUD CHP Feasibility Screening Tool Version 2.1

April 30 Draft, 2008

Manual developed by

U.S. Department of Energy, Oak Ridge National Laboratory

for

U.S. Department of Housing and Urban Development

# Table of Contents

Table of Contents	2

Getting Started	4

What is the HUD CHP Feasibility Screening Tool and who should use it?	4

What does the HUD CHP Tool do?	4

How do I use the HUD CHP Tool?	4

Overview of the HUD CHP Tool	5

Data Forms & Results	5

Monthly Utility Data	5

Utility Rate Data	6

Miscellaneous Input Information	7

Energy Plots	8

Results	10

Menu Commands	12

File Menu	12

Print Options Form under File Menu	14

Print:  Side-By-Side Comparison of Results	16

Print:  Method 1 Intermediate Results	16

Print:  Method 2 Intermediate Results	17

Print:  Method 3 Intermediate Results	18

Data Menu	20

Help Item	20

Electric Generation and Prime Movers	20

Reciprocating Engine Generators	21

Equipment Cost	21

Installation Cost	21

Heat Rate and Efficiency	22

Heat Recovery	22

Operating and Maintenance Costs	23

Gas Turbine Generators	23

Equipment Cost	23

Installation Cost	23

Heat Rate and Efficiency	24

Heat Recovery	24

Operating and Maintenance Costs	25

Microturbine Generators	25

Equipment Cost	25

Installation Cost	26

Heat Rate and Efficiency	26

Heat Recovery	26

Operating and Maintenance Costs	27

Algorithms and Methodology	27

“Method 1” Algorithms	27

“Method 2” Algorithms	29

Method 2 Assumptions & Methodology:	29

Method 2 Results	30

“Method 3” Algorithms	33

Details of Method 3 Calculations using the Sample Data:	36

Method 3 Assumptions & Methodology Applied to the Sample Data	38

Additional Information on Building Loads	38

Electrical & Thermal Loads	38

Electrical Loads	39

Space Heating & Hot Water Loads	40

Map of EIA Climate Zones for 2001 Residential Energy Consumption Survey (RECS)	40

# Getting Started

## What is the HUD CHP Feasibility Screening Tool and who should use it?

Combined heat and power (CHP) (or cogeneration) is the production of electricity and use of the heat created in that process. Putting heat recovery together with power generation can provide essentially free energy in the form of hot water or steam. In residential applications the heat can be used for domestic hot water, space heating, absorption cooling, or dehumidifying, at the building where it is produced. CHP systems consist of a package of equipment with a prime mover (for apartment buildings, most often a reciprocating engine or microturbine) driving an electric generator. If all of the recoverable heat is used, they can achieve overall efficiencies of about 80%, in contrast to the 33% average of more typical systems where electricity is produced at central power plants. CHP avoids transmission losses and reduces environmental impact.

The economic evaluation of proposed installations of combined cooling, heating, and power systems in multi-family housing units requires calculations that consider building heating, cooling, hot water, and electrical loads, the costs of power and natural gas, and the simulated performance of generators, chillers, boilers, and water heaters. Sometimes it is possible to simplify this process to get a “go/no-go” answer as to whether or not a building owner or operator should look more carefully into CHP and perhaps enlist some engineering support in conducting a site inspection and a rigorous economic analysis. The HUD CHP Feasibility Screening Tool is one of several tools available for “screening level” CHP analysis; this tool is “non-technical” and is directed specifically toward building owners and operators.  The tool may be installed from the following website:

http://eber.ed.ornl.gov/HUD_CHP_Guide_version_2.1/

While CHP is not recommended for emergency generators, it is frequently attractive in baseload or peak shaving operation with reciprocating engine driven generators, gas turbine generators, microturbines, or fuel cells. All-electric buildings are good prospects for installing CHP, but this Tool will not analyze them.  The better prospects for installing CHP are single apartment buildings with 100 or more units, master metered for electricity, with a central domestic hot water system, and with access to gas.

## What does the HUD CHP Tool do?

The HUD CHP Tool performs a coarse economic assessment of the viability of installing on site power generation combined with recovery of generator heat for use in producing domestic hot water, space heating, or even air conditioning using a heat driven absorption chiller. It does this assessment by using information provided by the user, primarily from the electric and gas utility bills, and some built in correlations for generator performance and costs. The energy cost and consumption data and generator information are combined to provide an estimate of the simple payback from installing combined cooling, heating, and power (CHP) at the site.

## How do I use the HUD CHP Tool?

The first step is to collect old billing information for both power and heating. The electric energy use or consumption and monthly peak demand and cost information can be found on the electric bills for the prior twelve months. Heating bill information can be from fuel oil purchases, natural gas, or steam purchased from a district energy system. Data are needed for a primary fuel and as an option information can also be provided for a secondary fuel.

The user also needs to be prepared to provide information about the electric and natural gas utility tariffs. This includes:

- the electric consumption or use charge ($/kWh),

- any fuel adjustment charge used by the utility ($/kWh),

- the peak demand rate ($/kW),

- any electric utility standby charges for providing backup capacity whenever the on site generator is down for scheduled or unscheduled maintenance, and

- the cost of natural gas.

The user enters these numbers into a “fill in the blank” form and an estimated simple payback is returned.

# Overview of the HUD CHP Tool

The HUD CHP Tool can be used to do a preliminary screening of the economic potential of combined heating and power or combined cooling, heating, and power in specific multifamily housing and apartment buildings. The Tool uses information the user provides about the building and energy costs from utility bills to make coarse estimates of the hot water and space heating and cooling loads. These estimates are combined with built-in data for electric generators to calculate approximate energy and cost savings from operating on site generators with heat recovery for domestic hot water, space heating, and space cooling. The estimated system installed cost is divided by annual savings on energy costs to calculate a simple payback in years.

# Data Forms & Results

The CHP Tool consists of a data form with several data “tabs.” These include the principal data entry forms under “Monthly Utility Data,” “Utility Rate Data,”  supplementary information under “Misc. Input Information,” and calculated savings and payback under “Results.”

## Monthly Utility Data

For the first form, the principal input data consist of information from the user’s monthly utility bills (Figure 1). There are three columns of numbers from the electric bills and two sets of two columns each for fuel consumption. Many sites will only use a single source of fuel for boilers, water heaters, or furnaces and they will only need to fill in the columns for “Fuel #1.” Sites that use two fossil fuels, for example natural gas and #2 fuel oil, complete both sets of columns for fuel data. Users need to select a type of fuel or energy for the pair(s) of column used and also the units of consumption in the case of natural gas (i.e. therms, decatherms, million Btu’s, hundreds of standard cubic feet, or thousands of standard cubic feet). Fuel oil data are assumed to be in gallons and purchased steam in thousands of pounds.

The table of numbers should be completed as carefully as possible using data from monthly utility bills. The user does not need to include “,” or “$” in the numbers as they are typed; the Tool will format each number as it proceeds. Use either the “Tab” or “Enter” keys to move from one data entry point to the next. Use Shift+Tab to move backwards. The average cost of power for the year is computed below the third column from the left for informational purposes (a bit of a reality check for misplaced decimal points) and below the Fuels columns.  (Note that if monthly data are not available, Method 3 can still produce results from utility rate data entered on the second tab.)

Figure 1 — Monthly utility data entry form.

## Utility Rate Data

The second form (second tab, Figure 2) contains two blocks of information about the utility rate structures. Many electric utilities use multiple block tariff structures, so the user should enter energy and demand rates “at the margin” -- the highest block where they are actually purchasing power since this is what would have applied to power generated on site. Many utilities use a basic energy charge ($/kWh) and also a fuel adjustment charge ($/kWh) to recoup their own costs as fuel prices increase. Savings from avoidance of purchased utility power are calculated using the sum of the energy charge and the fuel adjustment charge. The Tool assumes that any on-site power generation is produced using a natural gas-fired generator and it provides for the cost of gas to be computed using a flat rate. The “option” buttons are used to select the units of natural gas consumption.

Figure 2 — Utility rate data form.

## Miscellaneous Input Information

CHP calculations are performed using three different methods of estimating the building thermal loads. One of these methods employs a table of information for heating and cooling degree days that has been built into the Tool. In the third tab (Figure 3) users can select a state from the list under item “1” on this tab and then a city within that state from item “2.” The corresponding heating and cooling degree days selection for a typical year are based on this location. These are correlated to “energy intensity factors” (see Method 3 Algorithms) to estimate space heating and cooling loads using items 3a and b on this tab.  The “Prime Mover” box at the bottom has different technology types “greyed out” depending on the size of system needed.  If microturbines are an appropriate choice for the building, they will be available as a prime mover, but the sample building load is over 400 kW (Figure 4), so microturbines are not allowed as a reasonable screening choice for this building (a later more detailed analysis could include them).

Domestic hot water loads are estimated using an average per capita daily hot water usage and annual average ground temperature (cold water entering the water heater tank) for the city specified in item “2.” The approximate number of residents in the building is specified in Item 4 and a subjective measure of relative hot water consumption is chosen in Item 5. Hot water loads are estimated using these selections with data for multifamily housing hot water consumption reported by Goldner (1994, see “Method 3 Algorithms” for citation).

Methods 1 and 3 size the generator using the highest monthly power consumption (kWh) and an assumed generator “run time fraction.” The built-in sample data set, for instance, is for a site that uses 56,400 to 138,000 kWh per month with the maximum of 138,000 kWh occurring in August. This amount of power would be produced by a 247 kW generator (138,000 kWh / [31 days x 24 hr/day x 0.75] ).  A 250 kW generator would be the closest commercially available capacity to the computed size. A default run time fraction of 0.75 is built into the HUD CHP Tool, but this value can be changed by the user by selecting a number in Item 6 on the “Misc. Input Information” tab.

Fuel consumption data on the “Monthly Utility Data” tab are converted to heat and hot water loads using an assumed furnace, boiler, or water heater efficiency. There is a place on the “Misc. Input Information” tab where the user can change the built-in value for annual heating efficiency to another value using Item 7 if desired.

The “Misc. Input Information” tab is used so the user can change some default parameters used in the calculations. The CHP economic results are computed three different ways using different methods to estimate the heating and cooling loads. Each of the methods use data built into the Tool for generator equipment cost, installation cost, maintenance cost, and operating efficiency. The user selects information by specifying the type of generator to be used (i.e. reciprocating-engine, gas turbine, microturbine, or fuel cell) using the buttons at the bottom of this page. Reciprocating-engines, microturbines, and fuel cells are available (or soon will be) across the entire range of generator capacities applicable to multifamily housing, so these choices are always available. Gas turbines, however, are only applicable to the largest installations and this choice is only available if the estimated capacity is greater than 1,000 kW.

## Energy Plots

The “Energy Plots” tab of the main data form contains two rows of bar charts. The three charts at the top half of the page display the user supplied information (Input Data) from the “Monthly Utility Data” tab and shows (a) electric power consumption in kWh, (b) electric demand in kW, and (c)  total fossil fuel consumption for heating and hot water in millions of Btu’s (MMBtu). These charts should show distinct differences in energy use between the summer and winter months. If power and fuel consumption are fairly level throughout the year (i.e. bars all about the same height), then “Method 1” and “Method 2” may not give good estimates of heating and cooling loads that are subsequently used in the CHP calculations.

The three charts at the bottom of this page display results for the CHP simulation using “Method 2.” The blue bars in the chart on the left show the amount of electricity generated by the CHP system each month and the red bars the amount of electricity supplied by the utility. By comparing red bars in the upper chart for electricity purchased for the baseline system with the red bars in the lower chart for the CHP system, the user can see reductions in purchased utility power due to CHP. Likewise, the center chart at the bottom shows the maximum monthly power demand for the CHP system with the purchased utility demand in red and the CHP system capacity in blue. CHP systems that use recovered heat in absorption chillers to provide air conditioning will also have a green bar that indicates avoided power demand by using absorption air conditioning. Once again, the red bars in the upper and lower charts can be compared to see reductions in utility demand due to the CHP system.

Figure 4 — Energy plots.

The lower chart on the far right displays data for the monthly fuel consumption. The red segments correspond to boiler and water heater fuel and the blue segments correspond to fuel use for the CHP generator.

## Results

The HUD CHP Tool performs three separate sets of calculations that are summarized on the “Results” tab. This brief summary provides the range of simple payback periods from the analyses and also the range in generator capacities assumed. There is also a group of “check boxes” that can be used to display additional information about the calculations. Information about the assumptions and algorithms used in the calculations can be displayed by clicking the check box for “Summary.”

Figure 5 — Results tab.

The first method used for the calculations is for a CHP system that only uses recovered heat for domestic hot water; no recovered heat is assigned for space heating or powering an absorption chiller for space cooling. Hot water consumption is estimated from the utility data specified for the summer months (May through September) on the “Monthly Utility Data” tab. Electricity and natural gas costs are also taken from the input data for the gas and electric utilities on that data tab (at the bottom of the page, not the table of monthly usage and cost).

The second method assumes a CHP system that uses recovered heat for (1)domestic hot water, (2)space heating, and (3)space cooling with an absorption chiller. This algorithm also derives hot water and heating and cooling loads from the table of monthly fuel and power consumption and uses the input utility data for power consumption, demand rates, natural gas costs, etc. from the “Energy & Utility Data” tab. This algorithm performs a month-by-month evaluation and selects the generator size that provides the shortest simple payback.

The third method estimates annual heating and cooling loads from the building location and algorithms published by the Department of Energy’s Energy Information Administration based on heating and cooling degree days. It also uses the electric and gas utility rate information to calculate system operating costs.

Whether or not a CHP would be economical depends on the type and size of generator installed, the equipment and installation costs, generator efficiency, heat recovery rate, and annual maintenance costs. All of the generator related parameters vary by equipment type (i.e. reciprocating-engine, gas turbine, microturbine, fuel cell). CHP system installation costs can vary widely depending on site specific conditions (e.g. location and capacity of transformers, relocation of existing equipment, distance from gas line, gas line pressure). The user can use the buttons located on tab “Misc. Input Information” to select the type of generator and difficulty of installation. Simple payback is computed as the sum of the equipment and installation cost divided by the difference between the baseline operating cost (i.e. utility power and boiler/water heater fuel) and the CHP operating cost (generator and boiler/water heater fuel, generator maintenance costs, and any necessary utility power).

Figure 6 — Summary notes displayed when “Summary” check box is checked.

# Menu Commands

The HUD CHP Tool data form includes a menu bar to assist in data entry, printing, and maneuvering throughout the form. It is located at the upper-left of the form, as shown in Figure 7.

## File Menu

The File Menu can be used to start a new data file, print a summary of the current set of calculations, open and save data files, and exit the Tool. These commands can be invoked by clicking them with the mouse cursor, using the “Alt” key on the computer, or with the “CONTROL” key. Pressing “Alt” by itself causes the entries on the menu bar to be displayed with the “F” “D” and “H” underlined. Holding down “Alt” and pressing “F” displays the file menu. Continuing to hold the “Alt” key down and pressing another letter invokes one of the menu options:

- “N” clears all of the data selections for a new set of information,

- “P” prints the current set of information,

- “O” initiates the process of opening an existing data set,

- “S” saves the current set of data,

- “A” initiates the process of saving the present data under a new name, and

- “X” exits the Tool.

The file commands can also be invoked by holding down the control key, “Ctrl,” while typing “N” “P” “O” “S” “A” or “X”.

The last item on the “File Menu,” “Capture Screen Shots,” is a new feature. It allows the user to automatically create a Microsoft Word file that contains images of the HUD CHP Tool data tabs that are “open.”  Remember that additional tabs can be “opened” by clicking on the option boxes for “Summary,” “Method 1,” “Method 2,” or “Method 3” on the “Results” tab.  The screen captures put into the Word file are of all open tabs, so there can be differences depending on which tabs are open at the time.  The tab screens captured by default are:

- Monthly Utility Data

- Utility Rate Data

- Miscellaneous Input Information

- Energy Plots

- Summary of Results

- Comparison of Methods

This command can be invoked by using the menu directly or by pressing “Ctrl” and “H” keys together. The screen shots are stored in The HUD CHP Tool opens a Word document named “ScreenShots.DOC” in the currently active folder or subdirectory and places each screen shot into separate paragraphs. Word is left open, but it is “minimized” to an icon on the Windows Taskbar (Figure 9):

Figure 9 — Windows Taskbar showing ScreenShots.doc task item.

Clicking on the mouse on the Word task item on the Windows Taskbar (circled in red above) restores the Word window to the computer display (Figure 10).  The screen images in the Word file can be copied into other Windows applications using the “Cut” and “Paste” commands or left in the Word file (it is recommended that the user use the “File, Save As” commands in Word to save the file with a new file name since “ScreenShots.doc” will be reused by the HUD CHP Tool each time the “Capture Screen Shot” command is invoked and any old data will be overwritten).

Figure 10 — ScreenShots.doc Word window restored to working size with first captured screen shots.

## Print Options Form under File Menu

There are five options for printing that are selected from a form, as shown in Figure 11.  They enable the user to limit the printing to the input data and summary results or to choose the details of the three Methods. They are illustrated using the Sample Data, a composite created from several sources.  A printout of the sample input data and Summary of Results from those data are shown next.

HUD CHP Feasibility Screening Tool

<< Sample Data >>

Electricity

--------------------------        #2 fuel oil                 Fuel #2

Power  Demand              -----------------------  -----------------------

Month               kWh     kW       Cost     gallons         Cost      therms       cost

January          68,400    138      $8,058     27,979       $68,548

February         67,800    132      $7,980     25,326       $62,053

March            57,000    132      $6,709     29,645       $72,630

April            56,400    126      $6,638     16,939       $41,500

May              57,600    150      $6,674      7,390       $18,105

June            117,600    400     $13,842      6,797       $16,992

July            138,000    432     $16,242      5,532       $13,553

August          136,800    402     $16,101      4,722       $11,569

September        90,600    276     $10,663      6,405       $15,692

October          61,200    174      $7,203     12,761       $31,264

November         63,600    138      $7,486     15,407       $37,747

December         69,000    138      $8,121     24,922       $61,059

----------------------------------------------------------------------------------------------

Annual Total    984,000           $115,717    183,827      $450,712

Average Cost                        $0.118                   $2.452

Electric Utility Rate Data

Energy Charge                $0.0444/kWh                Natural Gas Utility Rate Data

Fuel Adjustment Charge       $0.0733/kWh                   cost of gas $1.3119/CCF

Demand Charge                  $0.00/kW/month

Standby Charge                 $0.00/kW/month

Location: Philadelphia, Pennsylvania

Building Specifications:                                    Equipment Specifications:

heated floor space            98,000 sq ft                   recip-engine driven generator

air conditioned floor space   98,000 sq ft                   typical installation costs

approx. number of occupants      200                         low hot water usage

Results:

1. Recovered Heat for Domestic Hot Water Only (Loads Estimated from Utility Bills)

a. simple payback of 5.4 years

b. potable hot water load estimated from summer fuel consumption

c. generator sized to meet potable hot wate4r loads operating 7,440 hours/year

d. 107 kW recip-engine generator

2. Recovered Heat for Heating, Air Conditioning and

Domestic Hot Water (Loads Estimated from Utility Bills)

a. simple payback of 6.0 years

b. space heating, cooling, and potable hot water loads estimated

from monthly power and fuel consumption

c. generator sized to meet heating, cooling, and hot water loads operating

6,570 hours/year

d. 110 kW recip-engine generator

3. Recovered Heat Used for Heating, Air Conditioning, and Domestic Hot Water

(Space Conditioning Loads Estimated from EIA Degree-Day Algorithms and

Hot Water Use Estimated from ASHRAE Publications)

a. simple payback of 8.3 years

b. space heating and cooling estimated using heating and cooling degree days

for Philadelphia, Pennsylvania using EIA algorithms

c. potable hot water load estimated using high hot water usage for multifamily

ground and hot water tank temperatures of 54.1 F and 140.0 F

d. generator sized to meet heating, cooling, and potable hot water loads

operating 6,570 hours/year

e. 51 kW recip-engine generator

### Print:  Side-By-Side Comparison of Results

Selecting the “Side-By-Side Comparison of Results for all Three Methods” option on the “Print Options” form, as shown in Figure 11 causes the results below to be sent to the computer default printer when the Print button is clicked.

HUD CHP Feasibility Screening Tool

Sample Data

Comparison of Loads and CHP System Information for Alternative Calculational Procedures:

Method 1        Method 2        Method 3

1. Service Hot Water Load                      7,607           7,607           1,874 MMBtu

2. Space Heating & Hot Water Load                             11,281           2,385 MMBtu

3. Space Cooling Load                                          2,756           1,909 MMBtu

4. Total Thermal Load                          7,607          21,643           6,618 MMBtu

5. Generator Capacity                            107             110              51 kW

6. Operating Time                              7,440           6,570           6,570 hours

7. Power Output                              799,014         729,000         331,790 kWh

8. Recovered Heat                              4,451           4,040           2,068 MMBtu

9. Installed Cost                           $200,992        $203,718        $141,471

10. Annual Operating Savings                  $37,377         $34,001         $16,963

11. Simple Payback                                5.4             6.0             8.3 years

### Print:  Method 1 Intermediate Results

Selecting the “Method 1 Intermediate Results” option on the “Print Options” form (refer to Figure 11) causes the results shown below to be sent to the computer default printer.

HUD CHP Feasibility Screening Tool

<< Sample Data >>

Details of Method 1 Calculations:

1. Cogeneration System Description

a. generator capacity                                           107 kW

b. generator heat rate (29.7% LHV)                           11,474 Btu/kWh

c. generator heat recovery rate                               5,571 Btu/kWh

d. annual operating time                                      7,440 hrs

Baseline                    107 kW

2. Power Consumption                    System              Recip-Engine CHP

a. utility power                     984,000                184,986 kWh

b. on-site generation                      0                799,014 kWh

c. total power consumed              984,000                984,000 kWh

d. approx. cost

(1) energy & fuel adj chg        $115,817                $21,773

(2) demand & standby charges           $0                     $0

(3) total approx. cost           $115,817                $21,773

3. Water Heater Summary

a. hot water load                      7,607                  7,607 MMBtu

b. recovered heat                          0                 -4,451 MMBtu

-----------------------       -----------               --------

c. net water heater output             7,607                  3,155 MMBtu

d. estimated fuel consumption         10,142                  4,207 MMBtu

4. Fuel Consumption

a. water heater                       10,142                  4,207 MMBtu

b. generator                               0                  9,168 MMBtu

------------------------      -----------               --------

c. total fuel consumption             10,142                 13,375 MMBtu

d. approx. cost                     $136,646               $180,199

5. Annual Operating Cost

a. purchased electricity            $115,817                $21,773

b. natural gas                      $136,646               $180,199

c. gen-set O&M                            $0                $13,113

------------------------     ------------              ---------

d. total operating cost             $252,462               $215,085

e. annual operating savings (loss)                          $37,377

6. Simple Payback

a. estimated gen-set installed cost                        $200,992

b. annual operating savings (loss)                          $37,377

c. simple payback                                               5.4 yrs

Method 1 Assumptions & Methodology

------------------------------------

1. Hot Water Heater Uses Fossil Fuel(s)

a. cost of fuel #1 and fuel #2 used to estimate annual cost of heating water

b. fuel consumption figures used only to calculate average cost of fuel as

a quick visual check of the data

2. Electrical Power Consumption and Monthly Peak Demand Data

a. used in sizing generator, efficiency, and heat recovery

b. monthly cost data only used to compute average cost of power as a quick visual check

3. Electric and Natural Gas Utility Data

a. used to estimate cost of operating generator

b. used to estimate avoided cost of purchased cost of electricity

### Print:  Method 2 Intermediate Results

HUD CHP Feasibility Screening Tool

<< Sample Data >>

Details of Method 2 Calculations (priority use of recovered heat to heating):

Generator Parameters:                  Simple Payback:

capacity                 110 kW        baseline operating cost           $455,125

equipment cost        $1,294/kW        CHP operating cost                $421,124

installation cost       $558/kW        annual operating savings/losses    $34,001

total installed cost  $1,852/kW        CHP system capital cost           $203,718

simple payback                        5.99 years

-------------------------------------------------------------------------------------------

Minimum Simple Payback Occurs for:

a. generator capacity         110 kW

b. heat & hot water load      485 MMBtu

c. space cooling load         881 MMBtu

Gen-Set   Total    Total     Total    Total    Total    Total     Total    Simple

Capacity    Cost     Cost      Cost     Cost     Cost     Cost     Annual   Payback

kW     Jan-Feb   Mar-Apr  May-Jun  Jul-Aug  Sep-Oct  Nov-Dec     Cost     years

------------------------------------------------------------------------------------

0   $114,425  $99,332  $46,807  $51,271  $53,244  $90,046  $455,125    999.0

12   $113,607  $98,514  $45,990  $50,453  $52,426  $89,229  $450,219     20.7

25   $112,926  $97,833  $45,308  $49,772  $51,744  $88,547  $446,129     12.7

37   $112,278  $97,185  $44,660  $49,124  $51,096  $87,899  $442,243      9.9

49   $111,649  $96,556  $44,031  $48,494  $50,467  $87,270  $438,467      8.4

62   $111,031  $95,939  $43,414  $47,877  $49,850  $86,653  $434,764      7.5

74   $110,423  $95,330  $42,805  $47,269  $49,242  $86,044  $431,113      6.9

87   $109,821  $94,728  $42,204  $46,667  $48,640  $85,443  $427,502      6.5

99   $109,225  $94,132  $41,607  $46,070  $48,043  $84,846  $423,923      6.2

111   $108,632  $94,043  $41,225  $45,478  $47,493  $84,254  $421,124      6.0

124   $108,127  $94,088  $40,953  $44,889  $47,223  $83,915  $419,194      6.1

136   $108,174  $94,127  $40,680  $44,303  $46,951  $83,960  $418,195      6.3

148   $108,215  $94,161  $40,406  $43,720  $46,678  $84,000  $417,180      6.4

161   $108,251  $94,192  $40,131  $43,139  $46,403  $84,036  $416,152      6.6

173   $108,284  $94,219  $39,855  $42,847  $46,399  $84,068  $415,671      6.8

185   $108,313  $94,243  $39,578  $42,814  $46,432  $84,096  $415,477      7.1

198   $108,340  $94,266  $39,302  $42,777  $46,461  $84,122  $415,267      7.4

210   $108,364  $94,286  $39,024  $43,146  $46,488  $84,146  $415,454      7.8

223   $108,386  $94,304  $39,040  $43,631  $46,513  $84,167  $416,042      8.2

235   $108,407  $94,321  $39,066  $44,108  $46,536  $84,187  $416,626      8.7

247   $108,426  $94,337  $39,090  $44,525  $46,557  $84,206  $417,141      9.1

Baseline Operating Cost:                  $455,125

Minimum CHP Operating Cost:               $421,124

CHP Annual Savings:                        $34,001

Minimum Simple Payback:                        6.0 years

Monthly On Site Generation:                 62,100 kWh

Annual On Site Generation (75% run time):  731,177 kWh

“Ideal” Generator Capacity:                    111 kW

### Print:  Method 3 Intermediate Results

HUD CHP Feasibility Screening Tool

<< Sample Data >>

Details of Method 3 Calculations:

For Philadelphia, Pennsylvania there are:

5,151 heating degree days

1,188 cooling degree days

and the average temperature is 54.1 F

Air conditioning consumes 0.974 kWh/sq ft per year

and space heating consumes 38,570 Btu/sq ft per year

Estimated annual thermal loads:

a. space heating                                   2,835 MMBtu

b. air conditioning (95,468 kWh)                   1,909 MMBtu

c. potable hot water                               1,874 MMBtu

d. total thermal load                              6,618 MMBtu

CHP System

a. generator capacity                                 51 kW

b. heat rate                                      11,907 Btu/kWh

c. heat recovery rate                              6,234 Btu/kWh

d. CHP system installed cost                      $2,801/kW

e. generator O&M cost                             $0.019/kWh

CHP System Economics

a. electricity                  Baseline           CHP

1. non-cooling power          346,920         346,920 kWh

2. cooling power               95,468          95,467 kWh

3. total power consumed       442,388         442,387 kWh

4. on site generation               0         331,790 kWh

5. utility power              442,338         110,597 kWh

b. natural gas

1. space heating                3,779           3,520 MMBtu

2. potable hot water            2,498               0 MMBtu

3. generator fuel                   0           3,950 MMBtu

4. total fuel consumed          6,277           7.470 MMBtu

c. operating costs

1. utility power              $52,069         $13,017

2. natural gas                $82,924         $98,684

3. generator O&M                   $0          $6,329

4. total operating cost       $134,993       $118,030

d. simple payback                                   8.34 years

Space Heating Summary                               Hot Water Summary

a. load                            2,835 MMBtu      a. load                            1,874 MMBtu

b. recovered heat                    195 MMBtu      b. recovered heat                  1,874 MMBtu

c. boiler load                     2,640 MMBtu      c. water heater load                   0 MMBtu

d. boiler fuel                     3,520 MMBtu      d. water heater fuel                   0 MMBtu

Space Cooling Summary

a. chilled water load              1,146 MMBtu

b. thermal input                   1,909 MMBtu

c. recovered heat                      0 MMBtu

d. absorption chiller output           0 MMBtu

e. electric chiller load           1,146 MMBtu

f. cooling power                  95,468 kWh

HUD CHP Feasibility Screening Tool

<< Sample Data >>

Method 3 Assumptions & Methodology:

1. Space Heating and Cooling loads computed using EIA algorithms based on Heating

and Cooling Degree Days

2. Domestic Hot Water loads computed from hot water consumption reported in ASHRAE

and average annual temperature for the location

3. The generator is sized to provide 3/4 of the annual power consumption with

a fraction of run time of 75%. It is assumed that peak power demand occurs during

the time when the remaining 1/4 of the power is consumed.

4. Heat recovered from the generator is allocated to thermal loads to domestic

(potable) hot water, space heating, and space cooling, in that order.

5. Ideally, there should be an iteration on generator capacity. This is not

necessary as long as the application is limited by the electrical loads. If

the thermal loads constrain the analysis, the cooling power listed in the

box above will be different than the cooling power listed in line 2 to the

left. The control logic has not been developed to iterate on the

generator capacity until the cooling power in line 2 equals the power

required by electric air conditioners supplementing the absorption chiller

(the cooling power listed above).

## Data Menu

The “Data Menu” can be used to clear the form so new data can be entered (identical action as “File” “New”) or to fill in the form with a sample set of data. The “Alt” key works as it does in the file menu with “Alt-D” displaying the data menu, “Alt-D-C” clearing the form, and “Alt-D-D” filling in entries for a sample data set.

The user should be aware of the fact that the sample data provided is not particularly current and the results will appear more attractive than are likely with current utility costs, particularly for natural gas.

Figure 12 — Data menu items.

## Help Item

The “Help” item is currently disabled, which allows revisions to the compiled HELP file outside of re-installing the tool.  The compiled HELP file should be downloaded separately (see the website), and it should run all by itself in a separate window.  The compiled HELP file is similar to this manual.

Figure 13 — Help item does not function.

# Electric Generation and Prime Movers

CHP systems primarily consist of an engine-driven generator and heat recovery equipment. The system can include an absorption chiller that uses recovered heat to produce chilled water for air conditioning.  Several types of equipment can be used to produce electricity:

- reciprocating engines

- gas turbines

- microturbines

- fuel cells

Electric power produced is usually consumed on site, although in some circumstances it is economical to produce power that is exported to the utility grid (though many prospective users would like to sell power to the grid this is rarely in their best interest with utilities buying power only at their own avoided cost).

Reciprocating engines and gas turbines are established technologies for on site power generation and CHP. Microturbines have been commercially available since the late 1990’s with several thousand units installed and operating.  Fuel cells have attracted a great deal of attention as candidate systems for on site power generation, but as of 2005 there are few products on the market and installations number in the dozens instead of hundreds or thousands. Fuel cells remain the most expensive option for on-site generation and CHP, and are not covered in this manual, although they can still be selected as a system in the tool if one wants to see some cost or other data displayed (paybacks are often negative or thousands of years).

## Reciprocating Engine Generators

Natural gas-fired reciprocating engines dominate the market for small on-site generators and CHP systems. While microturbines may appear a more glamorous technology, recips churn along as the established player in these applications, with low cost, high efficiency, and long durability.  Also, gas turbines are only for larger applications (1,000 kW or more).

### Equipment Cost

Correlations were developed based on data for generator cost (equipment only), typical installation cost, operating and maintenance (O&M) costs, efficiency, and heat recovery in the U.S. DOE Office of Energy Efficiency and Renewable Energy report Gas-Fired Distributed Energy Resource Technology Characterizations, NREL-TP-620-34783, 2003 (EERE report cited in the rest of this section). Equipment costs are very nearly linear in absolute terms, as shown by the blue dashed lines in Figure 14, but highly non-linear in terms of cost per unit capacity. There is a strong economy of scale favoring larger units.  The portion of the figure on the left expands the scale for 0 – 300 kW.

Figure 14 — Reciprocating engine generator equipment cost, two scales.

### Installation Cost

Installation costs of any CHP system will be highly dependent on site-specific factors with any retrofit installation being much more difficult and costly than systems put into new construction of buildings designed to use CHP. Difficult installations can cost 2.5 times easy installations, or more. That being said, the EERE report cites installation costs for reciprocating-engine based CHP systems at 17% of the total installed cost. This fraction is lower than values cited in many other sources and has been associated with the “Low” setting under “Installation Costs” on the “Intermediate Information” tab. Values of 25%, 50%, and 100% are associated with the “Typical,” “High,” and “Retrofit” selections of “Installation Costs” for reciprocating engine CHP systems.

### Heat Rate and Efficiency

The same source was used to correlate engine efficiency in terms of the fuel requirements. The natural gas consumed per unit of power generated, the heat rate (Btu/kWh, HHV), was correlated against the engine capacity. As illustrated by the blue dashed line in Figure 15, less fuel is consumed per unit of output as generator capacity increases. In other words, larger generators are typically more efficient than smaller ones (red line).

### Heat Recovery

Data from the EERE report were also used to correlate engine heat recovery against generator capacity. Graphs from this correlation are shown in Figure 16 with the blue line indicating the heat recovery rate (Btu/kWh generated per hour) and the red line the absolute recovered heat (Btu). Although more heat is available from larger generators, since they are also more efficient less heat can be recovered per unit of power output. Heat recovery rate declines as capacity increases.

### Operating and Maintenance Costs

Finally, the EERE report was used to correlate O&M costs against generator capacity. A graph from this correlation is shown in Figure 17 with the blue line indicating that non-fuel operating costs decline as generator capacity increases. This results from fixed maintenance costs being prorated over a greater quantity of power output.

## Gas Turbine Generators

Natural gas-fired combustion gas turbines can be used in larger on-site generation and CHP applications. These machines resemble jet engines used on civilian and military aircraft, though they have been designed for optimal torque and durability instead of maximum thrust and low weight. Electrical capacities of gas turbine generators range from about 750 kW to 40 MW, with only the smallest machines being appropriate for most commercial building and residential applications. Gas turbines typically have lower efficiencies than reciprocating-engine driven generators, though they also have lower maintenance costs and greater potential for waste heat recovery.

### Equipment Cost

Correlations were developed based on data for generator cost (equipment only), typical installation cost, operating and maintenance (O&M) costs, efficiency, and heat recovery in the EERE report.  Equipment costs are very nearly linear in absolute terms, as shown by the blue dashed line in Figure 18, but highly non-linear in terms of cost per unit capacity. There is a strong economy of scale favoring larger units.

### Installation Cost

The EERE report cites installation costs for gas turbine based CHP systems at 15% of the total installed cost. This fraction is lower than values cited in many other sources and has been associated with the “Low” setting under “Installation Costs” on the “Intermediate Information” tab. Values of 25%, 50%, and 100% are associated with the “Typical,” “High,” and “Retrofit” selections of “Installation Costs” for gas turbine CHP systems.

### Heat Rate and Efficiency

The same source was used to correlate turbine efficiency in terms of the fuel requirements. The natural gas consumed per unit of power generated, the heat rate (Btu/kWh), was correlated against the engine capacity. As illustrated by the blue dashed line in Figure 19, less fuel is consumed per unit of output as generator capacity increases. In other words, larger generators are typically more efficient than smaller ones (red line).

### Heat Recovery

Data from the EERE report were also used to correlate engine heat recovery against generator capacity. Graphs from this correlation are shown in Figure 20 with the red line indicating the absolute heat recovery rate (millions of Btu’s per hour) and the dashed blue line the recovered heat per unit of power generated (Btu/kWh). Although more heat is available from larger generators, since they are also more efficient, less heat can be recovered per unit of power output. Heat recovery rate declines as capacity increases.

### Operating and Maintenance Costs

Finally, the EERE report was used to correlate O&M costs against generator capacity. A graph from this correlation is shown in Figure 21 with the blue line indicating that non-fuel operating costs decline as generator capacity increases. This results from fixed maintenance costs being prorated over a greater quantity of power output.

## Microturbine Generators

Microturbines are a relatively new generator technology that can be used in small to medium-sized on-site generation and CHP applications. Electrical capacities of microturbines range from 30 to 200 kW. Microturbines typically have lower efficiencies and are expected to have low maintenance costs (since they are fairly new products, microturbines are still establishing a track record for O&M costs and reliability).

### Equipment Cost

Correlations were developed based on data for generator cost (equipment only), typical installation cost, operating and maintenance (O&M) costs, efficiency, and heat recovery in the EERE report.  Equipment costs are very nearly linear in absolute terms, as shown by the dashed blue line in Figure 22, but highly non-linear in terms of cost per unit capacity. There is a strong economy of scale favoring larger units.

### Installation Cost

The EERE report cites installation costs for gas turbine based CHP systems at 18% of the total installed cost. This fraction is lower than values cited in many other sources and has been associated with the “Low” setting under “Installation Costs” on the “Intermediate Information” tab. Values of 25%, 50%, and 100% are associated with the “Typical,” “High,” and “Retrofit” selections of “Installation Costs” for microturbine CHP systems.

### Heat Rate and Efficiency

The same source was used to correlate engine efficiency in terms of the fuel requirements. The natural gas consumed per unit of power generated, the heat rate (Btu/kWh), was correlated against the engine capacity. As illustrated by the dashed blue line in Figure 23, less fuel is consumed per unit of output as generator capacity increases. In other words, larger generators are slightly more efficient than smaller ones (red line).

### Heat Recovery

Data from the EERE report were also used to correlate engine heat recovery against generator capacity. Graphs from this correlation are shown in Figure 24 with the dashed blue line indicating the absolute heat recovery rate (millions of Btu’s per hour) and the red line the recovered heat per unit of power generated (Btu/kWh). Although more heat is available from larger generators, since they are also more efficient, less heat can be recovered per unit of power output. Heat recovery rate declines as capacity increases.

### Operating and Maintenance Costs

Finally, the EERE report was used to correlate O&M costs against generator capacity. A graph from this correlation is shown in Figure 25 with the dashed blue line indicating that non-fuel operating costs decline as generator capacity increases. This results from fixed maintenance costs being prorated over a greater quantity of power output.

# Algorithms and Methodology

The HUD CHP Tool employs three distinctly different algorithms for estimating operating characteristics and economics for CHP systems. “Method 1” allows for use of recovered heat only for producing domestic hot water.  “Method 2” uses a complicated process for sizing a CHP system that uses recovered heat for space heating, domestic hot water and chilled water using an absorption chiller. “Method 3” estimates the annual savings of operating a CHP system that uses a natural-gas driven electric generator with heat recovery for domestic hot water, space heating, and space cooling using an absorption chiller based on published tables rather than utility bills.

## “Method 1” Algorithms

Method 1 estimates the annual savings from operating a CHP system that produces electricity and uses recovered heat for domestic (potable) hot water. It does not incorporate waste heat recovery for either space heating or space cooling needs. Consequently, this method generally results in a smaller generator capacity and a longer simple payback than either Method #2 or Method #3.  Monthly hot water fuel consumption is calculated from the input data for building fuel consumption that the user specified on the “Energy & Utility Data” tab. It is computed as the average of the building fuel consumption for the months May through September as illustrated in Figure 26.

Any fuel consumption in excess of this summertime monthly average is assumed to be for space heating (see Figure 27) and is ignored in the Method 1 analysis.  Water heating fuel consumption is converted to estimated hot water load by multiplying it by a fixed annual boiler efficiency of 62% (there is an implicit assumption that the building contains a hot water or steam boiler that provides both space heating and domestic hot water needs and that there are significant hours at low part load, and consequently low efficiency, operation).  Boiler efficiency can be specified in the “Misc. Input Information” tab though.

Figure 27 — Method 1 heating and hot water fuel breakout.

Method 1 scales the summer hot water load to an annual load (MMBtu) and sizes the generator to provide that amount of recovered heat by operating 7,440 hours per year (generator heat recovery is provided across a range of capacities for reciprocating-engine driven generators, gas turbine generators, microturbines, and fuel cells). Annual costs for electricity and natural gas are calculated using user input data from the utility rate information (i.e. energy charge, fuel adjustment charge, demand charge, standby charge, and cost of natural gas) from the “Energy & Utility Data” tab and monthly peak demand from the monthly utility billing data. Gen-set equipment and operating and maintentance costs (O&M) are provided from the curves shown previously.

Details of the Method 1 analysis can be displayed on a separate “tab” by clicking the box for “Show Details for Method 1” on the “Results” tab of the data interface (Figure 28).

Figure 28 — Method 1 results tab.

## “Method 2” Algorithms

Method 2 allows selection of three end-use heat recovery options:

- Space Heating & Domestic Hot Water Only (No Cooling)

- Heating & Cooling With Priority to Heating

- Heating & Cooling with Priority to Cooling

Hot water fuel can also be specified if multiple fuels are used.  Method 2 is the most complicated.

### Method 2 Assumptions & Methodology:

1. Fuel Use for Space Heating and Hot Water

a. load derived from fuel use input data on “Monthly Utility Data” tab

b. default assumes boiler/water heater efficiency of 62%

c. hot water load set at load for Method 1

2. Space Cooling Load and Energy Use

a. load derived from input data for electrical power use for winter months on

“Monthly Utility Data” tab

b. electrical a/c efficiency assumed to be SEER 12

c. absorption chiller efficiency assumed to be gCOP 0.60 for “low temperature” heat for

recip engines, microturbines, and fuel cells; 1.20 for “high temperature” exhaust from

gas turbines

3. Cost of Power

a. uses specific input data for energy consumption, fuel adjustment charge, demand charge,

and standby charge on “Monthly Utility Data” and “Utility Rate Data” tabs

b. input data for monthly electric bills is not used

c. average cost of power displayed on “Monthly Utility Data” tab is not used

4. Cost of Fuel

a. specific input data for cost of natural gas on “Utility Rate Data” tab is used for

generator fuel

b. either natural gas cost or average cost of Fuel #1 from “Monthly Utility Data” tab is

used for water heater fuel (default is natural gas, selection is made on “Method 2” tab)

5. On-Site Power Generation

a. selected to give lowest simple payback

b. assumes each month has the same generation up to the actual monthly consumption

specified on the “Monthly Utility Data” tab

6. Generator Size & Characteristics

a. sized for 75% on-time by default, user selectable on “Misc. Input Information”

b. cost and performance taken from curve fits

### Method 2 Results

Details of the Method 2 analysis can be displayed on a separate “tab” by clicking the box for “Show Details for Method 2” on the “Results” tab of the data interface, as shown in Figure 29.  The table in the middle of the form contains intermediate results of the calculations for a single month, August, for the first 10 out of 20 or so generator sizes considered. The particular month that is displayed can be changed using the leftmost of the two scroll bars in the upper-right corner of the form.  The range of generator sizes displayed can be changed using the rightmost scroll bar.  The optimum generator size is in bold.

There are several option boxes at the top of the form, and a button labeled “View Payback Graph.”   The “View Payback Graph” button can be used to display a graph showing simple paybacks across a range of generator capacities.  The summary results are displayed in the table at the top of the form.  The options boxes allow specification of recovered heat allocation (top left) and water heating fuel.

Assumptions and methodology items are also displayed in the scroll box at bottom right, except boiler/water heater efficiency and generator runtimes may be different than shown.

Figure 29 — Method 2 results tab.

Each row of the intermediate results table in the middle shows results for a fixed output level from a hypothetical generator, ranging from 0 kWh (i.e. no on-site generation) to the maximum electrical load for any month in the year (from the input data on the “Monthly Utility Data” tab). Corresponding rows for each month of the year are added to create the table at the bottom of the form. Clicking either end of the rightmost scroll bar shifts the rows of this table up or down to see results that are outside the range being displayed. The row of the table that corresponds to the lowest simple payback (i.e. [CHP system equipment + installation cost] ÷ [Baseline Annual Operating Cost - CHP System Annual Operating Cost]) is shown in bold numbers (there is an implicit assumption that generator output is constant from month to month).

The intermediate result columns are:

- a specified generator capacity (column 1)

- the corresponding generator power output for the month (column 2)

- the corresponding amount of recovered heat (column 3) is computed from generator characteristics (Btu/kWh generated) and the assumed gen-set output in column 2

- the amounts of recovered heat allocated to space heating and domestic hot water (column 4)

- the output from a boiler or water heater (column 5)

- recovered heat allocated to an absorption chiller (column 6)

- chilled water produced from a recovered heat “fired” absorption chiller (column 7)

- cooling produced by an electric air conditioning system to meet any load not satisfied by a recovered heat fired chiller (column 8)

- total power consumption (column 11)

- space heating and hot water load is computed from input data for monthly fuel consumption (“Monthly Utility Data” tab) and a fixed boiler efficiency (i.e. 62% as an annual average

- the available recovered heat is allocated between heating and cooling needs (columns 3 and 5 in Fig. 1) with priority given either to heating needs or cooling needs based on the “radio” buttons in the upper left of the form (the display is slightly different if “priority chilled water” is selected):

- recovered heat is given to heat and hot water up to their combined load with anything left over given to an absorption chiller (priority heating) as displayed in Fig. 1.

- recovered heat is given to an absorption chiller up to the amount needed to satisfy the cooling load for that month with anything left over allocated to domestic hot water or heating (priority chilled water); this calculation incorporates assumed efficiencies for both the hypothetical or proposed absorption chiller (0.60 for CHP using generators with reciprocating engines, microturbines, or fuel cells and 1.20 for CHP systems using gas turbines) and the actual electric air conditioners (EER 12).

- water heater output, column 4, is the difference between the hot water load and recovered heat allocated to heating and hot water.

- absorption and electric chiller outputs, columns 7 and 8, are determined from the heat into the absorption chiller and the total cooling load

- electrical power for cooling, column 9, is computed from the necessary electric a/c output using an EER of 12

- non-cooling power, column 10, is set from the input for monthly power consumption

- total power, column 11, and purchased utility power, column 11, are calculated as the sum of cooling power and non-cooling power, and the difference between total power, column 10, and CHP system generator output, column 1

- gen-set fuel, column,13 water heater fuel, colum 14, and total fuel consumption, column 15, are calculated from a curve fit for generator and the assumed boiler efficiency (62%)

- the cost of power, column 16, is computed as the sum of:

- the purchased utility power (column 12) times the electric utility energy charge plus fuel adjustment charge (“Monthly Utility Data” tab),

- the demand charge times the monthly peak electrical demand (“Monthly Utility Data” tab) less the generator electrical capacity, and

- the standby charge (“Monthly Utility Data” tab) times the generator capacity.

- the cost of fuel, column 17, is computed using generator (column 13) and water heater (column 14) fuel consumption, input data for the cost of natural gas (“Monthly Utility Data” tab) for generator fuel consumption and either the average annual cost of fuel #1 (“Monthly Utility Data” tab) or the cost of natural gas for water heater fuel depending on the choice for water heater fuel (“radio” button next to choices for recovered heat allocation.

- total utility cost, column 18, is the sum of the cost of power and cost of fuel (columns 16 and 17)

- genset O&M cost is the generator power output (column 2) times the gen-set O&M rate ($/kWh generated)

- monthly operating cost, column 19, is the sume of total utility (i.e. energy) costs and gen-set O&M costs

CHP equipment cost is computed from the generator capacity (column 1) and curve fits for equipment and installation costs as functions of generator size (e.g. Reciprocating Engine Generators).

## “Method 3” Algorithms

Method 3 estimates the annual savings of operating a CHP system that uses a natural-gas driven electric generator with heat recovery for domestic hot water, space heating, and space cooling using an absorption chiller. Heating, cooling, and hot water loads are estimated from published tables and algorithms; the monthly table of electric and gas utility billing information on the “Energy & Utility Data” tab are not used except for calculating electric utility peak demand charges, so Method 3 results can be generated more easily and for a proposed design (and without monthly utility data, only rate data).

End-use calculations are based on the following references:

- space heating gas consumption: 2001 RECS, Table CE2-1c. Space-Heating Energy Consumption in U.S. Households by Climate Zone

- space cooling power consumption: 2001 RECS, Table CE3-1c. Electric Air Conditioning Energy Consumption in U.S. Households by Climate Zone

- non-cooling power: Ritschard, R.L., Huang, Y.J., and Fay, J.M., “Estimating Water Heating and Aggregate Electricity Loads in Multifamily Buildings,” ASHRAE Transactions 1990, Volume 96, Part 1, p. 799.

- hot water consumption: Goldner, F.S., “DHW System Sizing Criteria for Multifamily Buildings,” ASHRAE Transactions 1994, Volume 100, Part 1, p. p74.

Source:  2001 RECS refers to the 2001 Consumption and Expenditures Tables, Residential Energy Consumption Surveys, available as PDF documents from the US Dept of Energy, Energy Information Administration website:

(main current URL: http://www.eia.doe.gov/emeu/recs/contents.html)

(2001 RECS CE URL:  http://www.eia.doe.gov/emeu/recs/recs2001/detailcetbls.html)

(CE2-1c table URL: ftp://ftp.eia.doe.gov/pub/consumption/residential/2001ce_tables/spaceheat_consump2001.pdf)

(CE3-1c table URL: ftp://ftp.eia.doe.gov/pub/consumption/residential/2001ce_tables/ac_consump2001.pdf)

Baseline energy consumption for space heating is calculated using an algorithm derived by the U.S. Department of Energy from the 2001 RECS. Space heating “intensity” is correlated against heating and cooling degree days (HDD and CDD) and climate zone for several different types of space heating fuel. The correlations are summarized in the table below. Fuel use per 1000 sq feet of heated floor space is computed using input data for the building location and heated floor space on the “Intermediate Information” tab. Fuel use converted to annual heating load assuming a fixed boiler efficiency of 62%. The domestic hot water load is computed using data published by ASHRAE. Non-cooling electric loads are set to 3.54 kWh/yr/sq ft of heated floor space, with the floor space taken from the user specified input data on the “Intermediate Information” tab. Reference information:

| RECS 2001 Table CE2-1c. Space-Heating Energy Consumption in U.S. Households by Climate Zone |
| --- |
| Space-Heating Intensity, Where the Main Space-Heating Fuel Is: | Fewer than 2,000 CDD and -- | 2,000 CDD or More and Fewer than 4,000 HDD |
|  | More than 7,000 HDD | 5,500 to 7,000 HDD | 4,000 to 5,499 HDD | Fewer than 4,000 HDD |  |
|  | Space-Heating Intensity [PU÷{HDDx(HSF÷1000)}] |
| Electricity (kWh) Natural Gas (cubic feet) Fuel Oil (gallons) Kerosene (gallons) LPG (gallons) | 0.766 4.479 0.041 0.046 0.061 | 0.717 6.222 0.044 Q 0.066 | 0.834 8.291 0.051 Q 0.080 | 0.864 8.951 Q 0.046 0.099 | 0.998 8.969 Q Q 0.104 |
| Q = Data withheld because either the Relative Standard Error (RSE) was greater than 50% or fewer than 10 households were sampled. |

As an example, Albany, New York typically has 7,005 heating degree days (HDD) and 776 cooling degree days (CDD) per year. Consequently, for a building with 98,000 sq feet of heated space:

Natural Gas Consumption (cu ft) ÷ {7,005 HDD x (98,000 sq ft/1,000)} = 4.479

Natural Gas Consumption (cu ft) = 4.479 x 7,005 HDD x (98,000 sq ft/1000 sq ft) = 3,075,000 cu ft

Natural Gas Consumption = 3,075,000 cu ft x 1,027 Btu/cu ft x (1 MMBtu/1,000,000 Btu) = 3,158 MMBtu

Air-conditioning energy is also calculated using an algorithm published by the U.S. Department of Energy. Air-conditioning “intensity” is correlated against heating and cooling degree days (HDD and CDD) for central and room air-conditioners as summarized in the table below. Annual power consumption is determined using input data for the location and heated and air-conditioned floor space specified on the “Intermediate Information” tab. The annual cooling load is calculated assuming an electric air-conditioner EER of 12 Btu/Wh.

| 2001 RECS Table CE3-1c. Electric Air-Conditioning Energy Consumption in U.S. Households by Climate Zone, 2001 |
| --- |
| Space-Heating Intensity, Where the Main Space-Heating Fuel Is: | Fewer than 2,000 CDD and -- | 2,000 CDD or More and Fewer than 4,000 HDD |
|  | More than 7,000 HDD | 5,500 to 7,000 HDD | 4,000 to 5,499 HDD | Fewer than 4,000 HDD |  |
|  | Air-Conditioning Intensity [kWh÷{CDDx(CSF÷1000)}] |
| Electric Air Conditioning Central Air-Conditioning Room/Wall Air-Conditioning | 0.80 0.78 0.85 | 0.78 0.78 0.75 | 0.81 0.82 0.77 | 0.88 0.85 1.07 | 0.90 0.90 0.79 |

Continuing the Albany example:

Central Air Conditioning Power (kWh) ÷ {776 CDD x (98,000 sq ft/1,000 sq ft)} = 0.78

Central Air Conditioning Power (kWh) = 0.78 x {776 CDD x (98,000 sq ft / 1,000 sq ft)} = 59,320 kWh

Annual Air Conditioning Load (ton-hrs) = 59,320 kWh x 12 Btu/Wh x 1,000 Wh/kWh ÷ 12,000 Btu/ton-hr = 59,320 ton-hrs

Results of the Method 3 and intermediate calculations are displayed on the “Method 3” results tab (Figure 30). The text box can be used to change the default “Central A/C” selection to “Room/Wall A/C” to select a different row of air-conditioning intensity values for the calculations. Space heating calculations are performed using the row of space heating intensity factors for natural gas.

Method 3 is based on simplified estimating calculations, so calculated savings and simple paybacks for Method 3 can be more inaccurate in some cases where the “averaging” assumptions do not represent the building well.  Method 3 is more suited to quick, conceptual scoping estimates when energy data are not yet available.

Figure 30 — Method 3 results tab.

### Details of Method 3 Calculations using the Sample Data:

For Philadelphia, Pennsylvania there are:

5,151 heating degree days

1,188 cooling degree days

and the average temperature is 54.1 F

Air conditioning consumes 0.974 kWh/sq ft per year

and space heating consumes 38,570 Btu/sq ft per year

Estimated annual thermal loads:

a. space heating                                   2,835 MMBtu

b. air conditioning (95,468 kWh)        1,909 MMBtu

c. potable hot water                             1,874 MMBtu

d. total thermal load                            6,618 MMBtu

CHP System

a. generator capacity                                 51 kW

b. heat rate                                      11,907 Btu/kWh

c. heat recovery rate                              6,234 Btu/kWh

d. CHP system installed cost                      $2,801/kW

e. generator O&M cost                             $0.019/kWh

CHP System Economics

a. electricity                 		 Baseline           CHP

1. non-cooling power          	346,920         346,920 kWh

2. cooling power               	  95,468           95,467 kWh

3. total power consumed       	442,388         442,387 kWh

4. on site generation               	          0          331,790 kWh

5. utility power              	442,338         110,597 kWh

b. natural gas

1. space heating                	    3,779           3,520 MMBtu

2. potable hot water            	    2,498                  0 MMBtu

3. generator fuel                    	           0           3,950 MMBtu

4. total fuel consumed          	    6,277           7.470 MMBtu

c. operating costs

1. utility power              	  $52,069         $13,017

2. natural gas                	  $82,924         $98,684

3. generator O&M                              $0           $6,329

4. total operating cost       	$134,993       $118,030

d. simple payback                          		      8.34 years

Space Heating Summary                               Hot Water Summary

a. load                                 2,835 MMBtu      a. load                                   1,874 MMBtu

b. recovered heat                    195 MMBtu      b. recovered heat                  1,874 MMBtu

c. boiler load                       2,640 MMBtu      c. water heater load                     0 MMBtu

d. boiler fuel                        3,520 MMBtu      d. water heater fuel                     0 MMBtu

Space Cooling Summary

a. chilled water load              1,146 MMBtu

b. thermal input                     1,909 MMBtu

c. recovered heat                          0 MMBtu

d. absorption chiller output          0 MMBtu

e. electric chiller load            1,146 MMBtu

f. cooling power                   95,468 kWh

### Method 3 Assumptions & Methodology Applied to the Sample Data

1. Space Heating and Cooling loads computed using EIA algorithms based on Heating and Cooling Degree Days

2. Domestic Hot Water loads computed from hot water consumption reported in the ASHRAE papers cited above, and average annual temperature for the location

3. The generator is sized to provide 3/4 of the annual power consumption with a fraction of run time of 75%. It is assumed that peak power demand occurs during the time when the remaining 1/4 of the power is consumed. (Generator runtime can be changed on the “Misc. Input Information” tab.)

4. Heat recovered from the generator is allocated to thermal loads to domestic (potable) hot water, space heating, and space cooling, in that order.

5. Ideally, there should be an iteration on generator capacity. This is not necessary as long as the application is limited by the electrical loads. If the thermal loads constrain the analysis, the cooling power listed in the box above will be different than the cooling power listed in line a.2, CHP System Economics, to the left. The control logic has not been developed to iterate on the generator capacity until the cooling power in line 2 equals the power required by electric air conditioners supplementing the absorption chiller (the cooling power listed above).

# Additional Information on Building Loads

## Electrical & Thermal Loads

The CHP calculations require information about the space heating, hot water, and space cooling loads of the building. The HUD CHP Tool performs three different estimates for CHP using different assumptions about the use of recovered heat and algorithms for estimating these loads. These methods include CHP systems:

- employing recovered heat to produce domestic hot water using the billing information on Energy & Utility Data to estimate monthly and annual hot water loads.

- employing recovered heat for space heating, domestic hot water, and space cooling using the billing information on Energy & Utility Data to estimate monthly and annual hot water loads.

- employing recovered heat for space heating, domestic hot water, and space cooling using information specified by the user on the Intermediate Information tab for the building location, approximate numbers of heated and cooled square feet, the approximate number of people living in the building, and “high,” “medium,” or “low” hot water usage.

Additional information about these calculations is available under the headings for “Electrical Loads” and “Space Heating & Hot Water Loads”.

## Electrical Loads

The power consumption data from the utility bills (see Energy & Utility Data) is used to estimate the air conditioning power consumption and space cooling loads. Figure 31 illustrates how this is done in the HUD CHP Tool. It shows the power consumption for each month with a horizontal line indicating the average power for the winter months.

Figure 31 — Monthly power consumption and average winter power use.

The average power use during the winter is assumed to be almost entirely lighting and plug loads, and does not include any power for air conditioners. The plug and lighting loads are assumed to be constant throughout the year, so any electrical use during the summer months in excess of this average is for air conditioning. This is illustrated in Figure 32.

Figure 32 — Breakout of air conditioning energy.

Air conditioning power consumption is converted to monthly air conditioning loads by multiplying the power use by an assumed air conditioning efficiency (EER) of 12 Btu/kWh. The loads in millions of Btu’s per month are needed in order to estimate recovered heat requirements of an absorption chiller to provide air conditioning. An absorption chiller uses heat, instead of electrical energy, to produce 44°F water for space cooling. CHP systems using reciprocating-engine or microturbine generators or fuel cells produce low grade waste heat that can drive an absorption chiller with a COP of 0.60; gas turbines have much higher exhaust gas flows and temperatures and can operate chillers with COPs of 1.20.

## Space Heating & Hot Water Loads

Space heating and hot water loads are also estimated using the data on the Energy & Utility Data data form.  (See figures 26 and 27).

The HUD CHP Tool allows for use of up to two different fuels (e.g. natural gas and #2 fuel oil). Each value is converted from its customary units of measure (e.g. gallons, thousands of cubic feet) to millions of Btu’s using the appropriate conversion factors. The two values are added for each month to get a total “thermal” consumption and converted to heating and hot water loads by multiplying by the annual boiler efficiency (default of 60%, which includes distribution and standby losses).  Boiler annual efficiency can be set on the “Misc. Input Information” tab.

## Map of EIA Climate Zones for 2001 RECS

# Text boxes

Figure 3 — Miscellaneous input information.

Figure 11 — Side-By-Side option on Print Options form.

Figure 7 — Main menu at upper left of tool window.

Figure 8 — File menu items.

Figure 16 — Heat recovery for reciprocating engine generators

Figure 15 — Reciprocating engine HHV heat rate and efficiency.

Figure 17 — Reciprocation engine generator O&M costs

Figure 18 — Gas turbine equipment cost.

Figure 19 — Gas turbine HHV heat rate and efficiency.

Figure 20 — Gas turbine heat recovery.

Figure 21 — Gas turbine O&M costs.

Figure 22 — Microturbine equipment costs.

Figure 23 — Microturbine HHV heat rate and efficiency.

Figure 24 — Microturbine heat recovery.

Figure 25 — Microturbine O&M costs, $/kWh

Figure 26 — Hot water estimate from Summer months.