## User Interface
Simple Payback: Atlanta Metropolitan Area
Synopsis: Paybacks are relative to fossil fuel-fired space heating and hot water. Energy costs are $0.060/kWh for electricity and $7.60/MMBtu for fuel for a spark spread of $10.12/MMBtu. Results are based on 1 gas turbine generator(s) totaling 5,200 kW at a cost of $1,427 / kW, total installed cost is $1,622 / kW including absorption chillers (if any) and cost adjustment factors. O&M costs are $0.008 /kWh, standby charges of $24/kW and export rate of $0.025/kWh; 100% of generated power is used on site and the balance, if any, is exported. Net operating savings are -$0.011/kWh. Absorption chillers (2,500 tons) use 100% of recovered heat at a gCOP of 1.20 and cost of $405/ton in place of electric chilled water at 0.85 kW/ton. Other operating parameters include a generator heat rate of 11,378 Btu/kWh, heat recovery rate of 4,912 Btu/kWh and; boiler efficiency of 72%. There are 8,424 operating hours per year. Waste heat is used for space heating and hot water (0.0%), chilled water (100.0%), and desiccant regeneration (0.0%). Simple payback is -17.2 years with a financed payback at 6.00% of -12.2 years.
Conversion Factors for Solid Fuels: Btu / lb ton coal / ton alt. 1. Wood a. bone dry 7,600 - 9,600 0.58 - 0.73 b. air dry, 20% moisture 6,400 0.49 2. Agricultural Residues 4,300 - 7,300 0.33 - 0.56 3. Charcoal 12,800 0.97 4. Coal a. default data 13,130 1.00 b. lignite 11,500 -13,000 0.88 - 0.99 c. sub-bituminous 6,500 - 8,200 0.50 - 0.62

## Data
"Energy" |  |  | "System" |  |  |  | "Indices" |  |  | "Results" |  |  | "Chillers and Fuel Cells" |  |  | "Misc." |  |  | "Graph" |  |  |  | Desiccant Data |  |  |  | Rules of Thumb:
Site Name: | Atlanta Metropolitan Area |  | Number of Generators: | 1 |  |  | Derived Information: |  |  | Computed Results |  |  | Type of Chiller |  |  | Assumptions |  |  | Alternative Energy Costs |  |  |  | Reference Electric Dehumidifier
[7 empty] | a. average cost of electricity | 0.060485 | / kWh | a. CHP Capacity | 5200 | kW | a. no absorption chiller |  |  | a. standby charges | 24 | per kW / year | a. cost of electricity |  | / kWh |  | a. Power | 17990 | W
Electricity Data |  |  | Generator Capacity: | 5200 | kW |  | b. average electric demand | 3542.8572 | kW | b. approximate cost | 8432900 |  | b. absorption chiller | X |  | b. price for exported power | 0.025 | / kWh | b. cost of fuel |  | / MMBtu |  | b. Air Flow Rate | 0 | cfm
a. annual cost | 1877184 | [5 empty] | c. average cost of fuel | 7.602 | / MMBtu | c. annual operating savings | -490845.0389 |  |  |  |  | c. fraction of generated power used on site | 100% |  | c. payback information | simple | financed at 6.00% |  | c. Water Removal Rate | 1950 | pints / day
b. annual consumption | 31035429 | kWh | Type of Generator ("GT", "IC", "MT", "FC"): |  |  |  | d. spark spread | 10.12 | / MMBtu | d. CHP savings factor | -0.011205 | / kWh generated | Type of Absorption Chiller |  |  | d. interest rate | 6% |  | (1) 0% waste heat use | -5.2801 | -4.7231 | years
c. summer peak demand | 7300 | kW |  | GT |  |  | e. average to peak electric ratio | 0.48532 |  | e. simple payback using 100% recovered heat |  |  | a. steam-fired single effect |  |  | e. fraction of recoverable heat that is usable | 100% |  | (2) 25% waste heat use | -6.3859 | -5.5667 | years | Reference Desiccant Dehumidifier
d. winter peak demand | 7000 | kW |  |  |  |  | f. average thermal demand | 12.0138 | MMBtu / h | (1) current energy rates | -17.1804 | years | b. steam-fired double effect | X |  | f. alternative waste heat | 75% |  | (3) 50% waste heat use | -8.0776 | -6.7821 | years | a. Power | 4000 | W
|  |  | Electric Load Data: |  |  |  | g. thermal to electric ratio | 0.99356 |  | (2) alternative fuel rate | 7.9914 | years |  |  |  | f. boiler efficiency | 72% |  | (4) 75% waste heat use | -10.9887 | -8.6909 | years | b. Air Flow Rate
Natural Gas Data |  |  | a. average electric load | 3542.8572 | kW |  |  |  |  | f. simple payback using 75% of recovered heat |  |  | Other Data |  |  | g. miscellaneous thermal losses |  | no longer used | (5) 100% waste heat use | -17.1804 | -12.1581 | years | process | 2000 | cfm
a. annual cost | 1111178 |  | b. peak electric load | 7300 | kW |  |  |  |  | (1) current energy rates | -10.9887 | years | a. electric chiller efficiency | 0.85 | kW / ton | h. heat recovery heat exchanger effectiveness |  |  | d. computed parameters |  |  |  | reactivation | 2000 | cfm
b. annual consumption | 1461684 | therms | c. average to peak ratio | 0.48532 |  |  | Value of Recovered Heat: |  |  | (2) alternative fuel rate | 10.8298 | years | b. absorption chiller efficiency | 1.2 |  | i. alternative fuel cost for analysis | 4.5 | / MMBtu | (1) horizontal scroll bar |  |  |  | c. Water Removal Rate
c. consumption units | [6 empty] | space heating |  |  | g. minimum waste heat use for net savings | 144.4% |  | c. fraction of recovered heat used by chiller | 100% |  | j. space heat & hot water | Fossil |  | (a) minimum value | 0 |  |  | inlet humidity | 130 | grains H2O / lb dry air
(1) MMBtu |  |  | Thermal Load Data: |  |  |  | fossil fuel | 0.051864 | / kWh generated | h. fuel cost for 10 year payback at 100% heat use | 4.9253 | / MMBtu | d. cost of absorption chiller | 405 | / ton | Computed / Interpolated Parameters |  |  | (b) maximum value | 2500 |  |  | exit humidity | 92 | grains H2O / lb dry air
(2) therms | X |  | a. average thermal load | 12.0138 | MMBtu |  |  | 10.5584 | / MMBtu | i. electric cost for 10 year payback at 100% heat use | 0.081971 | / kWh | e. cost of fuel cell stack | 1750 | / kW | a. generator heat rate | 11378 | Btu / kWh | (c) current value | 604.852 |  |  | d. Reactivation Energy
(3) thousand cubic feet |  |  | b. average thermal to electric ratio | 0.99356 |  |  | electric heat | 0.12091 | / kWh generated | j financed payback assuming 100% use of waste heat | -12.1581 | years | f. fuel cell stack lifetime | 5 | years | b. CHP installed cost |  |  | (2) vertical scroll bar |  |  |  | regeneration temperature | 190 | °F
[8 empty] | 24.6139 | / MMBtu | Notes |  |  | g. fuel cell availability for stack calculations | 0.96 |  | (1) engine, generator, and HRHX | 1427 | / kW | (a) minimum value | 0 |  |  | inlet temperature | 80 | °F
Other Fuels |  |  | CHP Capacities: |  |  |  | chilled water |  |  | Simple payback using 75% of recovered heat |  |  | h. stack replacement cost | 0.041619 | / kWh | (2) absorption chiller | 194.7115 | / kW | (b) maximum value | 2000 |  |  | heat recovery wheel effectiveness | 0.325
a. fuel oil |  |  | a. total electrical capacity | 5200 | kW |  | single-effect | 0.014732 | / kWh generated | [6 empty] | (3) desiccant dehumidifier | 0 | / kW
(1) annual cost |  |  | b. total thermal capacity | 25.5432 | MMBtu / h |  |  | 2.9991 | / MMBtu |  |  |  | i. maximum absorption chiller capacity | 2554.3166 | tons / generator | (4) miscellaneous other costs | 0 | / kW |  |  |  |  | Specified Desiccant Dehumidifier
(2) annual consumption |  | gallons / year | c. chilled water capacity | 2500 | tons |  | double-effect | 0.025255 | / kWh generated |  |  |  | j. installed absorption chiller capacity | 2500 | tons | (5) subtotal | 1621.7115 |  | Graph Axis Limits |  |  |  | a. Air Flow Rate
b. coal & solid fuels | [7 empty] | 5.1412 | / MMBtu | [6 empty] | (6) multiplier | 1 |  | a. horizontal | 0 | 0.25 | / kWh | process | 0 | cfm
(1) annual cost |  |  | Financial Externalities: |  |  |  | desiccant regeneration | 0 | / kWh generated | [6 empty] | (7) adjusted installed cost | 1621.7115 | / kW | b. vertical | 0 | 20 | / MMBtu | reactivation | 0 | cfm |  |  | At the current average costs of fuel and O&M, the cost of generation is $0.094 / kWh. Part of the cost of generation can be offset by recovery of heat for space heating or hot water ($0.052 / kWh for fossil fuel-fired heating or $0.121 / kWh for electric resistance heat). Recovered heat used to produce chilled water can offset generation costs ($0.015 / kWh and $0.025 / kWh for single- and double-effect chillers, respectively). Recovered heat used to regenerate a desiccant dehumidifier is worth $0.012 / kWh.
(2) annual consumption |  | tons / year | a. up front buy-down | 0 |  |  |  | 0 | / MMBtu |  |  |  | Absorption Chiller Data |  |  | (8) subsidy or buy-down | 0 | /kW |  |  |  |  | b. Power | 6 | kW
|  |  | b. annual operating subsidy | 0 | / year | [7 empty] | a. specified chiller capacity | 2500 | tons | (9) net installed cost | 1621.7115 | /kW | Current Values for Alternative Energy Line |  |  |  | c. Installed Cost | 6.5 | $ / cfm
Average Energy Costs | [6 empty] | Old Notes: | [5 empty] | b. chiller unit cost | 405 | / ton | c. non-fuel operating & maintenance costs | 0.0076 | / kWh | a. electricity | 0.001 | / kWh |  | d. O&M Costs | 0.0075 | $ / year / cfm
a. electricity | 0.060485 | / kWh | Calculations |  |  | 1 | [6 empty] | c. fraction of recovered heat use | 100% |  | d. scheduled and unscheduled outages | 2 | weeks / year | b. fuel | 5 | / MMBtu
b. fossil fuels | 7.602 | / MMBtu | a. engine, generator, HRHX installed cost | 7420400 |  | 2 | Recovered energy used for absorption chillers is worth approximately $0.025 and $0.015 / kWh generated for double and single-effect chillers, respectively. | [5 empty] | d. gCOP | 1.2 |  | e. recoverable waste heat | 25.5432 | MMBtu / h (per generator) |  |  |  |  | Use of Waste Heat
|  |  | b. absorption chiller installed cost | 1012500 |  | 3 | [6 empty] | e. electric chiller efficiency for comparison | 0.85 | kW / ton |  |  |  | Manipulate Graph and Legends |  |  |  | a. fraction of recoverable waste heat used | 100%
Computations |  |  | c. desiccant dehumidifier installed cost | 0 | [8 empty] | f. chiller data complete | TRUE |  | Computations |  |  | a. data form size |  | no longer used; replaced by scroll bar inputs for 50% to 150% |  | b. fraction of used waste heat for space heating | 0%
a. natural gas | 146168.4 | / MMBtu | d. basic installed cost | 8432900 | [11 empty] | a. annual operating hours | 8424 | hours / year | (1) 100% | X |  |  | c. fraction of used waste heat for chilled water | 100%
b. fuel oil | 0 | / MMBtu | e. multiplier | 1 | [11 empty] | b. power generated | 43804800 | kWh | (2) 90% |  |  |  | d. fraction of used waste heat for desiccants | 0%
c. coal or coal equivalent | 0 | / MMBtu | f. adjusted installed cost | 8432900 | [11 empty] | c. fuel consumption | 498411.0144 | MMBtu | (3) 80% |  |  |  | e. total waste heat use | 100%
d. total consumption | 146168.4 | / MMBtu | g. up front buy down | 0 | [11 empty] | d. thermal production | 0 | MMBtu / year | (4) 70%
|  |  | h. net project cost | 8432900 |  |  | Notes: | [8 empty] | e. chilled water production | 21517563.2702 | ton-hrs / year | (5) 60% |  |  |  | Constants Used in Calculations
Conversion Factors |  |  | i. cost per unit capacity | 1621.7115 | / kW | 1 | Recovered energy used for heating purposes is worth approximately $10.56 / MMBtu when replacing fossil fuel-fired heating and $24.61 / MMBtu when replace electric heat or hot water ($0.052 and $0.121/ kWh generated, respectively). | [8 empty] | New Cost Factors: Unused So Far |  |  | b. legend |  |  |  | a. density of air | 0.072 | lb / ft3
a. therms | 0.1 | MMBtu |  |  |  | 2 | Recovered energy used for absorption chillers is worth approximately $5.14 and $3.00 / MMBtu for double and single-effect chillers, respectively ($0.025 and $0.015 / kWh generated, respectively). | [8 empty] | selective catalytic reduction |  |  | (1) horizontal scroll bar |  |  |  | b. specific heat of air | 0.24 | Btu / lb°F
b. thousand cubic feet | 1.027 | MMBtu |  |  |  | 3 | Recovered energy used to regenerate a desiccant wheel is worth approximately $0.00 / MMBtu ($0.000 / kWh generated). | [8 empty] | a. equipment cost | 144.9785 | / kW | (a) minimum value | 0 |  |  | c. conversion factor | 7000 | grains / lb H2O
c. gallon fuel oil | 0.1394 | MMBtu | [13 empty] | b. operating cost |  |  | (b) maximum value |  |  |  | d. conversion factor | 62.26 | lb /ft3
d. ton coal | 26.26 | MMBtu |  |  |  |  | Recoverable Waste Heat | [8 empty] | (1) catalyst lifetime | 5 | years | (c) current value |  |  |  | e. conversion factor | 7.48 | gal. / ft3
[7 empty] | a. available | 25543166.2751 | Btu / h | [6 empty] | (2) catalyst cost | 50% |  | (2) vertical scroll bar
[8 empty] | 4912.1474 | Btu / kWh | [6 empty] | (3) catalyst replacement alone | 0.001721 | / kWh | (a) minimum value | 0 |  |  | Maximum air flow regenerated using recovered heat | 663610.5467 | cfm
Notes | [6 empty] | b. useable | 4912.1474 | Btu / kWh | [6 empty] | (4) O&M costs | 0.0014781 | / kWh | (b) maximum value |  |  |  | Savings (loss) from desiccant operation | 0.011542 | / kWhgenerated
The thermal capacity is 2.13 times the average thermal load. | [6 empty] | (1) heating | 0 | Btu / kWh | [7 empty] | 0.0031991 | / kWh | (c) current value
The total electrical capacity is 1.47 times the average electrical demand. | [6 empty] | (2) cooling | 4912.1474 | Btu / kWh | [7 empty] | 0.0085875 |  | c. summary message |  |  |  | F1(equipment) | 0.0068224
[7 empty] | (3) desiccant regeneration | 0 | Btu / kWh | [9 empty] | (1) horizontal scroll bar |  |  |  | F2(equipment) | 0.41753
Synopsis: Paybacks are relative to fossil fuel-fired space heating and hot water. Energy costs are $0.060/kWh for electricity and $7.60/MMBtu for fuel for a spark spread of $10.12/MMBtu. Results are based on 1 gas turbine generator(s) totaling 5,200 kW at a cost of $1,427 / kW, total installed cost is $1,622 / kW including absorption chillers (if any) and cost adjustment factors. O&M costs are $0.008 /kWh, standby charges of $24/kW and export rate of $0.025/kWh; 100% of generated power is used on site and the balance, if any, is exported. Net operating savings are -$0.011/kWh. Absorption chillers (2,500 tons) use 100% of recovered heat at a gCOP of 1.20 and cost of $405/ton in place of electric chilled water at 0.85 kW/ton. Other operating parameters include a generator heat rate of 11,378 Btu/kWh, heat recovery rate of 4,912 Btu/kWh and; boiler efficiency of 72%. There are 8,424 operating hours per year. Waste heat is used for space heating and hot water (0.0%), chilled water (100.0%), and desiccant regeneration (0.0%). Simple payback is -17.2 years with a financed payback at 6.00% of -12.2 years. | [18 empty] | (a) minimum value | 0 |  |  | F3(equipment) | 0
(b) maximum value
Paybacks are relative to fossil fuel-fired space heating and hot water. Energy costs are $0.060/kWh for electricity and $7.60/MMBtu for fuel for a spark spread of $10.12/MMBtu. | [18 empty] | (c) current value
Results are based on 1 gas turbine generator(s) totaling 5,200 kW at a cost of $1,427 / kW, total installed cost is $1,622 / kW including absorption chillers (if any) and cost adjustment factors. | [18 empty] | (2) vertical scroll bar
O&M costs are $0.008 /kWh, standby charges of $24/kW and export rate of $0.025/kWh; 100% of generated power is used on site and the balance, if any, is exported. Net operating savings are -$0.011/kWh. | [18 empty] | (a) minimum value | 0 |  |  | Derived Parameters | Electric | Desiccant
Absorption chillers (2,500 tons) use 100% of recovered heat at a gCOP of 1.20 and cost of $405/ton in place of electric chilled water at 0.85 kW/ton. | [18 empty] | (c) current value |  |  |  | 1. Power Per Unit Air Flow | 2.67 | 1 | W / cfm
Other operating parameters include a generator heat rate of 11,378 Btu/kWh, heat recovery rate of 4,912 Btu/kWh and; boiler efficiency of 72%. | [22 empty] | 2. Power Per Unit Water Removed | 212.8091 | 85.2827 | Wh / lb H2O
There are 8,424 operating hours per year. Waste heat is used for space heating and hot water (0.0%), chilled water (100.0%), and desiccant regeneration (0.0%). | [22 empty] | 3. Desiccant Reactivation Energy
Simple payback is -17.2 years with a financed payback at 6.00% of -12.2 years. | [22 empty] | a. boiler |  | 79.2 | Btu / h / cfm
[23 empty] | b. waste heat |  | 38.4912 | Btu / h / cfm
[23 empty] | 4. Water Removal |  | 1081.9147 | pints / day
Alternative Messages for the Top Screen | [22 empty] | 5. Savings Factors
Synopsis: Paybacks are relative to fossil fuel-fired space heating and hot water. Energy costs are $0.060/kWh for electricity and $7.60/MMBtu for fuel for a spark spread of $10.12/MMBtu. Results are based on 1 gas turbine generator(s) totaling 5,200 kW at a cost of $1,427 / kW, total installed cost is $1,622 / kW including absorption chillers (if any) and cost adjustment factors. O&M costs are $0.008 /kWh, standby charges of $24/kW and export rate of $0.025/kWh; 100% of generated power is used on site and the balance, if any, is exported. Net operating savings are -$0.011/kWh. Absorption chillers (2,500 tons) use 100% of recovered heat at a gCOP of 1.20 and cost of $405/ton in place of electric chilled water at 0.85 kW/ton. Other operating parameters include a generator heat rate of 11,378 Btu/kWh, heat recovery rate of 4,912 Btu/kWh and; boiler efficiency of 72%. There are 8,424 operating hours per year. Waste heat is used for space heating and hot water (0.0%), chilled water (100.0%), and desiccant regeneration (0.0%). Simple payback is -17.2 years with a financed payback at 6.00% of -12.2 years. | [22 empty] | a. power reduction | 0.19083 | kWhsaved / kWhgenerated
WARNING: allocation of recovered heat exceeds 100% of available energy; change the allocation of recovered heat on the 'Cost & Heat Use' page of the user interface. | [22 empty] | b. dollar savings | 0.011542 | / kWhgenerated
WARNING: an incomplete set of data is provided for the chiller plant: absorption chiller capacity is set at 2,500 tons, fraction of recovered heat use is specified as 100%, chiller cost at $405 / ton, chiller efficiency at 1.20, and electric chiller efficiency as 0.85 kW/ton. Change the fraction of waste heat used for cooling on the 'Cost & Heat Use' page of the user interface, change the other parameters on the 'Chillers & Fuel Cells' page of the user interface. | [23 empty] | 2.3498 | / MMBturecovered
WARNING: the specified boiler efficiency of 72% is too low for electric resistance heating and hot water; change boiler efficiency in 'Misc.' page of the user interface. | [22 empty] | 6. Moisture Removal COP | 0.30463
WARNING: the specified boiler efficiency of 72% is too high for fossil-fuel fired heating and hot water; change boiler efficiency in 'Misc.' page of the user interface.
Note on W43: Cogeneration Design Guide, p. 34
Note on W44: Cogeneration Design Guide, p. 34
Note on W41: Curve fit to mfr data
Note on W46: for a lean burn IC-engine, 320 kW operating 4000 h/y in San Diego at a cost of $1892/year. Modern Power Systems, August 2002. Ravi Krishnan
Note on W45: Steve Fischer:
Note on X45: also estimated at $0.0086/kWh using data from "SCR: California Cleaning" by Ravi Krishnan, Moder Power Systems, August 2002 for a 320 kW natural-gas fired IC engine generator

## Default Values
"Energy"
Site Name | Default Data Set | C5
Electricity Data
a. annual cost | 550000 | C8
b. annual consumption | 10000000 | C9
c. summer peak demand | 2000 | C10
d. winter peak demand | 2000 | C11
Natural Gas Data
a. annual cost | 500000 | C14
b. annual consumption | 100000 | C15
c. consumption units
(1) MMBtu | X | C17
(2) therms |  | C18
(3) thousand cubic feet |  | C19
"System"
Number of Generators | 1 | G5 | Interpolated Data
Generator Capacity | 1210 | G7 | a. prime mover heat rate | 11378.4005 | W18
Type of Generator ("GT", "IC", "MT", or "FC") | GT | G10 | b. O&M costs | 0.0075605 | W29
|  |  | c. equipment costs | 1427.4307 | W20
Financial Externalities |  |  | d. outages | 2 | W30
a. up front buy-down | 0 | G27 | e. recovered heat rate | 25.5432 | W31
b. annual operating subsidy | 0 | G28 | f. maximum chilled water capacity | 2554.3166 | S23
|  |  | g. HRSG effectiveness | 0.62 | W14
|  |  | h. miscellaneous thermal losses | 0.05 | W13
"Chillers and Fuel Cells" |  |  | i. absorption chiller costs | 420 | S17
Type of Chiller
a. no absorption chiller | X | S6
b. absorption chiller |  | S7
Type of Absorption Chiller
a. steam-fired single-effect |  | S10
b. steam-fired double-effect |  | S11
Other Data
a. electric chiller efficiency | 0.85 | S14
b. absorption chiller efficiency | 0.7 | S15
c. fraction of recovered heat used by chiller | 0% | S16
d. cost of absorption chiller | 450 | S17
e. cost of fuel cell stack | 1750 | S18
f. fuel cell stack lifetime | 5 | S19
g. fuel cell availability for stack calculations | 0.96 | S20
h. installed absorption chiller capacity | 500 | S24
"Misc."
Assumptions
a. standby charges | 24 | W6
b. price for exported power | 0.025 | W7
c. fraction of generated power used on site | 100% | W8
d. interest rate | 6% | W9
e. fraction of recoverable heat that is usable | 100% | W10
f. alternative waste heat | 75% | W11
f. boiler efficiency | 72% | W12
g. miscellaneous thermal losses | 0.05 | W13
h. heat recovery heat exchanger effectiveness | 0.52 | W14
i. alternative fuel cost for analysis | 4.5 | W15
j. space heating & hot water | fossil
Graph Axis Limits
a. horizontal | 0 | 0.25 | AA25:AB25
b. vertical | 0 | 20 | AA26:AB26
c. data form size | 100% | AA34
"Misc. 2"
Desiccant System Properties
a. ventilation air exhaust temperature | 80 | AE6
b. regeneration temperature | 184 | AE7
c. electric dehumidifier (fan & compressor) | 204 | AE8
d. fan & motor power | 4000 | AE9
e. air flow rate | 2000 | AE10
f. heat recovery wheel effectiveness | 0.45 | AE11
g. bldg air conditioner COP | 4.1365 | AE12
h. unit cost | 6.5 | AE38
i. size | 507621.0483 | AE39 | cfm / kW | Qrecovered | 4912.1474 | Btu / h per kW capacity
|  |  |  | Qregenerator | 0.83866 | Btu / ft3
|  |  |  | mdesiccant | 97.6194 | cfm / kW capacity
Miscellaneous Equipment Costs | 0 | W23 |  |  | 0.07 | lb air / ft3
Cost Adjustment Factor | 1 | W25 |  |  | 0.24 | Btu / lb air °F
[5 empty] | 104 | °F
Distribution of Waste Heat
a. heating and hot water | 100% | AE33
b. chilled water | 0% | S16
c. desiccant regeneration | 0% | AE35

## Equipment
| Rated Capacity |  | 5200 | kW
| Type of Equipment |  | GT
|  |  |  | O&M | Installed
|  |  | Heat Rate | Cost | Cost | Waste Heat | [10 empty] | Absorption and Centrifugal Chiller Reference Material
| Prime Mover Data |  | (Btu / kWh) | ($ / kWh) | ($/kW) | (Btu / kWh)
| Steam Turbine-Generator | [15 empty] | Application Guide for Absorption Cooling / Refrigeration Using Recovered Heat
| 1000 | kW | 22750 | 0.0025 | 500 | ? |  | Btu / kWh | [8 empty] | Chad B. Dorgan, Steven P. Leight, and Charles E. Dorgan
| 5000 | kW | 18200 | 0.00175 | 400 | ? |  | Btu / kWh | [8 empty] | American Society of Heating, Refrigeration, and Air Conditioning Engineers, 1995
| 10000 | kW | 13650 | 0.001 | 300 | ? |  | Btu / kWh | [8 empty] | p. 26
| Gas Turbine-Generator |  | Ref: Solar Turbines proprietary software | [14 empty] | Single-Effect ($ / ton) |  |  | Double-Effect ($ / ton)
| 1210 | kW | 14025 | 0.01 | 3500 | 6588.2975 |  | Btu / kWh |  | Fuel Cell Assumptions | [6 empty] | Nominal Size | low | high | average | low | high | average
| 3515 | kW | 12240 | 0.0079 | 1750 | 5244.7954 |  | Btu / kWh |  | Stack Cost |  |  | 350000 |  |  |  | 250 | 330 | 660 | 495 | 460 | 920 | 690
| 5500 | kW | 11225 | 0.0075 | 1370 | 4852.9222 |  | Btu / kWh |  | Stack Lifetime |  |  | 5 | years |  |  | 500 | 220 | 490 | 355 | 310 | 690 | 500
| 10690 | kW | 10520 | 0.0075 | 1025 | 4763.899 |  | Btu / kWh |  | Availability |  |  | 0.96 |  |  |  | 1000 | 210 | 390 | 300 | 290 | 550 | 420
| IC-Engine Generator |  | The Market and Technical Potential for Combined Heat and Power in the Commercial / Institutional Sector: Revision 1, Onsite Sycom Energy, January 2000, pp. 22-23, 24-25, and 26-27 | [6 empty] | Stack Replacement Cost |  |  | 0.041619 | / kWh |  |  |  | 200 | 280 | 240 | 280 | 530 | 405
| 100 | kW | 10980.7011 | 0.015894 | 1390 | 5683 |  | Btu / kWh
| 800 | kW | 10006.3291 | 0.010321 | 975 | 4323 |  | Btu / kWh |  | Natural Gas:
| 3000 | kW | 9198.5784 | 0.010019 | 850 | 2909 |  | Btu / kWh |  | HHV | 1027
| Microturbine |  | The Market and Technical Potential for Combined Heat and Power in the Commercial / Institutional Sector: Revision 1, Onsite Sycom Energy, January 2000, pp. 22-23, 24-25, and 26-27 | [6 empty] | LHV | 930 | [9 empty] | Single-Effect Absorption Chillers
| 30 | kW | 12049.2502 | 0.010903 | 1870 | 4498 |  | Btu / kWh | [9 empty] | Capacity | Installed | Installed Cost | 100 | 285
| 60 | kW | 12049.2502 | 0.010903 | 1870 | 4498 |  | Btu / kWh | [8 empty] | R.S. Means 2002, p. 455 | (tons) | Cost | ($ / ton) | 500 | 210
| 200 | kW | 12049.2502 | 0.010903 | 1870 | 4498 |  | Btu / kWh | [8 empty] | Steam Absorption Chiller, Water Cooled | 750 | 434500 | 579.3333 | 1000 | 195
| Fuel Cell |  | arbitrary assumptions | [13 empty] | single-effect chiller is pictured | 955 | 506500 | 530.3665 | 1500 | 195
| 100 | kW | 8532.5 | 0.056619 | 3500 | 2250 |  | Btu / kWh | [9 empty] | 1465 | 713000 | 486.6894
| 200 | kW | 8532.5 | 0.056619 | 3500 | 2250 |  | Btu / kWh | [9 empty] | 1660 | 848000 | 510.8434
| 500 | kW | 8532.5 | 0.056619 | 3500 | 2250 |  | Btu / kWh | [12 empty] | Double-Effect Absorption Chillers
| References: | [19 empty] | 100 | 550
[17 empty] | University of Wisconsin Cogeneration Short Course |  |  |  | 200 | 550
| Interpolated Equipment Data |  | Gas Turbine | Micro-Turbine | IC Engine | Fuel Cell | [10 empty] | Rule of Thumb #15 |  |  |  | 500 | 500 | 475
[17 empty] | Single Effect Steam-Fired Absorption |  |  | 500 | 1000 | 450 | 425
| Heat Rate |  | 11378.4005 | 12049.2502 | 9198.5784 | 8532.5 |  | Btu / kWh | [8 empty] | Double-Effect Steam-Fired Absorption |  |  | 700 | 1500 | 450 | 425
| Installed Cost |  | 1427.4307 | 1870 | 850 | 3500 |  | / kW | [8 empty] | Centrifugal Chillers |  |  | $400 to $500
| O&M Cost |  | 0.0075605 | 0.010903 | 0.010019 | 0.056619 |  | / kWh | [12 empty] | Centrifugal Chillers
| Annual Outage |  | 2 | 2 | 3 | 2 |  | weeks | [8 empty] | Gas-Fired Chiller-Heaters as a Central Plant Alternative for Small Office Buildings |  |  |  | 200 | 450
| Recovered Waste Heat |  | 4912.1474 | 4498 | 2909 | 2250 |  | Btu / kWh | [12 empty] | 300 | 330
| HRSG Effectiveness |  | 0.62 | 0.67 | 0.52 | 0.5 | [10 empty] | Heating / Piping / Air Conditioning, January 1998, p. 103-112. |  |  |  | 350 | 308
| Miscellaneous Heat Losses |  | 5% | 5% | 5% | 5% | [14 empty] | 500 | 325
| Lookup Values | [15 empty] | centrifugal chiller | 200 | 69200 | 346 | 600 | 310
| prime mover heat rate |  |  |  | 11378.4005 | Btu/kWh | [10 empty] | double-effect absorption chiller | 200 | 119000 | 595 | 700 | 300
| CHP O&M costs |  |  |  | 0.0075605 | /kWh | [10 empty] | double-effect absorption chiller | 60 | 66000 | 1100 | 800 | 278
| equipment cost |  |  |  | 1427.4307 | /kW | [14 empty] | 900 | 278
| scheduled and unscheduled outages |  |  |  | 2 | weeks / year | [14 empty] | 1000 | 350
| recovered heat |  |  |  | 4912.1474 | Btu / kWh
[5 empty] | 25543166.2751 | Btu / h (per generator) | [14 empty] | Data from Arnold and Bahnfleth, "Peak Shaving Using Natural Gas Engine-Driven Chillers," HPAC, September 1998, p. 51-59
| maximum chilled water capacity |  |  |  | 2554.3166 | tons (per generator) | [14 empty] | Fax from Patti Garland (ORNL) to Ron Fiskum (DOE) datae March 19, 1998, and
| HRSG effectiveness |  |  |  | 0.62 | [15 empty] | Fax from Jay Kohler (York or Trane) to Patti Garland (ORNL) dated February 25, 1999.
| miscellaneous thermal losses |  |  |  | 0.05
Installed Cost Summary: Interpolated Initial Values
| generator and HRB |  |  |  | 1427.4307 | / kW
| absorption chiller |  |  |  | 206.3102 | / kW |  | 420 | / ton
| total |  |  |  | 1633.7409 | / kW
Absorption Chiller Costs
|  | Single-Effect | Double-Effect
| tons | ($ / ton) | ($ / ton)
| 0 | 495 | 690
| 250 | 495 | 690
| 500 | 355 | 500
| 1000 | 300 | 420
| 0 | 240 | 405
| 10000 | 240 | 405
Interpolated Chiller Costs
| tons | Single-Effect | Double-Effect
| 0 | 240 | 405
| 2554.3166 | 240 | 405
| 10000 | 240 | 405
[17 empty] | Fuel Cell | Micro-Turbine
| Combustion Gas Turbines | [7 empty] | Cost Component |  |  |  |  | IC Engine Generators
| Nominal Capacity |  |  | kW | 1000 | 5000 | 10000 |  | Capacity |  |  |  | kW | 100 | 800 | 3000 | 200 | 100
| Combustion Turbine |  |  | $ | 550000 | 2102940 | 4319200 |  | Package Cost |  |  |  | $ / kW | 550 | 430 | 380 | 2425 | 800
| Heat Recovery Steam Generator |  |  | $ | 250000 | 350000 | 590000 |  | Heat Recovery |  |  |  | $ / kW | 100 | 75 | 65 | 75 | 150
| Water Treatment System |  |  | $ | 30000 | 100000 | 150000 |  | Interconnect / Switchgear |  |  |  | $ / kW | 150 | 60 | 35 | 75 | 100
| Electrical Equipment |  |  | $ | 150000 | 375000 | 625000 |  | Miscellaneous Equipment |  |  |  | $ / kW | 70 | 50 | 50 | 0 | 135
| Other Equipment |  |  | $ | 145000 | 315000 | 575000 |  | Installation / Civil Work |  |  |  | $ / kW | 150 | 105 | 90 | 285 | 210
| Total Equipment |  |  | $ | 1125000 | 3242940 | 6259200 |  | Engineering and Management |  |  |  | $ / kW | 90 | 60 | 60 | 180 | 130
[9 empty] | General Contractor Markup |  |  |  | $ / kW | 150 | 105 | 90 | 310 | 150
| Materials |  |  | $ | 143952 | 356723 | 688512 |  | Contingencies and Guarantees |  |  |  | $ / kW | 60 | 40 | 35 | 105 | 95
| Labor |  |  | $ | 347509 | 908023 | 1752576 |  | Carrying Charges During Construction |  |  |  | $ / kW | 70 | 50 | 45 | 220 | 100
[9 empty] | Total |  |  |  | $ / kW | 1390 | 975 | 850 | 3675 | 1870
| Total Process Capital |  |  | $ | 1616461 | 4507686 | 8700288
[9 empty] | O&M Costs |  |  |  | $ / kW / y | 131.2 | 85.2 | 82.7 | 87 | 90
| General Facilities Capital |  |  | $ | 48483 | 135231 | 261009 | [5 empty] | $ / y | 13120 | 68160 | 248100 | 17400 | 9000
| Engineering and Fees |  |  | $ | 48483 | 135231 | 261009 |  |  | 94.23% | 8254.6154 | h / y | $ / kWh | 0.015894 | 0.010321 | 0.010019 | 0.039917 | 0.010903
| Process Contingency |  |  | $ | 48483 | 135231 | 261009 |  | Heat Rate (HHV) |  |  |  | Btu / kWh | 12126 | 11050 | 10158 | 9481 | 13306
| Project Contingency |  |  | $ | 171305 | 477815 | 922231 |  | Heat Recovery
[9 empty] | exhaust |  |  |  | Btu / kWh | 2273 | 1491 | 1934 |  | 4498
| Total Plant Cost |  |  | $ | 1933215 | 5391194 | 10405546 |  | jacket water |  |  |  | Btu / kWh | 3410 | 2832 | 975 | 3500
| Actual Turbine Capacity |  |  | kW | 1205 | 5007 | 10798 |  | total |  |  |  | Btu / kWh | 5683 | 4323 | 2909 | 3500 | 4498
| Total Plant Cost per kW |  |  | $ / kW | 1604.3278 | 1076.7314 | 963.6549
The Market and Technical Potential for Combined Heat and Power in the Commercial / Institutional Sector: Revision 1, Onsite Sycom Energy, January 2000, pp. 22-23, 24-25, and 26-27
| O&M Costs |  |  | $ / kW / y | 76.8 | 46.8 | 44.3
|  |  |  | $ / y | 76800 | 234000 | 443000
| 96.15% | 8423.0769 | h / y | $ / kWh | 0.0091178 | 0.0055562 | 0.0052594
| Heat Rate (HHV) |  |  | Btu / kWh | 15600 | 12375 | 11750 |  | Fuel Cell Stack Replacement
| Heat Recovery |  |  | Btu / kWh | 7820 | 5622 | 5283 |  | minimum | 3 | years
| The Market and Technical Potential for Combined Heat and Power in the Commercial / Institutional Sector: Revision 1 | [7 empty] | maximum | 7 | years
[9 empty] | cost | 50% | of initial cost
| Onsite Sycom Energy, January 2000, pp. 29 and 31 | [8 empty] | 0.029378 | / kWh
| Desiccant System Specifications: |  |  |  |  | Commercial Desiccant Dehumidifiers
| Air Flow |  |  |  |  | Parameter |  | Units |  | Solid |  |  | Liquid
| a. process |  | #REF! | cfm |  | Flow Rate |  | scfm |  | 2000 | 7000 | 12000 | 10000 | 50000 | 84000
| b. regeneration |  | 3500 | cfm |  | Installed Cost |  | $ / scfm |  | 7.5 | 5.5 | 4.3 | 6.9 | 5.63 | 4.95
| c. total |  | #REF! | cfm |  | O&M Costs |  | $ / y / scfm |  | 0.09 | 0.075 | 0.06 | 0.15 | 0.125 | 0.113
| c. operating hours |  | 8424 | / year |  | Thermal Input |  | Btu / h / scfm |  | 45 | 45 | 45 | 35 | 35 | 35
| Regeneration |  |  |  |  | Latent Heat Removal |  | Btu / h / scfm |  | 45 | 45 | 45 | 30 | 30 | 30
| a. temperature |  | 0 | °F |  | Parasitic Electric Use |  | Wh / scfm |  | 0.8 | 0.8 | 0.8 | 1.3 | 1.3 | 1.3
| b. reactivation |  | 17990 | °F
| c. DT |  | -17990 | °F
| d. hboiler |  | 0.72 |  |  | Industrial Desiccant Dehumidifiers
| e. hheat recovery wheel |  | 4000 |  |  | Parameter |  | Units |  | Solid |  |  |  | Liquid
| Properties of Air |  |  |  |  | Flow Rate |  | scfm |  | 600 | 4500 | 20000 | 40000 | 3000 | 7500 | 84000
| a. Cp |  | 0.24 | Btu / lb°F |  | Installed Cost |  | $ / scfm |  | 20.4 | 9.2 | 5.6 | 4.4 | 18 | 9.78 | 5.04
| b. r |  | 0.072 | lb / ft3 |  | O&M Costs |  | $ / y / scfm |  | 0.255 | 0.12 | 0.075 | 0.06 | 0.375 | 0.213 | 0.113
[6 empty] | Thermal Input |  | Btu / h / scfm |  | 55 | 55 | 55 | 55 | 45 | 45 | 45
| Interpolated Parameters |  |  |  |  | Latent Heat Removal |  | Btu / h / scfm |  | 35 | 35 | 35 | 35 | 30 | 30 | 30
| a. unit cost |  | #REF! | / cfm |  | Parasitic Electric Use |  | Wh / scfm |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.3 | 1.3 | 1.3
| b. unit O&M costs |  | #REF! | / cfm / year
| c. parasitic power |  | #REF! | W / cfm |  | Source: Advanced Microturbine System Market Assessment - Task Report: Integration of Desiccant Dehumidification with the
Advanced Microturbine System, Energy and Environmental Analysis, May 31, 2003, p. 12.
Calculated Parameters
| a. cost |  | #REF! | #REF!
| b. O&M costs |  | #REF! | #REF! | / year
| c. reactivation heat |  | 103596494.4 | #REF! | Btu / h / cfm
| d. unit power |  | #DIV/0! | #REF! | W / cfm
| d. power |  | #DIV/0! | #REF! | kW
| e. power consumption |  | #DIV/0! | #REF! | kWh / y
Desert Aire
| air flow | kW | pints / day | lb / h | W / cfm | W / lb H2O
| 400 | 0.85 | 65 | 2.8099 | 2.125 | 302.5023
| 400 | 1.48 | 121 | 5.2307 | 3.7 | 282.9433
| 400 | 1.55 | 165 | 7.1328 | 3.875 | 217.3056
| 540 | 1.63 | 161.9277 | 7 | 3.0185 | 232.8571
| 950 | 2.24 | 259.0843 | 11.2 | 2.3579 | 200
| 1400 | 3.5 | 425.6386 | 18.4 | 2.5 | 190.2174
| 2300 | 6.12 | 730.988 | 31.6 | 2.6609 | 193.6709
| 3500 | 8.85 | 1022.4578 | 44.2 | 2.5286 | 200.2262
| 4100 | 11.23 | 1381.012 | 59.7 | 2.739 | 188.1072
| 5500 | 15.01 | 1600.7711 | 69.2 | 2.7291 | 216.9075
| 6900 | 17.99 | 1950.0723 | 84.3 | 2.6072 | 213.4045
Cost of Absorption Chillers per unit electrical capacity
|  |  | (Btu / kWh) | ($ / kWh) | ($ / kW) | (Btu / kWh) | (tons) | ($/ton) | ($ / kW)
Gas Turbine-Generator
| 1210 | kW | 14025 | 0.01 | 3500 | 6588.2975 | 797.184 | 452.4506 | 298.0879 | [5 empty] | Single-Effect ($ / ton)
| 3515 | kW | 12240 | 0.0079 | 1750 | 5244.7954 | 1843.5456 | 405 | 212.4142 |  |  |  |  | Nominal Size | low | high | average
| 5500 | kW | 11225 | 0.0075 | 1370 | 4852.9222 | 2669.1072 | 405 | 196.5433 |  |  |  |  | 250 | 330 | 660 | 495
| 10690 | kW | 10520 | 0.0075 | 1025 | 4763.899 | 5092.608 | 405 | 192.9379 |  |  |  |  | 500 | 220 | 490 | 355
| IC-Engine Generator | [12 empty] | 1000 | 210 | 390 | 300
| 100 | kW | 10980.7011 | 0.015894 | 1390 | 5683 | 33.1508 | 495 | 164.0966 |  |  |  |  | 0 | 200 | 280 | 240
| 800 | kW | 10006.3291 | 0.010321 | 975 | 4323 | 201.74 | 495 | 124.8266
| 3000 | kW | 9198.5784 | 0.010019 | 850 | 2909 | 509.075 | 354.0018 | 60.0711 | [5 empty] | Double-Effect ($ / ton)
| Microturbine | [13 empty] | low | high | average
| 30 | kW | 12049.2502 | 0.010903 | 1870 | 4498 | 7.8715 | 495 | 129.8798 |  |  |  |  | 250 | 460 | 920 | 690
| 60 | kW | 12049.2502 | 0.010903 | 1870 | 4498 | 15.743 | 495 | 129.8798 |  |  |  |  | 500 | 310 | 690 | 500
| 200 | kW | 12049.2502 | 0.010903 | 1870 | 4498 | 52.4767 | 495 | 129.8798 |  |  |  |  | 1000 | 290 | 550 | 420
| Fuel Cell | [12 empty] | 0 | 280 | 530 | 405
| 100 | kW | 8532.5 | 0.056619 | 3500 | 2250 | 13.125 | 495 | 64.9688
| 200 | kW | 8532.5 | 0.056619 | 3500 | 2250 | 26.25 | 495 | 64.9688
| 500 | kW | 8532.5 | 0.056619 | 3500 | 2250 | 65.625 | 495 | 64.9688

## Dehumidifiers
|  | Specified / Calculated | [5 empty] | Commercial Electric Dehumdifiers
Parameters |  |  | Interpolated |  | Reference Electric Dehumidifier |  |  | air flow | kW | pints / day | lb / h | W / cfm | W / lb H2O
a. unit cost |  | 6.5 | 7.5 | / cfm | a. Power | 17.99 | kW | 400 | 0.85 | 65 | 2.8099 | 2.125 | 302.5023
b. unit O&M costs |  | 0.0075 | 0.09 | / cfm / year | b. Air Flow | 0 | cfm | 400 | 1.48 | 121 | 5.2307 | 3.7 | 282.9433
c. specified capacity |  | 0 |  | cfm process air | c. Water Removal | 1950 | pints / day | 400 | 1.55 | 165 | 7.1328 | 3.875 | 217.3056
a. cost |  | 0 | 0 |  |  | 84.5358 | lb / h | 540 | 1.63 | 161.9277 | 7 | 3.0185 | 232.8571
b. O&M costs |  | 0 | 0 | / year |  |  |  | 950 | 2.24 | 259.0843 | 11.2 | 2.3579 | 200
[5 empty] | Reference Desiccant Dehumidifier |  |  | 1400 | 3.5 | 425.6386 | 18.4 | 2.5 | 190.2174
[5 empty] | a. Power | 4 | kW | 2300 | 6.12 | 730.988 | 31.6 | 2.6609 | 193.6709
1. P*ref, elec | 212.8091 | Wh / lb H2O |  |  | b. Air Flow |  |  | 3500 | 8.85 | 1022.4578 | 44.2 | 2.5286 | 200.2262
2. Pref, desi | 4 | kW |  |  | process | 2000 | cfm | 4100 | 11.23 | 1381.012 | 59.7 | 2.739 | 188.1072
3. mref, desi, water | 46.9029 | lb H2O / h |  |  | reactivation | 2000 | cfm | 5500 | 15.01 | 1600.7711 | 69.2 | 2.7291 | 216.9075
4. P*ref, desi | 85.2827 | Wh / lb H2O |  |  | c.Water Removal |  |  | 6900 | 17.99 | 1950.0723 | 84.3 | 2.6072 | 213.4045
5. mmax cfm, desi, total | 127.6174 | cfm / kWhgenerated |  |  | win | 130 | grains H2O
6. mmax, desi, process | 63.8087 | cfm / kWhgenerated |  |  | wout | 92 | grains H2O | Source: Desert Aire Product Literature
| 331805.2733 | cfm |  |  | derived | 46.9029 | lb / h
7. mspecified, desi, process | 0 | cfm | [5 empty] | Commercial Desiccant Dehumidifiers
8. mspecified, desi, water | 0 | lb H2O / h |  |  | Reactivation Energy |  |  | Parameter |  | Units |  | Solid |  |  | Liquid
9. DPelectric-desiccant | 0 | kW |  |  | a. Temperatures |  |  | Flow Rate |  | scfm |  | 2000 | 7000 | 12000 | 10000 | 50000 | 84000
| 0 | kWh / kWhgenerated |  |  | Tregenerator | 190 | °F | Installed Cost |  | $ / scfm |  | 7.5 | 5.5 | 4.3 | 6.9 | 5.63 | 4.95
10. DCdesiccant | 0 | / kWhgenerated |  |  | Tinlet | 80 | °F | O&M Costs |  | $ / y / scfm |  | 0.09 | 0.075 | 0.06 | 0.15 | 0.125 | 0.113
[5 empty] | b. hheat recovery wheel | 0.325 |  | Thermal Input |  | Btu / h / scfm |  | 45 | 45 | 45 | 35 | 35 | 35
[8 empty] | Latent Heat Removal |  | Btu / h / scfm |  | 45 | 45 | 45 | 30 | 30 | 30
Qrecovered | 4912.1474 | Btu / kWhgenerated |  |  | Boiler Efficiency | 0.72 |  | Parasitic Electric Use |  | Wh / scfm |  | 0.8 | 0.8 | 0.8 | 1.3 | 1.3 | 1.3
Qe | 5200 | kW
Ce | 0.060485 | / kWh |  |  | Desiccant System Metrics
[5 empty] | a. heat input |  |  | Industrial Desiccant Dehumidifiers
F3 | 0 |  |  |  | boiler input | 79.2 | Btu / h / cfm | Parameter |  | Units |  | Solid |  |  |  | Liquid
11. Pspecified, desi | 0 | kW |  |  | waste heat input | 38.4912 | Btu / h / cfm | Flow Rate |  | scfm |  | 600 | 4500 | 20000 | 40000 | 3000 | 7500 | 84000
12. mref, desi, water | 1081.9147 | pints / day |  |  | b. power | 1 | W / cfm total air flow | Installed Cost |  | $ / scfm |  | 20.4 | 9.2 | 5.6 | 4.4 | 18 | 9.78 | 5.04
13. DPdehumidifiers | 0.19083 | kWhsaved / kWhgenerated | [5 empty] | O&M Costs |  | $ / y / scfm |  | 0.255 | 0.12 | 0.075 | 0.06 | 0.375 | 0.213 | 0.113
14. DCdehumidifiers | 0.011542 | / kWhgenerated |  |  | Constants |  |  | Thermal Input |  | Btu / h / scfm |  | 55 | 55 | 55 | 55 | 45 | 45 | 45
| 2.3498 | / MMBturecovered |  |  | Cpair | 0.24 | Btu / lb°F | Latent Heat Removal |  | Btu / h / scfm |  | 35 | 35 | 35 | 35 | 30 | 30 | 30
15. mspecified, water | 0 | lb H2O / h |  |  | density air | 0.072 | lb air / ft3 | Parasitic Electric Use |  | Wh / scfm |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.3 | 1.3 | 1.3
| 0 | pints / day |  |  | density water | 62.26 | lb /ft3
16. moisture removal COP | 0.30463 |  |  |  | conversion factors |  |  | Source: Advanced Microturbine System Market Assessment - Task Report: Integration of Desiccant Dehumidification with the
[6 empty] | 7000 | grains / lb | Advanced Microturbine System, Energy and Environmental Analysis, May 31, 2003, p. 12.
[6 empty] | 60 | min / h
[6 empty] | 7.48 | gal. / ft3
[6 empty] | 24 | h / d
[6 empty] | 8 | pints / gallon
[5 empty] | latent heat of vaporization | 1000 | Btu / lb H2O

## Tabular Results
Assumptions
1. Cost of power | 0.060485
2. Cost of fuel | 7.602
Project Cost | ($) | ($/kW)
1. Generator & Heat Recovery Heat Exchanger | 7420400 | 1427
2. Absorption Chiller | 1012500 | 194.7115
3. Desiccant Dehumidifier | 0 | 0
4. Miscellaneous Other Costs | 0 | 0
5. Total Installed Cost | 8432900 | 1621.7115
6. Adjusted Installed Cost | 8432900 | 1621.7115
7. Cost Buydown | 0 | 0
8. Net Project Cost | 8432900 | 1621.7115
| Current Energy Costs |  | Alternative Energy Cost
Components of Cost | 100% | 75% | 100% | 75%
1. Cost of Fuel for Generation | 0.086496 | 0.086496 | 0.051201 | 0.051201 | / kWh
2. O&M Costs | 0.0076 | 0.0076 | 0.0076 | 0.0076
3. Standby Charges | 0.002849 | 0.002849 | 0.002849 | 0.002849
4. Value of Power Produced | 0.060485 | 0.060485 | 0.060485 | 0.060485
5. Value of Power Exported | 0 | 0 | 0 | 0
6. Value of Recovered Heat for Heat and Hot Water | 0 | 0 | 0 | 0
7. Value of Recovered Heat for Chilled Water | 0.025255 | 0.018941 | 0.025255 | 0.018941
8. Value of Recovered Heat for Desiccant Regeneration | 0 | 0 | 0 | 0
9. Net Savings or Losses from Operation | -0.011205 | -0.017519 | 0.02409 | 0.017776
10. Operating Subsidy | 0 | 0 | 0 | 0
12. Total Net Savings or Losses from Operation | -0.011205 | -0.017519 | 0.02409 | 0.017776
13. Simple Payback | -17.1804 | -10.9887 | 7.9914 | 10.8298
Components of Cost | ($/kWh) | ($/year)
1. Cost of Fuel for Generation | 0.086496 | 3788940.3877
2. O&M Costs | 0.0076 | 332916.48
3. Standby Charges | 0.002849 | 124800
4. Value of Power Produced | 0.060485 | 2649541.9053
5. Value of Power Exported | 0 | 0
6. Value of Recovered Heat for Heat and Hot Water | 0 | 0
7. Value of Recovered Heat for Chilled Water | 0.025255 | 1106269.9235
8. Value of Recovered Heat for Desiccant Regeneration | 0 | 0
9. Net Savings or Losses from Operation | -0.011205 | -490845.0389
10. Operating Subsidy | 0 | 0
12. Total Net Savings or Losses from Operation | -0.011205 | -490845.0389
Recoverable Waste Heat | 25543166.2751 | Btu / h | 4912.1474 | Btu / kWh
Value ($ / kWhgenerated)
|  | (Btu / kWh) | 100% | specified %
2. Recoverable Waste Heat Used |  | 4912.1474
3. Recoverable Waste Heat Used for Space Heating & Hot Water | 0% | 0 | 0.051864 | 0
4. Recoverable Waste Heat Used for Chilled Water Production | 100% | 4912.1474 | 0.025255 | 0.025255
5. Recoverable Waste Heat Used for Desiccant Wheel Regeneration | 0% | 0 | 0 | 0
| 100% | 4912.1474 |  | 0.025255

## Emissions Calculations
State: | U.S. Average
Energy Input: | 7723.4895 | Btu / kWh |  |  | Power Generated: | 43804800 | kWh |  | U.S. Average
Carbon Dioxide | 1.3899 | lb / kWh |  |  | Natural Gas Consumption: | 498411.0144 | MMBtu |  | Alabama
NOx | 0.002937 | lb / kWh | [6 empty] | Alaska
SOx | 0.0060836 | lb / kWh | [6 empty] | Arizona
Arkansas
California
| Energy | Annual Emissions (tons) |  |  | Avoided Boiler Fuel | 0 | MMBtu / year |  | Colorado
| MMBtu | CO2 | NOx | SOx | Avoided A/C Electricity | 18289928.7796 | kWh / year |  | Connecticut
Baseline System | 338325.9122 | 30442.4688 | 64.3282 | 133.2448 | Avoided Dehumidifier Electricity | 0 | kWh / year |  | Delaware
CHP System | [8 empty] | Florida
a. power generation | 498411.0144 | 27412.6058 | 79.7458 | 0.8473 |  |  |  |  | Georgia
b. credit for heating / hot water | 0 | 0 | 0 | 0 |  | Emission Rates (lb / MMBtu) |  |  | Hawaii
c. credit for chilled water | 141262.0726 | 12710.7209 | 26.8591 | 55.6341 |  | CO2 | NOx | SOx | Idaho
d. credit for dehumidification | 0 | 0 | 0 | 0 | Gas Turbine - Uncontrolled | 110 | 0.32 | 0.0034 | Ilinois
d. net emissions | 357148.9418 | 14701.8849 | 52.8866 | -54.7868 | Commercial Boiler - Uncontrolled | 117.6471 | 0.1 | 0.00058824 | Indiana
CHP Emission Reductions | -18823.0296 | 15740.584 | 11.4416 | 188.0316 |  |  |  |  | Iowa
Kansas
Kentucky
Louisiana
Maine
Maryland
Massachusetts
Michigan
Minnesota
Mississippi
Missouri
Montana
Nebraska
Nevada
New Hampshire
New Jersey
New Mexico
New York
North Carolina
North Dakota
Ohio
Oklahoma
Oregon
Pennsylvania
Rhode Island
South Carolina
South Dakota
Tennessee
Texas
Utah
Vermont
Virginia
Washington
Washington DC
West Virginia
Wisconsin
Wyoming

## Alternative Energy
Changes were made to the positioning of labels for 100%, 50%, and 0% so these values should no longer be needed.
Coordinates of Plot Area
| Installed Cost |  | 1621.7115 | / kW | 1621.7115 |  | Left |  | 78.6 | Top | 25.8
| Annual Operation |  | 8424 | hours |  |  | Width |  | 288 | Height | 184.8
| Cost of Electricity |  | 0.06 | / kWh |  |  | Right |  | 366.6 | Bottom | 210.6
| Cost of Fuel |  | 7.6 | / MMBtu |  |  | Label Height |  | 8
| Payback at Alternative Rates |  | -16.2185 |  |  |  | Horizontal Offset (?) |  | 0
Current Energy Costs
| Cost of Electricity |  | 0.06 | / kWh |  | Simple payback at current energy rates is -16.2 years. Payback at $0.060 / kWh and $7.60 / MMBtu is -16.2 years.
| Cost of Fuel |  | 7.6 | / MMBtu
| Payback at Current Rates |  | -16.2185
|  | Simple Payback |  |  | Label Positions |  |  | Financed
|  | (years) |  |  | horizontal | vertical | DCCHP | (years)
| 0% | -5.214 | 0.06 | 9.8018 | 147.72 | 114.0315 | -0.036922 | -999 |  |  |  | 1. Gamma | g | 100%
| 25% | -6.2791 | 0.06 | 9.2513 |  |  | -0.030659 | -999 |  | -16.2185 |  | 2. Alpha | a | 11378
| 50% | -7.8911 | 0.06 | 8.7009 | 147.72 | 124.2037 | -0.024396 | -999 |  |  |  | 3. Beta | b | 100%
| 75% | -10.6167 | 0.06 | 8.1504 |  |  | -0.018133 | -999 |  |  |  | 4. Beta2 | b2 | 100%
| 100% | -16.2185 | 0.06 | 7.6 | 147.72 | 134.376 | -0.01187 | -999 |  |  |  | 5. Delta | d | 0
[12 empty] | 6. Epsilon | e | 0
[12 empty] | 7. gCOP | gCOP | 1.2
[8 empty] | 0.085052 |  |  |  | 8. EtaChiller | hchiller | 0.85
| Heat Content | [6 empty] | -0.01187 |  |  |  | 9. EtaBoiler | hboiler | 72%
| Btu / lb |  | MMBtu / ton |  | multipliers | [6 empty] | 10. Qe | Qe | 5200
Solid Fuels | low | high | low | high | low | high |  | 0.025052 | 0.025255 |  |  | 11. H | H | 8424
wood | [7 empty] | 0 | 0 |  |  | 12. COM | CO&M | 0.0076
bone dry | 7600 | 9600 | 15.2 | 19.2 | 0.57143 | 0.7218 |  | 0.06 | 0.060485 |  |  | 13. Cstandby | CStandby | 24
air dry, 20% moisture |  | 6400 |  | 12.8 |  | 0.4812 | [5 empty] | 14. Cexport | Cexport | 0.025
agricultural residues | 4300 | 7300 | 8.6 | 14.6 | 0.32331 | 0.54887 | [5 empty] | 15. Psubsidy | Psubsidy | 0
charcoal |  | 12800 |  | 25.6 |  | 0.96241 | [5 empty] | 16. Pbuydown | Pbuydown | 0
coal | [11 empty] | 17. Pturbine | Pturbine | 1427
default data |  |  |  | 26.6 |  | 1 | [5 empty] | 18. Pchiller | Pchiller | 194.7115
lignite | 11500 | 13000 | 23 | 26 | 0.86466 | 0.97744 | [5 empty] | 19. Kappa | k | 1
sub-bituminous | 6500 | 8200 | 13 | 16.4 | 0.48872 | 0.61654 | [5 empty] | 20. i | i | 6%
[12 empty] | 21. QkWh | QkWh | 43804800
| Recoverable Heat Rate |  |  | 4912.1474 | Btu / kWh
Note on K16: -999 is flagged to indicate no payback

## Input Report
Atlanta Metropolitan Area: Input Summary
1. Electric Utility Information
a. annual cost of power | 1877184
b. annual consumption | 31035429 | kWh
c.summer and winter peak demands | 7300 | 7000 | kW
2. Fuel Consumption Information | cost | consumption
a. natural gas | 1111178 | 1461684 | therms
b. #2 fuel oil | 0 | 0 | gallons
c. coal | 0 | 0 | tons
3. Generator Information
a. number of generators | 1
b. capacity of each generator | 5200 | kW
c. type of generator | Gas Turbine
d. heat rate | 11378 | Btu / kWh
e. non-fuel operating and maintenance costs | 0.0076 | / kWh
f. scheduled and unscheduled outages | 2 | weeks / year
g. recoverable waste heat | 25.5432 | MMBtu / h
4. Chiller Data
a. type of chillers (if any) | double-effect absorption
b. chiller capacity | 2500 | tons
c. electric chiller efficiency | 0.85 | kW / ton
d. absorption chiller efficiency | 1.2
e. cost of absorption chillers (if any) | 405 | / ton
5. Desiccant Dehumidifier Data
a. desiccant system capacity | #REF! | cfm
b. desiccant system installed cost | #REF! | / cfm
c. electric dehumidifier power consumption | 1950 | / lb H2O
d. desiccant system power consumption | #DIV/0! | W / cfm
e. heat recovery wheel effectiveness | 4000
f. regeneration and ventilation exhaust temperatures | 0 | 17990 | °F
g. desiccant inlet and exit humidities | 2000 | 0 | grains
6. Fuel Cell Data
a. cost of stack | 1750 | / kW
b. stack lifetime | 5 | years
c. availability of fuel cell for stack replacement calculations | 0.96
7. Allocation of Recovered Waste Heat
a. space heating and hot water | 0%
b. absorption chilled water production | 100%
c. desiccant regeneration | 0%
d. fraction of recoverable waste heat used effectively | 100%
8. Miscellaneous Assumptions
a. standby charges | 24 | / kW per year
b. price of exported power | 0.025 | / kWh
c. fraction of generated power used on site | 100%
d. boiler efficiency | 0.72
7. Data for Graph
a. maximum for horizontal axis | 0.25 | / kWh
b. maximum for vertical axis | 20 | / MMBtu
c. alternative cost of fuel | 4.5 | MMBtu

## Output Report
Atlanta Metropolitan Area: Output Summary
1. Current Plant
a. average electric load | 3542.8572 | kW
b. peak electric load | 7300 | kW
c. average thermal load | 12.0138 | MMBtu / h
2. CHP Plant
a. electrical capacity | 5200 | kW
b. thermal capacity | 25.5432 | MMBtu / h
c. installed cost
(1) generator and HRSG | 7420400 | 1427 | / kW
(2) absorption chiller | 1012500 | 194.7115 | / kW
(3) desiccant dehumidifier | 0 | 0 | / kW
(4) miscellaneous project costs | 0 | 0 | / kW
(5) subtotal | 8432900 | 1621.7115 | / kW
(6) project scaling factor | 1 | 1
(7) adjusted project cost | 8432900 | 1621.7115 | / kW
(8) equipment subsidy or buy-down | 0 | 0 | / kW
(9) net project cost | 8432900 | 1621.7115 | / kW
d. annual cost savings | -490845.0389
3. Energy Summary
a. fuel input | 498411.0144 | MMBtu
b. energy outputs
(1) electricity generated | 149505.7824 | MMBtu | 43804800 | kWh
(2) useful recovered heat | 215175.6327 | MMBtu
(3) total outputs | 364681.4151 | MMBtu
c. efficiencies
(1) electrical | 30%
(2) overall | 73.17%
4. CHP Metrics
a. average cost of power | 0.060485 | / kWh
b. average cost of fuel | 7.602 | / MMBtu
c. spark spread | 10.12 | / MMBtu
d. average to peak electric ratio | 0.48532
e. average to peak thermal ratio | unknown
f. thermal to electric ratio | 0.99356
g. simple payback | -17.1804 | years
h. financed payback at 6.00% | -12.1581 | years
5. Cost of Operation
a. increased costs
(1) fuel and O&M | 4121856.8677 | / year | 0.094096 | / kWh generated
(2) standby charges | 124800 |  | 0.002849
(3) total increased costs | 4246656.8677 |  | 0.096945
b. avoided costs
(1) purchased electricity | 2649541.9053 | / year | 0.060485 | / kWh generated
(2) boiler fuel for heat & steam | 0 |  | 0
(3) electricity for chiller operation | 1106269.9235 |  | 0.025255
(4) electricity for dehumidification | 0 |  | 0
(4) exported electricity | 0 |  | 0
(5) total avoided costs | 3755811.8288 |  | 0.08574
c. net savings / losses from operation | -490845.0389 | / year | -0.011205 | / kWh generated

## Plot Data
| Current Energy Rates | Future Energy Rates |  |  |  | Parameters Used in Table
[6 empty] | f1 | 0 | A | 1.4175
Energy Rates | [5 empty] | f2 | 0.41753 | B | -0.011378 | Axis Limits | Minimum | Maximum
1. Electricity | 0.060485 | 0.060485 | / kWh |  |  | f3 | 0 | K1 | 0.19251 | 1. Electricity | 0 | 0.25 | / kWh
2. Fuel | 7.602 | 7.602 | / MMBtu |  |  | f4 | 0.0068224 | K2 | 0.010449 | 2. Natural Gas | 0 | 20 | / MMBtu
3. DCCHP | -0.011205 | -0.011205 | / kWh
4. Payback | -17.1804 | -17.1804 |  |  |  | DCCHP = AACe + BACfuel - K2 | [5 empty] | Parameters
[6 empty] | N = Pnet cost / (HADCCHP) = K1 / DCCHP | [5 empty] | 1. Gamma | g | 1 |  | 4.1343
Type of Heating System: |  | fossil | [9 empty] | 2. Alpha | a | 11378 | Btu / kWh
[6 empty] | 0 | 5 | 10 | 15 | 20 |  | 3. Beta | b | 1
[12 empty] | 4. Beta2 | b2 | 1
| Simple Payback | [10 empty] | 5. Delta | d | 0
Years | Horizontal Coordinate - Cost of Electricity |  |  |  |  | Vertical Coordinate - Cost of Fuel | [5 empty] | 6. Epsilon | e | 0
1 | 0.14318 | 0.18331 | 0.22344 | 0.25 | 0.25 | 0 | 5 | 10 | 13.3084 | 13.3084 |  | 7. gCOP | gCOP | 1.2
2 | 0.075275 | 0.11541 | 0.15554 | 0.19567 | 0.23581 | 0 | 5 | 10 | 15 | 20 |  | 8. EtaChiller | hchiller | 0.85 | kW / ton
3 | 0.05264 | 0.092773 | 0.13291 | 0.17304 | 0.21317 | 0 | 5 | 10 | 15 | 20 |  | 9. EtaBoiler | hboiler | 0.72
4 | 0.041323 | 0.081456 | 0.12159 | 0.16172 | 0.20186 | 0 | 5 | 10 | 15 | 20 |  | 10. Qe | Qe | 5200 | kW
5 | 0.034533 | 0.074666 | 0.1148 | 0.15493 | 0.19507 | 0 | 5 | 10 | 15 | 20 |  | 11. H | H | 8424 | hours / year
6 | 0.030006 | 0.070139 | 0.11027 | 0.15041 | 0.19054 | 0 | 5 | 10 | 15 | 20 |  | 12. COM | CO&M | 0.0076 | / kWh
7 | 0.026772 | 0.066905 | 0.10704 | 0.14717 | 0.1873 | 0 | 5 | 10 | 15 | 20 |  | 13. Cstandby | CStandby | 24 | / KW / year
8 | 0.024347 | 0.06448 | 0.10461 | 0.14475 | 0.18488 | 0 | 5 | 10 | 15 | 20 |  | 14. Cexport | Cexport | 0.025 | / kWh
9 | 0.022461 | 0.062594 | 0.10273 | 0.14286 | 0.18299 | 0 | 5 | 10 | 15 | 20 |  | 15. Psubsidy | Psubsidy | 0 | / year
10 | 0.020952 | 0.061085 | 0.10122 | 0.14135 | 0.18148 | 0 | 5 | 10 | 15 | 20 |  | 16. Pbuydown | Pbuydown | 0
11 | 0.019717 | 0.05985 | 0.099984 | 0.14012 | 0.18025 | 0 | 5 | 10 | 15 | 20 |  | 17. Pturbine | Pturbine | 1427 | / kW
12 | 0.018689 | 0.058822 | 0.098955 | 0.13909 | 0.17922 | 0 | 5 | 10 | 15 | 20 |  | 18. Pchiller | Pchiller | 194.7115 | / kW
13 | 0.017818 | 0.057951 | 0.098084 | 0.13822 | 0.17835 | 0 | 5 | 10 | 15 | 20 |  | 19. Kappa | k | 1
14 | 0.017072 | 0.057205 | 0.097338 | 0.13747 | 0.1776 | 0 | 5 | 10 | 15 | 20 |  | 20. i | i | 6%
15 | 0.016425 | 0.056558 | 0.096691 | 0.13682 | 0.17696 | 0 | 5 | 10 | 15 | 20
16 | 0.015859 | 0.055992 | 0.096125 | 0.13626 | 0.17639 | 0 | 5 | 10 | 15 | 20
17 | 0.01536 | 0.055493 | 0.095626 | 0.13576 | 0.17589 | 0 | 5 | 10 | 15 | 20
18 | 0.014916 | 0.055049 | 0.095182 | 0.13532 | 0.17545 | 0 | 5 | 10 | 15 | 20
19 | 0.014519 | 0.054652 | 0.094785 | 0.13492 | 0.17505 | 0 | 5 | 10 | 15 | 20
20 | 0.014162 | 0.054295 | 0.094428 | 0.13456 | 0.17469 | 0 | 5 | 10 | 15 | 20
1000 | 0.0075071 | 0.04764 | 0.087773 | 0.12791 | 0.16804 | 0 | 5 | 10 | 15 | 20
Vertical level of contour labels (fuel price) |  |  |  | 0.5
Coordinates for labeling contour lines
5 | 0.038546 | 0.5
10 | 0.024965 | 0.5
15 | 0.020438 | 0.5
20 | 0.018175 | 0.5
1000 | 0.01152 | 0.5
Simple Payback
Years | Horizontal Coordinate - Cost of Electricity |  |  |  |  | Vertical Coordinate - Cost of Fuel
1 | 0.14318 | 0.18331 | 0.22344 | 0.25 | 0.25 | 0 | 5 | 10 | 13.3084 | 13.3084
2 | 0.075275 | 0.11541 | 0.15554 | 0.19567 | 0.23581 | 0 | 5 | 10 | 15 | 20
3 | 0.05264 | 0.092773 | 0.13291 | 0.17304 | 0.21317 | 0 | 5 | 10 | 15 | 20
4 | 0.041323 | 0.081456 | 0.12159 | 0.16172 | 0.20186 | 0 | 5 | 10 | 15 | 20
5 | 0.034533 | 0.074666 | 0.1148 | 0.15493 | 0.19507 | 0 | 5 | 10 | 15 | 20
6 | 0.030006 | 0.070139 | 0.11027 | 0.15041 | 0.19054 | 0 | 5 | 10 | 15 | 20
7 | 0.026772 | 0.066905 | 0.10704 | 0.14717 | 0.1873 | 0 | 5 | 10 | 15 | 20
8 | 0.024347 | 0.06448 | 0.10461 | 0.14475 | 0.18488 | 0 | 5 | 10 | 15 | 20
9 | 0.022461 | 0.062594 | 0.10273 | 0.14286 | 0.18299 | 0 | 5 | 10 | 15 | 20
10 | 0.020952 | 0.061085 | 0.10122 | 0.14135 | 0.18148 | 0 | 5 | 10 | 15 | 20
11 | 0.019717 | 0.05985 | 0.099984 | 0.14012 | 0.18025 | 0 | 5 | 10 | 15 | 20
12 | 0.018689 | 0.058822 | 0.098955 | 0.13909 | 0.17922 | 0 | 5 | 10 | 15 | 20
13 | 0.017818 | 0.057951 | 0.098084 | 0.13822 | 0.17835 | 0 | 5 | 10 | 15 | 20
14 | 0.017072 | 0.057205 | 0.097338 | 0.13747 | 0.1776 | 0 | 5 | 10 | 15 | 20
15 | 0.016425 | 0.056558 | 0.096691 | 0.13682 | 0.17696 | 0 | 5 | 10 | 15 | 20
16 | 0.015859 | 0.055992 | 0.096125 | 0.13626 | 0.17639 | 0 | 5 | 10 | 15 | 20
17 | 0.01536 | 0.055493 | 0.095626 | 0.13576 | 0.17589 | 0 | 5 | 10 | 15 | 20
18 | 0.014916 | 0.055049 | 0.095182 | 0.13532 | 0.17545 | 0 | 5 | 10 | 15 | 20
19 | 0.014519 | 0.054652 | 0.094785 | 0.13492 | 0.17505 | 0 | 5 | 10 | 15 | 20
20 | 0.014162 | 0.054295 | 0.094428 | 0.13456 | 0.17469 | 0 | 5 | 10 | 15 | 20
1000 | 0.0075071 | 0.04764 | 0.087773 | 0.12791 | 0.16804 | 0 | 5 | 10 | 15 | 20

## Equations
g | fraction of generated power used on site
a | heat rate of generator (Btu / kWh)
b | fraction of recoverable waste heat used effectively
b2 | fraction of recoverable waste heat used to produce chilled water
d | misc. engine-generator thermal losses (%)
e | HRHX effectiveness
gCOP | absorption chiller efficiency
hchiller | alternative electric chiller efficiency (kW / ton)
hboiler | alternative boiler efficiency
H | annual hours of operation
CO&M | non-fuel generator operating and maintenance costs ($ / kWh generated)
CStandby | annual utility charges for distributed generation ($ / kW installed per year)
Cexport | value of exported electricity ($ / kWh)
Ce | average avoided cost of electricity ($ / kWh)
Psubsidy | annual operating subsidy for "externalities" (e.g. energy security), ($ per year)
Pbuydown | one-time payment to subsidize equipment and installation
Pturbine | installed cost of turbine, IC-engine generator, microturbine, or fuel cell ($ / kW)
Pchiller | installed cost of absorption chiller ($ / kW of generating capacity)
k | multiplier for final cost (generally equal to 1.0)
i | interest rate
Three recent changes have been made that are not reflected in these equations
1. Annual operating subsidy for "externalities" is included in value of generation ($ per year divided by annual generation, kWh)
2. Net installed cost is computed by subtracting a one time payment divided by the total installed capacity (to get $/kW) from the cost of prime-mover/generator and any absorption chillers
3. A multiplier "k" has been added to increase (or decrease) the computed net installed cost to account for other, non-itemized, costs.
The primary use of this spreadsheet to date has been for retrofit applications in federal facilities where there is no cost associated with the "Do Nothing" alternative to CHP.
Comparisons with a non-CHP alternative can be determined by assigning the cost associated with the alternative as an up-front one-time payment in order to get a net installed cost.

## EGRID 200 Data
EGRID-2000 Data
| Energy Input | CO2 | NOx | SOx | State abbreviation | State 2000 annual heat input (MMBtu) | State 2000 annual net generation (MWh) | State 2000 annual NOx emissions (tons) | State 2000 annual SO2 emissions (tons) | State 2000 annual CO2 emissions (tons)
| Btu / kWh | lb / kWh | lb / kWh | lb / kWh | PSTATABB | STHTIAN | STNGENAN | STNOXAN | STSO2AN | STCO2AN
Alabama | 7790.2175 | 1.4463 | 0.0030477 | 0.0082836 | AL | 968808334.7 | 124362167.4 | 189508.64 | 515083.663 | 89932307.145
Alaska | 9714.5625 | 1.2913 | 0.0048659 | 0.0013486 | AK | 59807942.9 | 6156524.6 | 14978.584 | 4151.465 | 3975039.19
Arizona | 6194.4516 | 1.1752 | 0.002343 | 0.0016277 | AZ | 551083831 | 88964102.9 | 104220.977 | 72401.525 | 52273856.921
Arkansas | 8071.781 | 1.4533 | 0.0024252 | 0.0034654 | AR | 356424151.1 | 44156816.1 | 53543.838 | 76510.438 | 32085814.142
California | 5598.7198 | 0.63274 | 0.00057206 | 0.00017304 | CA | 1167200156.8 | 208476257.8 | 59630.503 | 18037.088 | 65955473.959
Colorado | 10382.1873 | 2.0138 | 0.0034941 | 0.0040765 | CO | 459315302.7 | 44240706.6 | 77289.646 | 90174.261 | 44545288.177
Connecticut | 5038.8006 | 0.73883 | 0.0014468 | 0.0022697 | CT | 167397060.5 | 33221608.7 | 24031.923 | 37702.08 | 12272639.363
Delaware | 10248.2915 | 1.9515 | 0.0034666 | 0.012955 | DE | 61521626.4 | 6003110.5 | 10405.288 | 38885.946 | 5857558.735
Florida | 8424.0812 | 1.4204 | 0.0033893 | 0.0060435 | FL | 1616637108.9 | 191906639 | 325217.031 | 579895.186 | 136293930.605
Georgia | 7358.4956 | 1.4139 | 0.0031415 | 0.0085209 | GA | 908545417.3 | 123468907.8 | 193937.169 | 526033.203 | 87284671.905
Hawaii | 10290.8353 | 1.7166 | 0.0052748 | 0.0045801 | HI | 109528728.2 | 10643327.3 | 28070.491 | 24373.532 | 9135395.518
Idaho | 1235.2261 | 0.093036 | 0.00016217 | 9.3948e-05 | ID | 15674135.2 | 12689283.9 | 1028.91 | 596.065 | 590281.072
Ilinois | 5614.9953 | 1.1094 | 0.0027075 | 0.0049321 | IL | 996364273.1 | 177447035.1 | 240217.737 | 437593.104 | 98433953.14
Indiana | 10648.9381 | 2.153 | 0.0052192 | 0.013254 | IN | 1411176758.7 | 132518073 | 345817.277 | 878200.882 | 142652630.001
Iowa | 9680.2386 | 1.972 | 0.0040452 | 0.0069096 | IA | 402115397.1 | 41539822.9 | 84018.467 | 143511.781 | 40957670.406
Kansas | 9478.1374 | 1.8685 | 0.0042515 | 0.0051963 | KS | 424684921 | 44806790.8 | 95247.455 | 116415.431 | 41861631.122
Kentucky | 10888.8438 | 2.2288 | 0.0053071 | 0.012569 | KY | 1013813701.8 | 93105725.7 | 247060.664 | 585141.362 | 103757223.176
Louisiana | 8910.6058 | 1.3863 | 0.0025389 | 0.0035263 | LA | 830108293.2 | 93159580 | 118263.577 | 164255.006 | 64572703.379
Maine | 7583.994 | 0.65509 | 0.0014629 | 0.0021705 | ME | 107159489.2 | 14129690.7 | 10334.859 | 15334.151 | 4628116.082
Maryland | 7272.0908 | 1.3728 | 0.0035088 | 0.010083 | MD | 372706722 | 51251659.3 | 89916.257 | 258396.765 | 35179893.829
Massachusetts | 8335.8838 | 1.2932 | 0.0021035 | 0.0055569 | MA | 340480345.2 | 40845140.5 | 42957.939 | 113485.947 | 26409475.572
Michigan | 8488.0234 | 1.5647 | 0.0033627 | 0.0070641 | MI | 885497574.8 | 104323177.8 | 175401.933 | 368475.446 | 81618637.965
Minnesota | 8440.2295 | 1.6401 | 0.0039125 | 0.0049837 | MN | 418696194.7 | 49607205.2 | 97045.228 | 123612.814 | 40679792.912
Mississippi | 7420.7252 | 1.3167 | 0.0034233 | 0.0070516 | MS | 279207499.5 | 37625365.6 | 64401.776 | 132660.033 | 24771252.024
Missouri | 9598.1056 | 1.9794 | 0.0043143 | 0.006153 | MO | 731083037.9 | 76169513.7 | 164309.342 | 234337.24 | 75384700.203
Montana | 7121.247 | 1.4602 | 0.0028475 | 0.0017428 | MT | 188369989.5 | 26451826.4 | 37660.395 | 23049.955 | 19312920.014
Nebraska | 7612.4945 | 1.5468 | 0.0031212 | 0.0042903 | NE | 215334721.4 | 28287011.8 | 44145.39 | 60679.297 | 21877751.556
Nevada | 9007.9469 | 1.5521 | 0.0029638 | 0.0029726 | NV | 322883224.7 | 35844263.6 | 53117.591 | 53275.616 | 27817510.553
New Hampshire | 4566.7698 | 0.70863 | 0.0014162 | 0.0068787 | NH | 68645386.2 | 15031497 | 10643.503 | 51698.926 | 5325908.552
New Jersey | 4951.4876 | 0.73255 | 0.0013934 | 0.0021239 | NJ | 296707119.9 | 59922823.8 | 41748.505 | 63635.564 | 21948363.668
New Mexico | 11014.7297 | 2.137 | 0.0051204 | 0.0040443 | NM | 374820909.9 | 34029061 | 87121.259 | 68812.162 | 36360448.804
New York | 6241.1947 | 0.97968 | 0.0014683 | 0.0041351 | NY | 866014343.3 | 138757783.1 | 101872.382 | 286891.656 | 67968927.293
North Carolina | 6591.9154 | 1.2928 | 0.0029301 | 0.0076106 | NC | 806304005.3 | 122317105.4 | 179199.122 | 465456.192 | 79068763.88
North Dakota | 11009.2722 | 2.3933 | 0.0050038 | 0.009729 | ND | 344713468.9 | 31311194.9 | 78338.196 | 152313.235 | 37468872.705
Ohio | 9072.6149 | 1.844 | 0.0051314 | 0.016538 | OH | 1352210836.6 | 149043120.9 | 382403.49 | 1232450.969 | 137417886.892
Oklahoma | 10388.292 | 1.8359 | 0.0036437 | 0.003466 | OK | 582753992.9 | 56097190.5 | 102200.915 | 97217.134 | 51494005.465
Oregon | 2363.7002 | 0.32927 | 0.00055786 | 0.00056423 | OR | 122474595.2 | 51814774.9 | 14452.645 | 14617.674 | 8530490.713
Pennsylvania | 6255.2314 | 1.2341 | 0.0027225 | 0.0095268 | PA | 1250947788.4 | 199984254 | 272232.319 | 952602.435 | 123400394.126
Rhode Island | 8735.9307 | 1.0017 | 0.00053241 | 0.00019355 | RI | 53145092.1 | 6083506.6 | 1619.464 | 588.72 | 3046927.593
South Carolina | 4560.7983 | 0.89325 | 0.0019584 | 0.0044184 | SC | 425750086.9 | 93349905.2 | 91409.431 | 206228.698 | 41692217.426
South Dakota | 4466.1387 | 0.83272 | 0.0035412 | 0.0027515 | SD | 46989089 | 10521189 | 18628.867 | 14474.49 | 4380617.568
Tennessee | 6821.6092 | 1.3685 | 0.0033225 | 0.0087402 | TN | 653773361.4 | 95838583.3 | 159211.173 | 418823.674 | 65578412.253
Texas | 9269.5889 | 1.4685 | 0.0023081 | 0.0030447 | TX | 3513927468.6 | 379081264.8 | 437470.548 | 577102.286 | 278341667.857
U.S. Average | 7723.4895 | 1.3899 | 0.002937 | 0.0060836 |  | 26140803484.1 | 3384584589.1 | 4970330.706 | 10295183.097 | 2352142023.461
Utah | 10370.1501 | 2.0955 | 0.004435 | 0.0015603 | UT | 379580456.6 | 36603178.7 | 81167.422 | 28555.693 | 38350381.556
Vermont | 1244.4082 | 0.056934 | 0.00031091 | 5.3274e-05 | VT | 7843523.1 | 6303014.4 | 979.837 | 167.894 | 179428.566
Virginia | 6581.6737 | 1.2231 | 0.0025407 | 0.0058289 | VA | 508271225.9 | 77225223.5 | 98104.543 | 225069.163 | 47228008.007
Washington | 1920.1322 | 0.28749 | 0.00055529 | 0.0015759 | WA | 206634315.8 | 107614631.7 | 29878.621 | 84793.052 | 15468832.85
Washington DC | 17023.6899 | 2.657 | 0.0052124 | 0.013622 | DC | 2457773.1 | 144373.7 | 376.265 | 983.318 | 191797.152
West Virginia | 9890.3765 | 2.0273 | 0.005786 | 0.01288 | WV | 918471538.1 | 92865174.7 | 268659.985 | 598053.146 | 94134001.269
Wisconsin | 9004.423 | 1.7607 | 0.0037541 | 0.0066323 | WI | 537277129.2 | 59668135.3 | 112000.027 | 197867.364 | 52527449.3
Wyoming | 11220.0776 | 2.3024 | 0.0040476 | 0.0037291 | WY | 509697355.9 | 45427257.8 | 91936.597 | 84702.289 | 52294863.973