## 4.8-1 Tech Equip vs Loc
| MI-60 Service Building South | MI-60 Service Building North | MI-62 Service Building | MI-65 Service Building | Target Hall PS Support Room | MINOS Service Building | MINOS Near Detector Hall | Absorber Access Tunnel
| 60S | 60N | 62SB | 65SB | THSR | MSB | MND | AAT
Power Supplies
Single Turn Extraction Kicker | X
Lambertsons |  | X
Dipole Magnets - Ramped |  | X | X | X
Quadrupole Magnets - Ramped |  | X | X | X
Trim Correction Elements |  | X |  | X
Focusing Horns Including Stripline |  |  |  |  | X
Loss and Profile Monitor High Voltage |  | X | X | X | X
Near Detector Analysis Magnet | [6 empty] | X
Vacuum
Primary Beam Transport - Including Isolation Valves, Gauges & Ion Pumps |  | X | X
Decay Pipe (PLC) | [7 empty] | X
Fluid Systems
Flourinert Cooling for Extraction Kickers | X
MI-62 LCW and Pond Water Systems (PLC) |  |  | X
Target & Baffle RAW System (PLC) |  |  |  |  | X
Horn 1 RAW System (PLC) |  |  |  |  | X
Horn 2 RAW System (PLC) |  |  |  |  | X
Target Pile Air Cooling System (PLC) |  |  |  |  | X
MINOS LCW System (PLC) | [6 empty] | X
MINOS Sump Pumps | [5 empty] | X | X
Decay Pipe Cooling RAW System (PLC) |  |  |  |  | X |  |  | X
Intermediate Water Cooling for Absorber RAW System (PLC) | [7 empty] | X
Absorber Cooling RAW System (PLC) | [7 empty] | X
Instrumentation
Primary Transport Beam Position Monitors |  | X |  | X
Beam Profile Monitors |  | X |  | X
Loss Monitors |  | X | X |  | X
Total Loss Monitors |  |  | X
Beam Intensity Toroids |  |  | X |  | X
Baffle and Target Instrumentation (PLC) |  |  |  |  | X
Target Budal Monitors |  |  |  |  | X
Positioning Systems for Target and Horn 1 |  |  |  |  | X
Horn 1 and 2 Module and Stripline Instrumentation (PLC) |  |  |  |  | X
Horn Bdot Magnetic Field Probes |  |  |  |  | X
Absorber Instrumentation (PLC) | [7 empty] | X
Hadron Monitor at Downstream End of Decay Pipe | [7 empty] | X
Muon Monitors at Muon Alcoves #1, #2 and #3 | [7 empty] | X
Beam Permit System - Process Channel Interface (7 Total) | X | XX | X | X | XX
ACNET Connectivity
Ethernet | X | X | X | X | X | X | X | X
VME | X | X | X | X | X |  |  | X
Internet Rack Monitor - IRM |  |  |  |  | X
Programmable Logic Controller - PLC |  | X | X | X | X |  | X | X
CAMAC | X | X | X | X | X | X | X | X

## 4.8-2 $29 Cycle Timing
Timing Observations of MI $29 Cycle for P-Bar Production Cycle
Event | Description / Comment | Time in Milliseconds | Note
80 | 3 x 15 Hz Ticks Before $29 MI Reset or -201 ms | -201
29 | Main Injector Reset | 0 | 1
22 | Start of Ramp | 89
25 | Start of Flattop | 778.9
MIBS $79 | Initiate P-Bar Production Beam Transfer | 838.9
| MI-52 Kicker Fire Time MIBS $79 + 24.918 MR Rev | 839.1517
26 | End of Beam Operations | 848.9
| Total $29 Cycle Time | 1466.7 | 2
| Flattop to Actual P-Bar Production Beam Extraction | 60.2517
Note 1 | The $29 to $22 Interval Accommodates One $14 Booster Batch to Main Injector.
Note 2 | The Current $29 Cycle is Judged to be Twenty-Two 15 Hz Ticks Long or 1.467 Seconds

## 4.8-3 $23 Cycle Timing
Expected Timing for MI $23 Cycle for P-Bar Production and NuMI Operations
Event | Description / Comment | Time in Milliseconds | Note
80 | Signature Event for P-Bar Production Cycle | ? | 3
$A5 | Signature Event for NuMI Beam Cycle | -0.001 | 4
23 | Main Injector Reset | 0 | 5 & 6
22 | Start of Ramp | 422.3
25 | Start of Flattop | 1112.2
MIBS $79 | Initiate P-Bar Production Beam Transfer | 1172.2
| MI-52 Kicker Fire Time MIBS $79 + 24.918 MI Rev | 1172.4517
MIBS $74 | Initiate NuMI Beam Extraction | 1173.3 | 7
| I:KPS6N Kicker Fire Time MIBS $74 + 20.xxx MI Rev | 1173.5 | 8
26 | End of Beam Operations | 1182.2
| Total $23 Cycle Time | 1800 | 9
| Flattop to Actual P-Bar Production Beam Extraction | 60.2517
| Flattop to Actual NuMI Beam Extraction | 61.3
Note 3 | $80 May be Placed Before or After the $23, but Must be Before the $14.
Note 4 | The $A5 Event is Now Expected to be Imediately Before the $23 MI Reset. That Stated, $A5 May be Placed Before or After the $23, but Must be Before the $19s.
Note 5 | The $23 to $22 Interval Will Accommodate Six Booster Batches to Main Injector. Normally a Single $14 Batch for P-Bar Production and 5 x $19 Batches for NuMI.
Note 6 | The $29 to $22 Interval of 89 ms is Extended by Five 15 Hz Ticks for the $23 Ramp Scenario. Subsequent Times Generally Advance by 333.3 ms.
Note 7 | Exact Placement of MIBS Extraction Event is Subject to Observed Peak of Longitudinal Bunch Length and Number of Integral MI Turns of Beam After MIBS $74.
Note 8 | Time is About 1 ms After P-Bar Production Beam Extraction When Longitudinal Bunch Length is Peaked. 20 MI Revolutions is the Suggested Integral Value of Delay After MIBS $74. ".xxx" Fractional Turn Delay to be Field Determined.
Note 9 | The Expected $23 Cycle is Judged to be Twenty-Seven 15 Hz Ticks Long or 1.8 Seconds

## 4.8-4 NuMI TCLK & MIBS Events
NuMI TCLK and MIBS EVENTS
TCLK | DEFINITION | COMMENT
$A5 | NuMI Reset for Extracted Beam | Expected to be Closely Synchronous With and Well in Advance of NuMI Extracted Beam. Primary Reset for NuMI Ramped Devices.
23 | Main Injector Cycle Reset for P-Bar Production and NuMI Operations | Usually Has Beam for Both P-Bar Production and NuMI Operations. But Could Have Beam for Only One Destination.
14 | Booster Reset for P-Bar Production Beam | Normally One High Intensity Batch.
19 | Booster Reset for NuMI Operations Beam | Normally One to Five Batches for NuMI with Programmable Intensity.
52 | Beam for Previous Booster Reset Will Be Accelerated. | A Generic Event.
53 | Beam for Previous Booster Reset Will Not Be Accelerated. | A Generic Event.
$1F | Booster Beam About to be Transferred to Main Injector | A Generic Event.
22 | Main Injector Ramp Begins | A Generic Event.
25 | Main Injector Flattop | A Generic Event.
81 | Reflected MIBS Event $79 | Expected to be Synchronous Within a Few Microseconds.
$A9 | Reflected MIBS Event $74 | Expected to be Synchronous Within a Few Microseconds.
27 | Detected Fall of the Main Injector Beam Permit | Fires the Main Injector Abort Kicker
$2F | Fire the Main Injector Abort | Happens Every Cycle.
26 | End of Beam Operations in the Main Injector | All Beam Should be Gone.
$A6 | NuMI Beam Permit Has Fallen to Non-Permit State | Serves to Inhibit Accelerating Beam Associated With Booster $19 Reset. Also Will Inhibit Generation of MIBS $74.
$A8 | NuMI Beam Permit System Reset | Issued by Operator Command. Rcvd by C200 and C201 Modules. Clears Latched Inputs of C200.
$FA | Reflected MIBS $ED | A Generic Event.
MIBS | DEFINITION | COMMENT
$AA | Main Injector Revolution Marker | Once Every 588 RF Cycles. Approximate 10 Microsecond Period.
79 | Initiate Transfer of 120 GeV P-Bar Prod Beam to P-Bar Tgt | Reflected as TCLK $81.
74 | Initiate Transfer of 120 GeV NuMI Beam to NuMI Primary Beamline | Reflected as TCLK $A9.
$ED | Request for a MIBS Transfer Event Has Been Denied | Reflected as TCLK $FA. This is a Generic Event. If One Expects to See $74 or $79 and Does Not, This $ED Event Should Be Generated.

## 4.8-5 Interlk Areas & Barriers
Area # | Area Description | RSS | Associated Barrier
Area 1 | Upstream Carrier Tunnel | Main Inj | G1 D2
Area 2 | Downstream Carrier Tunnel, Pre-Target Enclosure and Target Hall, Including Entrance Labyrinth | NuMI | D2 G3 D4
Area 3 | Decay Pipe Passageway (Mini-Loop) | NuMI | D4 G5
Area 4 | Absorber Hall Including Upstream End of Absorber Access Tunnel, Entrance Labyrinth and Muon Alcove #1 | NuMI | G5 D6
Area 5 | Muon Alcove #2 | NuMI | D7
Area 6 | Muon Alcove #3 | NuMI | D8
Area 7 | Muon Alcove #4 | NuMI | D9
Gate or Door# | Barrier Location | RSS | Area
Gate 1 | Upstream End of Carrier Tunnel | MI | Area 1
Door 2 | Fire Door and CMU Wall at Mid-Point of Carrier Tunnel | MI + NuMI | Areas 1 & 2
Gate 3 | Beginning of Entrance Labyrinth to Pre-Target and Target Hall at Bottom of MI-65 Shaft Stairway | NuMI | Area 2
Door 4 | Fire Door at Upstream End of Decay Pipe Passageway | NuMI | Areas 2 & 3
Gate 5 | Gate at Downstream End of Decay Pipe Passageway | NuMI | Areas 3 & 4
Door 6 | Fire Door Across Absorber Access Tunnel Between Absorber Hall and Muon Alcove #2 | NuMI | Area 4
Door 7 | Entrance to Muon Alcove #2 | NuMI | Area 5
Door 8 | Entrance to Muon Alcove #3 | NuMI | Area 6
Door 9 | Entrance to Muon Alcove #4 (This Door May Be Simply Locked Closed by RSO Lock) | NuMI | Area 7

## 4.8-6 MI-65 Shaft Cables
MI-65 Service Building Shaft Wire and Cable - Installed Under SB&O Subcontract
Quantity | Avg Length | Type of Cable | Start | Finish | Route | Utilization | Provided & Used By
14 | 491 | Insulated Copper Building Wire 500 MCM THHN Black | Electrical Room | Two Locations in Pre-Target | Power Tray | E:V118 String of Four B2 Dipoles | Subcontractor WBS 1.1.3
20 | 583 | Insulated Copper Building Wire 1/0 THHN Black | Electrical Room | Varied Locations in Carrier Tunnel & Pre-Target | Power Tray | Q113-Q121 Quads and H117 Dipole | Subcontractor WBS 1.1.3
9 | 585 | Shielded Twisted Pair 10 AWG | Electronics Room | Varied Locations in Carrier Tunnel & Pre-Target | Power Tray | Trim Elements | Fermilab WBS 1.1.3
24 | 536 | 3/8" Low Loss Heliax Coax Andrew LDF2RN-50 | Electronics Room | Varied Locations in Carrier Tunnel & Pre-Target | Signal Tray | Beam Position Monitors & Calibration Signals | Fermilab WBS 1.1.1
12 | 555 | Amphenol Spectra Strip Round 'n' Flat #843-159-2801-050 | Electronics Room | Varied Locations in Carrier Tunnel & Pre-Target | Signal Tray | Profile Monitor Signal | Fermilab WBS 1.1.1
2 | 500 | Multiconductor, 19 Conductor, 18 AWG, Alpha 1898/19C | Electronics Room | Pre-Target | Power Tray | Profile Monitor Motors Trunk | Fermilab WBS 1.1.1
4 | 500 | Multiconductor, 9 Shielded Twisted Pairs, 18 AWG, Alpha 6025C | Electronics Room | Pre-Target | Signal Tray | Profile Monitor LVDTs Trunk | Fermilab WBS 1.1.1
1 | 500 | Multiconductor, 15 Shielded Twisted Pairs, 22 AWG, Alpha 6018C | Electronics Room | Pre-Target | Signal Tray | Profile Monitor Limit Switches Trunk | Fermilab WBS 1.1.1
1 | 500 | Multiconductor, 15 Shielded Twisted Pairs, 22 AWG, Alpha 6018C | Electronics Room | Pre-Target | Signal Tray | Magnet Klixons Trunk | Fermilab WBS 1.1.3
1 | 300 | Fiber Optic Trunk Cable 24 Fiber Singlemode | Electronics Room | Target Hall PS Support Room | Signal Tray | Networking | Fermilab WBS 1.1.8
1 | 300 | Fiber Optic Trunk Cable 36 Fiber Multimode | Electronics Room | Target Hall PS Support Room | Signal Tray | Controls | Fermilab WBS 1.1.8
2 | 300 | Multiconductor, 20 Conductor, 18 AWG, Custom, Blue Jkt | Electronics Room | Target Hall PS Support Room | Signal Tray | Radiation Safety System | Fermilab WBS 1.1.8
2 | 300 | Multiconductor, 4 Shielded Twisted Pairs, 18 AWG, Custom, Blue Jkt | Electronics Room | Target Hall PS Support Room | Signal Tray | RSS Data Links & Audio Warning | Fermilab WBS 1.1.8
1 | 300 | Multiconductor, 15 Shielded Twisted Pairs, 22 AWG, Alpha 6018C | Electrical Room | Target Hall PS Support Room | Signal Tray | FIRUS Utility Monitors & Spare Utility | Fermilab WBS 1.1.8
2 | 300 | RG213/U 50 Ohm Coax Red Jkt, Stk #1170-044500 | Electronics Room | Target Hall PS Support Room | Signal Tray | EAV-2 and EAV-3 Stack Rad Monitors | Fermilab WBS 1.1.8
1 | 300 | Multicoax, 16 x RG58C/U, 50 Ohm, Custom, Orange Jacket | Electronics Room | Target Hall PS Support Room | Signal Tray | Profile Monitor Clearing HV & Spare Utility | Fermilab WBS 1.1.1
2 | 300 | CAC-6 75 Ohm Coax | Electronics Room | Target Hall PS Support Room | Signal Tray | CATV Monitors | Fermilab WBS 1.1.8
4 | 300 | RG59/U 75 Ohm Coax | Electronics Room | Target Hall PS Support Room | Signal Tray | CATV Cameras | Fermilab WBS 1.1.8
1 | 300 | Multiconductor, 25 Twisted Pairs, 24 AWG, Teflon Jacket | Electrical Room Inside Terminal | Target Hall PS Support Room | Signal Tray | Telecom POTS | Fermilab WBS 1.1.8

## 4.8-7 MINOS Shaft Cables
MINOS Service Building Shaft Wire and Cable - Installed Under SB&O Subcontract
Quantity | Length Each | Type of Cable | Start | Finish | Route | Utilization | Provided & Used By
1 | 725 | Fiber Optic Trunk Cable 24 Fiber Singlemode | Mechanical - Electrical Area | MINOS Hall | Signal Conduit | Network Fiber | Fermilab WBS 1.1.8
1 | 725 | Fiber Optic Trunk Cable 36 Fiber Multimode | Mechanical - Electrical Area | MINOS Hall | Signal Conduit | Controls Fiber | Fermilab WBS 1.1.8
1 | 725 | Multiconductor, 15 Shielded Twisted Pairs, 22 AWG, Alpha 6018C | Mechanical - Electrical Area | MINOS Hall | Signal Conduit | FIRUS Utility Monitors & Spare Utility | Fermilab WBS 1.1.8
4 | 725 | CAC-6 75 Ohm Coax | Mechanical - Electrical Area | MINOS Hall | Signal Conduit | CATV Monitors | Fermilab WBS 1.1.8
6 | 725 | RG59/U 75 Ohm Coax | Mechanical - Electrical Area | MINOS Hall | Signal Conduit | CATV Cameras | Fermilab WBS 1.1.8
3 | 725 | RG213/U 50 Ohm Coax Red Jkt, Stk #1170-044500 | Mechanical - Electrical Area | MINOS Hall | Signal Conduit | Spare Utility | Fermilab WBS 1.1.8
1 | 725 | Multicoax, 16 x RG58C/U, 50 Ohm, Custom, Orange Jacket | Mechanical - Electrical Area | MINOS Hall | Signal Conduit | Spare Utility | Fermilab WBS 1.1.8
1 | 725 | Multiconductor, 25 Twisted Pairs, 24 AWG, Teflon Jacket | Mechanical - Electrical Area | MINOS Hall | Signal Conduit | Telecom POTS | Fermilab WBS 1.1.8
2 | 1100 | Multiconductor, 20 Conductor 18 AWG, Custom, Blue Jkt | Mechanical - Electrical Area | Upstream End of Absorber Access Tunnel | Signal Conduit and Tray | Radiation Safety System | Fermilab WBS 1.1.8
2 | 1100 | Multiconductor, 4 Shielded Twisted Pairs, 18 AWG, Custom, Blue Jkt | Mechanical - Electrical Area | Upstream End of Absorber Access Tunnel | Signal Conduit and Tray | Radiation Safety System Data Links | Fermilab WBS 1.1.8

## 4.8-8 MI-65 Comm Ducts
Comm Duct Cables from MI-62 to MI-65 Service Building 900 Feet
Qty | Type of Cable | Utility
1 | Fiber Optic Trunk 24 Singlemode Fibers | Accelerator Computer Network
3 | Fiber Optic Trunks 12 Multimode Fibers Each | Accelerator Controls including:
Main Injector CAMAC Link
Tevatron Clock (TCLK)
Main Inj Beam Sync (MIBS)
Machine Data (MDAT)
NuMI Beam Permit
DDC Utility Monitor System
2 | 20 Conductor 18 AWG Cables | Safety Interlock
2 | Four Twisted Pair Cables, 18 AWG | Safety Data Links and Audio Warning
1 | Three Twisted Pair, 18 AWG | ES&H Radiation Mux Trunk
3 | 1/2" 75 Ohm Hardline Coax Cables | FIRUS
3 | 1/2" 75 Ohm Hardline Coax Cables | CATV
1 | Four Twisted Pairs 16 AWG | NuMI Fire Protection Connectivity between MI-62 and MI-65 Bldgs
1 | Telephone Trunk Cable 50 Pair 24 AWG | Telephone Communications (POTS)

## 4.8-9 MI-65 to MBD Comm Ducts
MI-65 to MiniBooNE Detector Building 4,000 Feet
Qty | Type of Cable | Utility
2 | 20 Conductor 18 AWG Cables | Safety Interlock
2 | Four Twisted Pair Cables 18 AWG | Safety Data Links and Audio Warning
1 | Four Twisted Pairs 16 AWG | NuMI Fire Protection Connectivity between MI-65 and MINOS Bldgs

## 4.8-10 MINOS Comm Ducts
MiniBooNE Detector Building to MINOS Service Building 1,600 Feet
Qty | Type of Cable | Utility
1 | Fiber Optic Trunk 24 Singlemode Fibers | Accelerator Computer Network Including Wide Area Network Connectivity and Access to Fermilab Central Analysis and Data Storage Facilities
3 | Fiber Optic Trunks 12 Multimode Fibers Each | Accelerator Controls including:
Main Injector CAMAC Link
Tevatron Clock (TCLK)
Main Inj Beam Sync (MIBS)
Machine Data (MDAT)
NuMI Beam Permit
DDC Utility Monitor System
2 | 20 Conductor 18 AWG Cables | Safety Interlock
2 | Four Twisted Pair Cables, 18 AWG | Safety Data Links and Audio Warning
3 | 1/2" 75 Ohm Hardline Coax Cables | FIRUS (Sourced from Science Education Building and Accelerator Cross Gallery)
3 | 1/2" 75 Ohm Hardline Coax Cables | CATV (Sourced from Science Education Building and Accelerator Cross Gallery)
1 | Telephone Trunk Cable 50 Pair 24 AWG | Telephone Communications (POTS) (Sourced from Science Education Building Area and Accelerator Cross Gallery)
1 | Four Twisted Pairs 16 AWG | NuMI Fire Protection Connectivity between MI-65 and MINOS Bldgs