## #4 - And., Green, Total cryo
HYDRONGEN RELIEF VALVE SIZING FOR THE MUCOOL LH2 TOTAL LOOP
Anderson, Greenwood data base
Absorber volume (liter) | 25 | liter
Pressure of the system, MAWP | 25 | psia
Required mass flow rate |  |  |  | DATA FR Cryogenic systems, Barron
q, heat flux to vessel | 3500 | BTU/hr-ft^2
LH2 total surface area | 10.197 | ft^2
Delta-H | 206.72 | BTU/lb
| 88.8896 | Joule/g
Q, Heat transfer rate to vessel = qS | 35689.5 | BTU/hr-ft^2
| 10457.0235 | watt
Qbeam, | 1706.4846 | BTU/hr-ft^2
| 500 | watt
Total Q, adding the beam heat load | 37395.9846 | BTU/hr-ft^2
| 10957.0235 | watt
m, Mass-flow rate = Q/Delta_H | 180.9016 | lb/hr
| 22.7936 | g/s |  |  | Condition 1: |  | P=25psia, T=17K | P=25psia, Tsat=22.21K | Delta H
[6 empty] | H (BTU/lb) | -109.7 | 97.02 | 206.72
M (hydrogen) | 2.02
W, flow capacity (lbs/hr) | 180.9016 |  |  |  | Condition 2: |  | P=17.63psia, T=17K | P=17.63psia, Tsat=20.91K | Delta H
V (SCFM) | 565.9893 |  |  |  |  | H (BTU/lb) | -110 | 95.05 | 205.05
Required Relief valve orifice
Mass-flow rate | 180.9016 | lb/hr
| 22.7936 | g/s
T, absolute temperature | 530 | R
M, Molecular weight of H2 | 2.02
Z, compressibility | 1
K, valve discharge coefficient | 0.816
DP, pressure drop absorber to valve | 0.2 | psi
P1, pressure at valve inlet | 24.8 | psia
C, gas constant | 356
A, required area of orifice | 0.40674 | in^2
Diameter | 0.71982 | in
Actual flow capacity of relief device (subsonic formula)
P1, Pressure inlet | 25 | psia
P2, pressure outlet | 15 | psia
M, | 2.02
T | 530 | R
Z, compressibility | 1
A, commercial valve | 0.503 | in^2 | serie G
K, valve discharge coefficient | 0.816
k, ratio of specific heat | 1.41
m, actual mass-flow rate | 414.1045 | lb/hr
| 52.1772 | g/s