# Review

of

# The ATLAS ID evaporative cooling system

CERN, 14th June 2000

| The small scale evaporative cooling system for the ATLAS Inner Detector was reviewed. Conclusions are drawn from the results of the tests and the demonstration given to the reviewers. Recommendations for future work are given. |
| --- |
| Prepared by : S.Stapnes | Checked by : E.Anderssen,G.Gilchriese, M.Olcese,R.Apsimon,E.Perrin,D.Greenfield J.Godlewski, W.Witzeling,G.Bachy,G.Tappern | Approved by : |
| for information, you can contact : | S.Stapnes | Tel. +41.22.767 3706 | Fax. +41.22.767 8350 | E-mail steinar.stapnes@ cern.ch |

# Distribution: 	EB Members, TC Members, Members of the ID steering group, All participants mentioned in the report.

# Purpose of the review

Wednesday 14.6.2000 there was an internal ATLAS Inner Detector review of the small scale evaporative system setup in the cooling lab. The review was limited to the system aspects and did not include results of the structure tests, except that the structures were used as load and their temperatures were monitored to verify that the system operated correctly.

The purpose was :

- review the results obtained with the small scale setup (studies of system performance at startup, stop, sudden load variations, varying loads from standby to 100%).

- review of baseline system, including cooling services and control.

- identify key issues yet to be studied.

- review the phase two program leading up to the FDR in January 2001.

The report is written in three parts :

- The external parts and overall concept.

- The internal system, the cooling services.

- The phase II plans.

# Review committee.

E.Anderssen (LBNL), G.Gilchriese (LBNL), M.Olcese (Genova), R.Apsimon (RAL), E.Perrin (Geneva), D.Greenfield (RAL), J.Godlewski (Cracow), W.Witzeling (CERN), G.Bachy (CERN).

Ex-officio : G.Tappern (RAL), S.Stapnes (Oslo), M.Tyndel (RAL), L.Rossi (Genova).

# Background.

In the ID TDR April 1997 both the SCT and PIXEL groups presented binary ice as the baseline cooling, but the PIXEL group also presented an evaporative system (both systems low pressure).

The LHCC review in the summer 1997 strongly recommended an aggressive approach to material reduction in the ID - pointing to the cooling system as one area for saving.

The cooling review in Sept./Oct. 1997 concluded:

- Fluorinert should replace water for use in the cooling systems for the different sub-detectors

- The committee has a distinct preference for the evaporative systems for the following reasons :

- it has lower material budget

- the cooling medium is much safer

- the consequences of a leak are less dramatic

- there are less components so reliability should be higher

- the routing of pipes is simpler and more likely to fit into the available space

- The committee also recommended that the teams should combine resources and propose one evaporative system and pursue studies of such a system.

The Pixel TDR in May 1998 showed a C4F10 evaporative cooling system as baseline and a very important material reduction compared to binary ice. The SCT changed to monophase fluorinerts and also participated in the evaporative program.

Compared to monophase fluorinerts the material savings are also substantial:

0.4 % (o for the PIXELs - per layer, even more for the B-layer  (above 0.6 %).

0.05 - 0.1 % (o for the SCT - per layer.

In addition there are changes (positive or negative) depending on pipe-dimensions, pressures, heating blocks, manifolding versus capillaries and insulation thickness (several of these influence services space as well as material).

In the Spring 1999 both the SCT and PIXEL groups increased their power budgets for the FE electronics by 50%.

The phase I evaporative programme for the SCT and PIXEL was nevertheless concluded with a cooling review in May 1999, confirming the evaporative systems of the PIXEL and SCT detectors. A regulated system with input capillaries as demonstrated in the small scale review today was then presented. While the SCT already at that point suggested use of C3F8 , the PIXEL group officially changed to C3F8 in the fall 1999.

The CORE cost of the evporative system is 710 000 CHf and the next critical milestones are the FDR and PRR in the January/April 2001. These milestones are largely driven by the delivery of the first system to Oxford in the fall 2001.

# The external system and overall concept.

Observations : A small scale system which performed well and in a predictable way under many different conditions have been demonstrated and presented.

Main conclusion :

The reviewers all expressed that the system shown worked well and that they believe it can be made to work as a large system.

Concerns :

Resources for the next steps; in particular engineering manpower.

System complexity, reliability, operation complexity and need for experts during operation.

A complete new costing needed.

## Recommendations :

Move ahead with development of the complete evaporative cooling system.

Produce complete project plan for the project (both phase II and production).

Identify more manpower for the project.

Improve operational specifications (pressures, transient modes, delta T versus delta p in stave, failure modes); consistency across the SCT and PIXEL systems.

Develop model so that the system performance can be predicted and compared against data obtained with prototypes.

Define and cost pre-cooling system if used.

Use current system to develop and test the simplest possible configuration for the final system (more tests might be needed). In general the system and operation should be kept as simple as possible.

Perform radiation tests of the components, even though problems are not expected.

# The internal system, the cooling services.

Observations : The system was demonstrated with pre-cooling and no heating in return path. Results were also shown without pre-cooling and large heaters (200% of normal load) in the return. In both cases the cooling performance of the system was stable.

Most likely the services area will increase compared to the current layout, but further work is needed to optimise the services with the new grouping of services.

Main conclusion : Not conclusive with respect to the services but several of the implementations shown could work.

Concerns :

Large heaters, their operation, temperature and safety.

Complicated control loops between temperatures of the return, mass-flow regulations and heater power.

Resources (engineering).

Active insulation not well tested.

Space and layout of services.

Recommendations :

The ID cooling group should as soon as possible propose an engineered cooling services layout which keep the temperatures above the dew point (15 degrees to be safe) and below 25 degrees outside the active or passive insulation, justified by measurements and calculations.

Use the simplest and safest solution that does the job.

Identify/clarify responsibilities for this part of the system, design and implementation.

# Phase II.

Observation : The plans are well advances and the structures are being prepared. The components are identified. Timescale driven by delivery of the first system to Oxford (SCT assembly) in Sept 2001.

Main conclusion : The phase II work to move ahead as soon as possible.

Concerns :

The engineering support and documentation must be improved.

Resources (manpower mostly) not sufficient.

Structure measurements, including long term tests, will need to continue in parallel adding to the manpower problem.

Recommentation :

Move ahead with purchase of key components (compressor and regulators).

Define test-program (tests to be performed and conditions to be explored - as various geometrical orientations, thermal cross-talks, active heating, failures).

Identify manpower (include in costing if it has to be paid for as part of the project).

Identify responsible for services part of the system - in an attempt to increase the manpower involved.

The phase II system should be as close as possible to final system (identical in for all key elements), also the services part. Again, chose the simplest solutions for the implementation based on the results from the small scale tests (minimal heaters and simple control loops).

As a part of the project plan the phase II programme must be detailed, as well as structure tests on the parallel system (test-needs for the next year to be specified by the SCT and PIXEL groups).

Identify additional tests (material studies, irradiation studies).

# 7. Summary of main conclusion

Move ahead with the system as shown.

Use simplicity and safety as important guideline for further technical choices related to the services configuration and control aspect.

Develop complete project plan for phase II and production.

Improve resource situation quickly, in particular engineering manpower.

Re-cost system as important increases compared to CORE have been identified.

# 8. Acknowledgements

The reviewers would like to thank the participants in the review, in particular Gregory Hallewell and Vaclav Vacek, for the impressive effort put into the preparing the system, and to demonstrate and present it during the review. Their effort is very much appreciated.

# Appendix I: Format and agenda

9:00-12:00  : 	Demonstration  in the lab with the cooling group, seeing the system in action under varying conditions.

13:30-14:00 :   In 40-RD-10 Pre-meeting of reviewers.

14:00-17:00 :  	In 40-RD-10 (this meeting is open).

This will be followed by 3 hours of presentations of the small scale system and its performance.

The following will be covered (informal and with reasonable time for discussions):

- History and background

- Postmortem of the Counter Current Heater Exchanger tests.

- Description of the May setup in the lab.

- Results from the tests early May.

- Description of the current setup (shown in the morning).

- Results (mostly demonstrated in the morning, some additional comments).

- Description of a baseline system with regulated input / output for each channel (as tested).

- Phase (2) plans  - some comments.

An outline of the above  (results as of the IDSG 12.05.00) is available on :

http://edmsoraweb.cern.ch:8001/cedar/doc.info?document_id=111369&version=1

(all above G.Hallewell and V.Vacek)

- The services associated to the cooling (space limitations and first estimates).

(G.Tappern)

17:00-18:30 :   Closed session for the reviewers.

The transparencies shown can be found : pointer to be included.